## Slide 1: Additional CREs to address Stability Limits
Beth Garza
TAC
June 26, 2008

## Slide 2: Since the Adoption of PRR764
ERCOT and CMWG have been reviewing existing CREs
  ERCOT staff and Luminant analyses posted
  Two meetings of CMWG held, another scheduled for July11
  Discussion of a CRE ‘effectiveness criteria’ to supplement the two CRE tests already defined in Protocols
Today: ERCOT not prepared to propose removal of any existing CREs
  Is TAC willing to entertain a proposal to modify CRE list via email rather than waiting 6 weeks for next meeting?
Today: ERCOT recommending the addition of two CREs

## Slide 3: Section 7.2.3 (excerpt)
During the effective year, ERCOT staff may propose modifications to the list of CREs or the approved list of contingencies for managing CSC and CRE related congestion, including the expected duration of those modifications, as needed to more closely represent actual system constraints that can be effectively resolved by Zonal Balancing Energy deployments.
Any modifications to the list of CREs or the approved list of contingencies for managing CSC and CRE related congestion will not affect Congestion Zone definition or composition, nor will they affect CSC definitions.
ERCOT shall present modifications proposed to the list of CREs or the approved list of contingencies for managing CSC and CRE related congestion after the start of the year to TAC for approval.
TAC will have seven (7) days to take action on the proposed modification. If TAC takes no action within seven (7) days, the proposed modification shall be deemed approved.

## Slide 4: Need for additional CREs
Protocols are silent about using zonal congestion to manage stability limits
Market notice (M-B012908-01) issued in January described how ERCOT will use zonal congestion management to not violate stability limits
PRR764 clarified language related to the use of zonal congestion management to handle particular contingencies and overloaded elements
  No mention of zonal CM being appropriate to maintain stability limits
Since PRR764 implementation ERCOT has OOME’d units to maintain stability limits (6 days)

## Slide 5: ERCOT West-to-North Stability Limit
“Why” do we need to have West-North transfer stability limit?
  Potential inter-area oscillation may cause units in the West and South have large oscillations and trip during disturbances which degrade system reliability and lead to firm load shed or islanding.
“What” is the concern with system oscillation?
  Many static exciters in system are designed to help voltage regulation, but also induce “undesired” negative damping, which may cause oscillation during system disturbance.
“When” do we need to consider system oscillation?
  Weak transmission links and heavy power transfers.
“How” do we prevent system from undesired oscillation?
  Have Power System Stabilizers in service.
  Limit the power transfer across the weak link.
The WN stability limit is updated periodically or if there is a significant change in the system topology.

## Slide 6: West-to-North Stability Interface
Monitoring Elements:
  Selected machines in West Texas and South Texas were monitored for speed deviations
West to North Interface:
  Bowman to Jacksboro,
  Bowman to Graham,
  Tonkawa to Graham,
  Sweetwater to Graham,
  Long Creek to Graham,
  Red Creek to Comanche,
CSC

## Slide 7: W-N Transient Stability Limit
An annual stability study is performed which includes about 500 scenarios which are most credible for analysis.
Using the scenarios from this study, real time conditions are continually monitored to determine which limit is currently in effect.
Operators can set a CSC transfer limit based on the flows on the 6 monitored lines.
ERCOT proposes to resume using deployments of zonal BES to control CSCs flow as a proxy limit for when the stability limit is reached. This will have the effect of deploying Resources in both the West and North zones, similar to when the CSC is thermally limited. ERCOT believes this to be the quickest and most effective method for maintaining the West to North flow below the transient stability limit.

## Slide 8: ERCOT North-to-Houston Stability Limit
ERCOT runs a voltage stability analysis of the North to Houston transfer once every hour.
ERCOT studies 3 transfer scenarios to analyze the voltage stability for the Houston region
  Increase generation outside Houston - Increase load in Houston
  Increase generation in North – Increase load in Houston
  Increase generation in North – Decrease generation in Houston
The lowest of the 3 limits calculated for the different transfers will be used to constrain the North to Houston transfer.
The interface for the North to Houston includes the four 345 KV lines
  Jewett to TH Wharton
  Jewett to Tomball
  Gibbons Creek to O’Brien
  Roans Prairie to Kuykendahl

## Slide 9: ERCOT Proposes the addition of two ‘Combinatorial’ CREs
Sum of flows on these six lines:
  LONG CREEK SWITCHING STATION – GRAHAM SES (345KV double circuit)
  TONKAWA SWITCH – GRAHAM SES (345KV)
  BOWMAN SWITCH – GRAHAM SES (345KV)
  BOWMAN SWITCH – JACKSBORO SWITCHING (345KV)
  SAN ANGELO CREEK – COMANCHE SWITCH TU (345KV)
Sum of flows on these four lines:
  Jewett to TH Wharton
  Jewett to Tomball
  Gibbons Creek to O’Brien
  Roans Prairie to Kuykendahl