## Slide 1: American Electric Power Service Corporation Presidio Area Reliability Improvements Project
James Teixeira
Manager, Regional Planning

## Slide 2: Description of Recommendation
Presidio Area
Install a second 138/69 kV autotransformer at Alamito Creek substation in 2008.
Cost: $4,000,000
Install two 2.4 MW NaS battery units at Presidio in 2009.
Cost: $15,000,000
Replace existing 69 kV line with new 69 kV line designed for 138 kV operation from Alamito Creek to Chinati to Presidio in 2012.
Cost: $48,000,000
TOTAL COST: $67,000,000

## Slide 3: Project Need - Reliability Analysis
Install a second 138/69-kV autotransformer at Alamito Creek Substation
  Necessary to meet NERC criteria under maintenance conditions during load periods when maintenance is normally performed.
Install a 4.8 MW NaS battery at Presidio Substation
  The line can not be rebuilt until end of 2010 at the earliest and voltage criteria exceeded in 2009 pre and post-contingency.
  The battery is a short term solution that allows area voltages to meet NERC/ERCOT pre and post-contingency voltage limits as soon as possible and can serve most of the area load when the 69-kV line in not available.
  Allows rebuild of 69 kV line to be delayed until 2012 because battery alone can provide adequate voltage support until 2012.

## Slide 4: Project Need - Reliability Analysis continued
Construct a new Alamito Creek-Presidio 69-kV line (built for 138-kV service)
  provides long term solution and capacity for expansion.
  Existing line was built in 1948 as 33 kV line using conductor that is used for residential service today.
  Existing construction is all wooden and failing at an “unacceptable rate”.
  Extremely rough terrain makes maintenance costly and lengthy.
  Losses on existing line adds to low voltage problems
    R approximately 2 times greater than X
    Losses equal to 1.5 MW to serve 6.8 MW of load (22% compared to system wide 2.3%)
  Needed to meet NERC criteria and provide reliable transmission service to rural communities as mandated in PURA §38.005.

## Slide 5: Alternatives Considered
Installation of a small asynchronous tie with CFE
  10 MW VSC asynchronous tie would have comparable cost
  estimated to take two additional years to install.
  can not be scaled up to a size that would be more commercially significant in the future. It would have to be completely replaced.
  A 100 MW VFT asynchronous tie would be more than twice the cost and still not be in place for an additional two years or longer.
Installation of 10 MW Diesel Generation
  regulated transmission provider can not provide generation services such as RMR.
  Generation services must be provided by an unregulated market participant.
Block load transfer to CFE
  requires the load in the area to be subject to outages before and after block load transfer to CFE occurs.
  the block load tie to CFE is unable to serve the entire load.

## Slide 6: Alternatives Considered Continued
Addition of Static Capacitors
  Two 3.6 MVar banks had to be installed at both Presidio and Chinati to relieve post-contingency voltage violation.
  Mvar flow opposite to MW flow causes thermal overload of Alamito to Bryant Ranch segment.
  Does not address power quality issue.

## Slide 7: Stakeholder Review
The Stakeholder review period for this project was held in April 2008
Comments received include (from one entity):
  $ 67 M for 10 MW load compared to ERCOT average $ 2 M for 10 MW (accuracy of calculation unknown)
  Consider Alternatives such as Diesel Gen, DC Tie, etc.
  Precedent for radial load service could increase transmission costs substantially

## Slide 8: ERCOT Support for the Project
ERCOT will be requesting that the Presidio Area Reliability Improvements project be endorsed by the ERCOT Board Of Directors.

## Slide 9
Questions?