## Slide 1: Unannounced Generation Capability Testing
Temp Range | Date of Test: | QSE: | CONFIGU-RATION | NUMBER OF UNITS | Ambient Temperature | TYPE | MW at Start of Test (MW) | Seasonal HSL(MW) | Resource Plan HSL (MW) | 30 Minute sustained (MW) | HSL Reached and Sustained | HSL Reached but not Sustained | HSL not Reached
< 85 F | 4/4/2008 | QSEA | UNIT | 1 | 68 | TEST | 552 | 553 | 553 | 552 | NO | NO | Y
 | 5/15/2008 | QSEB | UNIT | 1 | 70 | TEST | 197 | 250 | 222 | 227 | Y |  | 
 | 5/15/2008 | QSEB | UNIT | 1 | 70 | TEST | 205 | 250 | 220 | 227 | Y |  | 
 | 5/15/2008 | QSEB | UNIT | 1 | 70 | TEST | 205 | 250 | 228 | 228 | Y |  | 
 | 5/15/2008 | QSEB | UNIT | 1 | 70 | TEST | 232 | 250 | 232 | 233 | Y |  | 
 | 5/12/2008 | QSEA | UNIT | 1 | 72 | TEST | 71 | 412 | 412 | 417 | Y |  | 
 | 5/27/2008 | QSEL | CCY | 3 | 72 | TEST | 642 | 707 | 675 | 666 | NO | Y | 
 | 5/16/2008 | QSEC | UNIT | 1 | 73 | TEST | 201 | 502 | 502 | 506 | Y |  | 
 | 4/17/2008 | QSEC | UNIT | 1 | 74 | TEST | 288 | 530 | 530 | 519 | NO | NO | Y
 | 5/15/2008 | QSED | CCY | 3 | 74 | TEST | 300 | 525 | 522 | 519 | NO | Y | 
 | 5/15/2008 | QSEE | CCY | 3 | 75 | TEST | 308 | 491 | 498 | 498 | Y |  | 
 | 4/3/2008 | QSEF | UNIT | 1 | 75.8 | TEST | 430 | 543 | 559 | 537 | NO | NO | Y
 | 4/11/2008 | QSEG | CCY | 7 | 76 | TEST | 325 | 571 | 510 | 482 | NO | NO | Y
 | 5/14/2008 | QSEH | CCY | 3 | 79.34 | TEST | 370 | 487 | 424 | 430 | Y |  | 
 | 4/11/2008 | QSEG | CCY | 7 | 81.4 | RETEST | 421 | 482 | 476 | 485 | Y |  | 
 | 4/7/2008 | QSEB | UNIT | 1 | 82 | TEST | 313 | 413 | 413 | 428 | Y |  | 
 | 4/23/2008 | QSEC | UNIT | 1 | 83 | RETEST | 65 | 519 | 519 | 524 | Y |  | 
 | 5/14/2008 | QSEI | UNIT | 1 | 83 | TEST | 55 | 347 | 347 | 347 | Y |  | 
 | 5/13/2008 | QSEJ | CCY | 2 | 83.2 | TEST | 331 | 546 | 528 | 530 | Y |  | 
85 F to 95 F | 6/6/2008 | QSEA | UNIT | 1 | 87 | TEST | 421 | 439 | 439 | 424 | NO | NO | Y
 | 6/22/2008 | QSEP | CCY | 3 | 87 | TEST | 174 | 210 | 212 | 214 | Y |  | 
 | 5/28/2008 | QSEM | UNIT | 1 | 89 | TEST | 55 | 110 | 110 | 109 | NO | NO | Y
 | 6/6/2008 | QSEF | UNIT | 1 | 90 | TEST | 100 | 174 | 172 | 169 | NO | NO | Y
 | 5/9/2008 | QSED | UNIT | 1 | 91 | TEST | 96 | 330 | 329 | 323 | NO | NO | Y
 | 6/4/2008 | QSEN | CCY | 3 | 91 | TEST | 340 | 389 | 361 | 364 | Y |  | 
 | 5/15/2008 | QSEK | CCY | 3 | 92 | TEST | 92 | 467 | 454 | 458 | Y |  | 
 | 5/20/2008 | QSEF | UNIT | 1 | 92 | TEST | 610 | 745 | 749 | 735 | NO | NO | Y
> 95 F | 6/24/2008 | QSEO | CCY | 4 | 97 | TEST | 722 | 728 | 750 | 762 | Y |  | 

## Slide 2: Summary of Unannounced Generation Capability Testing
TEMPERATURE | UNITS TESTED | HSL REACHED AND SUSTAINED | HSL NOT SUSTAINED
< 85 F | 40 | 24 | 16
85 F - 95 F | 14 | 9 | 5
> 95 F | 4 | 4 | 0