## Slide 1: Early Delivery Systems Status – R6.3 2 Hour Test
John Dumas and Jeff Gilbertson

## Slide 2: Agenda
EDS 3
  Release 5 & 6: SCED / LFC
    2-Hour Total System Test Results
      Test Chronology
      LFC Review
      Constraints
      State Estimator
      System Items of Note
    Future of LFC and SCED Testing

## Slide 3: Agenda
EDS 3
  Release 5 & 6: SCED / LFC
    2-Hour Total System Test Results
      Test Chronology
      LFC Review
      Constraints
      State Estimator
      System Items of Note
    Future of LFC and SCED Testing

## Slide 4: Test Chronology – June 25, 2008
08:00 Taylor Control Room Hotline announcement of EDS 3 LFC R6.3 2 Hour Test to Start at 11:00
09:00 ERCOT discontinues the use of Zonal Congestion Management Techniques (No OC1s in effect at the time)
10:50 Taylor Control Room Hotline announcement of EDS 3 LFC R6.3 2 Hour VDI effective Market Wide at 11:00 AM
11:00 Taylor Control Room Issues first Zonal to Nodal Switching Order
12:18 Last QSE Confirms Switch to Nodal
12:18 – 12:47 ERCOT manages Grid Control via Nodal
12:47 First QSE confirms switch back to Zonal
13:37 Last QSE confirms switch back to Zonal
14:40 ERCOT resumes the use of Zonal Congestion Management Techniques
15:00 VDI Ended

## Slide 5: LFC CPS1 Scores
CPS1 Score (1 Min.) Average | 
All in Zonal (900-1106) | 107.27
Transition to Nodal (1107-1217) | 111.25
All in Nodal (1218-1247) | 159.92
Transition to Zonal (1248-1337) | 120.04
All in Zonal (1338-1530) | 125.27

## Slide 6: LFC Regulation, Total Load and Total Generation

## Slide 7: LFC Transition Time and Nodal Operation Duration

## Slide 8: Constraints
Nodal RTCA & Zonal RTCA showed the same contingency violations.
Constraints in effect from 9:30 and throughout the test:
Austrop Transformer
  Loss of #2 Austrop 345/138kV transformer overloads #1 Austrop 345/138kV transformer
  Due to Generation Topology
Brownwood Switch
  Loss of 345kV Temple Switch to Lake Creek & Temple Pecan Creek to Tradinghouse double circuit overloads Brownwood Switch to Goldthwaite 138kV line
  A CRE for the North to South (Zonal) corridor

## Slide 9: State Estimator Convergence (15 MW/30 MVAR Mismatch Tolerance)
09:37 - Large change in breaker status that went from closed to open due to a QSE’s ICCP data failure, impacted hour ending 10.
10:30 - RTU went down impacting telemetry from 3 units, impacted hour ending 11.

## Slide 10: Limits during test period 6/25, 11am – 1pm
GTBD within 2000-3000MW of HDL (plenty of room).
LEL > LSL for all but four intervals of test – check your telemetered LEL and LSL

## Slide 11: Reference LMP, Max LMP, Min LMP
Two constraints implemented for entire test – limits not reached until halfway through test
Reference LMPs steady increase from $95 to $122
Temporary Max/Min LMP reduction at 12:35; transformer constraint not at limit briefly

## Slide 12: Distribution of Prices with Line Constraint (12:30)
288 of 433 (66%) Resource node LMPs at $109.11
Max $1,388; Min -$425

## Slide 13: Reference LMP, GTBD, SPP, Zonal MCPE (6/25)
Reference LMP comparable to MCPE (Zonal MCPE same in all Zones throughout test)
Maximum difference of $14 between LMP and MCPE at beginning of test
Differences between LMP/SPP/MCPE $0-$10 throughout test, except for South Zone

## Slide 14: System Items of Note
Permissive Control for UDBP was not in effect
RLC p1 parameter set at 1.0 which affects operation below the LSL (will change to 0.9)
Regulation Reduction was in effect and will need further tuning before next LFC test
SCED issue identified and to be corrected before next test (memory issue)
No off cycle SCED runs executed
Combined Cycle Configuration Validation Check was not effect

## Slide 15: Agenda
EDS 2
  Release 3: Telemetry & State Estimator
EDS 3
  Release 5 & 6: SCED / LFC
    2-Hour Total System Test Results
      Test Chronology
      LFC Review
      Constraints
      State Estimator
      System Items of Note
    Future of LFC and SCED Testing

## Slide 16: Near-Term Future of State Estimator
MW and MVar tolerance set to 15 on July 1 based on last ½ of June results (~91% Convergence)
Staffing shift engineers in 24-hr incremental blocks in August to drive SE issues and build toward 24x7 real-time operations
  ‘Blackout’ will be communicated to MPs and all efforts should be made to keep systems running and accurate
  On non-blackout dates ERCOT will continue to monitor 8x5
These efforts will position ERCOT and MPs well for an 8-Hour LFC test in Mid-September
  With or without CIM
  A longer test is needed for MPs and ERCOT to tune their systems

## Slide 17: 8 Hour Test
Preparation activities for 8 Hour Test
ERCOT Publish LFC 2 Hour Test Report
Resolve SCED memory issue
Further LFC tuning efforts
Work with MP’s towards State Estimator and Telemetry Standard compliance
Works with MP’s towards a 24 X 7 Nodal operation support (ICCP)
Schedule LFC Phase 3 Test Work Shop
Schedule Blackout Days for State Estimator convergence testing
Schedule LFC 8 hour test

## Slide 18: Near-Term Future of SCED
ERCOT proposal for Real-Time submissions until re-plan is complete
  ERCOT will continue to run SCED / Post Real-Time LMPs
    QSEs continue TPO submittals up to 30-days in advance
      TPO’s should continue to cover 80-120% of cost
      Min Energy / Startup Costs may be 0.00 since no DAM/RUC execution
      FIP / FOP % must still continue to = 100% combined
    COP will only be required in the case of using an output schedule
      Output schedules use the sustainable limits in the COP for validation
      In this circumstance, COP’s updates are not required in Adjustment Period
  ICCP
    ICCP must continue to be in place 24/7 to support State Estimator and basic SCED input values
      Basic data required include configuration, MW output, breaker status, HSL, LSL.
      Ancillary Services not required (zero for AS Schedules and Responsibility)
    ICCP data quality must continue to be monitored and problems resolved
    These are the ongoing requirements communicated to the market from November of 2007
  ERCOT will implement 24/7 constraint management in nodal systems starting 7/5