# 2008 CRE Recommendation

July 10, 2008

Version 1.1

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |
| 07/07/2008 | 1.0 | First draft | Isabel Flores |
| 07/10/2008 | 1.1 | Incorporated group comments | Isabel Flores |

Table of Contents

1.	Background	1

2.	Analysis	1

3.	Recommendation	2

4.	Concerns & Potential Risks	3

5.	Attachments	3

# 2008 CRE Recommendation

# Background

As a result of PRR764 and as requested by Market Participants, ERCOT performed an analysis of the 2008 CREs to determine the effectiveness of each Closely Related Element (CRE) in resolving zonal congestion.  ERCOT used a Power Transfer Distribution Factors (PTDF) analysis to meet this request.  On June 19, 2008, ERCOT presented its analysis to the Congestion Management Working Group for its review and discussion.

Luminant Energy also submitted its Average Weighted Shift Factor (AWSF) analysis for consideration and suggested a 5% shift-factor cut-off for 138 kV lines and 10% shift-factor cut-off for 345kV lines.

# Analysis

Market Participants also discussed analyzing specific contingency and element pairs to determine their effectiveness in resolving Zonal Congestion.  ERCOT performed its PTDF analysis for each specific pair, and presented the results to CMWG.  It is, however, currently not possible to implement in this manner in the ERCOT systems.  Below are the PTDFs for each CRE under Base Case (no contingency) conditions..  The PTDF for all contingency and overloaded element combinations of CSCs and CREs may be found in the attached file.  ERCOT believes that the PTDF analysis conducted has yielded similar results as those presented by Luminant Energy in its analysis and has used the PTDF to make its recommendation.

North to South and South to North:

| Element | Contingency | PTDF |
| --- | --- | --- |
| CSC_3 | Base Case | 36 |
| BRNWDSW_8_L_GOLDTH8_1Y_138_Line | Base Case | 3.1 |
| THOUSE__5_LAKE_CRK1_5_345_Line | Base Case | 6.7 |
| LAKE_CRK1_5_TEMP_SS__5_345_Line | Base Case | 19.9 |
| LAKE_CRK1_8_TEMP_PEC__8_138_Line | Base Case | 2.6 |
| THOUSE__5_TEMP_PEC__5_345_Line | Base Case | 17.7 |
| TEMP_PEC__5_TEMP_SS__5_345_Line | Base Case | 17 |
| TEMP_SS__8_ROGERS1A_8_138_Line | Base Case | 2.3 |
| TEMP_PEC__8_TEMP_SS__8_138_Line | Base Case | 2.8 |
| SANDOW1_8_ELGIN_SS__8_138_Line | Base Case | 2.6 |
| SANDOW1_8_SALTY_P_8_138_Line | Base Case | 2.6 |
| SANDOW__5_L_AUSTRO5_1Y_345_Line | Base Case | 18 |
| L_AUSTRO5_1Y_L_ZORN__5_2Y_345_Line | Base Case | 9.5 |
| L_AUSTRO5_1Y_L_GARFIE5_1Y_345_Line | Base Case | 12.1 |
| SAND_TXU_5_L_AUSTRO5_1Y_345_Line | Base Case | 17.8 |
| L_EVANT_8_1Y_L_ADAMSV8_1Y_138_Line | Base Case | 2.7 |
| L_GOLDTH8_1Y_L_EVANT_8_1Y_138_Line | Base Case | 2.7 |
| ROGERS1A_8_SANDOW1_8_138_Line | Base Case | 2.3 |
| THOUSE__5_LAKE_CRK2_5_345_Line | Base Case | 7.9 |

West to North and North to West:

| Element | Contingency | PTDF |
| --- | --- | --- |
| CSC_1 | Base Case | 34.9 |
| TONKAWAWI_5_GRAHAMSES1_5_345_Line | Base Case | 13.9 |
| MURRY_P8_GRAHAMSES1_8_138_Line | Base Case | 3.5 |
| SWEETWTR_5_GRAHAMSES1_5_345_Line | Base Case | 13.9 |
| WILLOWCK_5_JACKSBRO_5_345_Line | Base Case | -14.9 |
| WILLOWCK_5_PARKER_5_345_Line | Base Case | 12.1 |
| FISHRDSS1_5_BOWMAN_5_345_Line | Base Case | 9.2 |
| BOWMAN_5_JACKSBRO_5_345_Line | Base Case | 9.6 |
| OKLA7A_FISHRDSS1_5_345_Line | Base Case | 10.7 |
| JACKSBRO_5_W_DENT_5_345_Line | Base Case | 11.5 |
| GRAHAMSES1_5_JACKSBRO_5_345_Line | Base Case | 16.9 |
| GRAHAMSES1_5_BENBRK_5_345_Line | Base Case | 16.3 |
| GRAHAMSES1_8_GRAHAME_8_138_Line | Base Case | 2.4 |
| LONGCREK_5_GRAHAMSES1_5_345_Line | Base Case | 23.9 |
| ABMULCE7_LONGCREK_5_345_Line | Base Case | 13.1 |
| PARKER_5_BENBRK_A_T5_345_Line | Base Case | 8.1 |
| COMCHESS1_5_COMCHPKW_5_345_Line | Base Case | 16.7 |
| SARC7A_COMCHESS1_5_345_Line | Base Case | 17.1 |
| LKAROWHD_8_NEWPRT_P8_138_Line | Base Case | 2.5 |
| GRAHAMSW_8_BARTON_8_138_Line | Base Case | 2.5 |
| GRAHAME_8_GRAHAMSW_8_138_Line | Base Case | 2.4 |
| BARTON_8_ORAN1_8_138_Line | Base Case | 4.6 |
| LEONSW_8_FLATCRK_T8_138_Line | Base Case | 3.3 |
| LINGLVLL_P8_STPHNVIL_8_138_Line | Base Case | 3.3 |
| FLATCRK_T8_LINGLVLL_P8_138_Line | Base Case | 3.3 |
| PAIP4B_MURRY_P8_138_Line | Base Case | 3.5 |
| BLF_CRK7A_ABMULCE7_345_Line | Base Case | 9 |

North to Houston:

| Element | Contingency | PTDF |
| --- | --- | --- |
| CSC_4 | Base Case | 34 |
| GIBN_CREK_5_OBRIEN__345A_345_Line | Base Case | 16.1 |
| JEWETT_N5_TOMBAL__345B_345_Line | Base Case | 18 |
| JEWETT_S5_T_H_W___345B_345_Line | Base Case | 17.9 |
| KUYDAL745005_KING____345A_345_Line | Base Case | 11.5 |
| KUYDAL755010_KING____345A_345_Line | Base Case | 15.3 |
| L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | Base Case | 1.2 |
| ROANS___345C_KUYDAL755010_345_Line | Base Case | 15.3 |
| TOMBAL__345B_KUYDAL745005_345_Line | Base Case | 11.5 |

# Recommendation

ERCOT recommends applying a 3% PTDF threshold to determine the effectiveness of using zonal balancing to manage a particular constraint.  ERCOT has reviewed all PTDF results and the potential generators that could be used to resolve the congestion were local tools to be implemented.  When both local and zonal results were similar ERCOT recommends using zonal methods in order to directly assign the associated costs.

Based on this analysis, ERCOT recommends that the following lines should no longer be considered CREs.  ERCOT believes that establishing a 3% standard is in line with the current 3% trigger that is used for local congestion.

| CSC | Element | PTDF |
| --- | --- | --- |
| S_N & N_S | SANDOW1_8_ELGIN_SS__8_138_Line | 2.6 |
| S_N & N_S | SANDOW1_8_SALTY_P_8_138_Line | 2.6 |
| S_N & N_S | ROGERS1A_8_SANDOW1_8_138_Line | 2.3 |
| W_N & N_W | GRAHAMSES1_8_GRAHAME_8_138_Line | 2.4 |
| W_N & N_W | LKAROWHD_8_NEWPRT_P8_138_Line | 2.5 |
| W_N & N_W | GRAHAMSW_8_BARTON_8_138_Line | 2.5 |
| W_N & N_W | GRAHAME_8_GRAHAMSW_8_138_Line | 2.4 |
| N_H | L_WALLER8_1Y_L_PRAIVI8_1Y_138_Line | 1.2 |

Notes:  PTDFs shown are for Base Case conditions.

# Concerns & Potential Risks

In performing its analysis ERCOT has identified these concerns:

- With the removal of certain CREs, coal units may be the most effective generation to reduce to resolve congestion using local methods.

- In situations where several generators have equal effectiveness, using local congestion management tools may lead to significant loss of Ancillary Service capacity.

# Attachments

PTDF analysis of 2008 CREs: