# 2009 CSC Study

Version 2.0

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |
| 07/02/2008 | 1.0 | First draft | Jeff Billo |
| 07/09/2008 | 1.1 | Draft – added scenario 4 | Jeff Billo |
| 07/09/2008 | 1.2 | Draft – added 2008 congestion data and minor edits | Isabel Flores |
| 07/10/2008 | 1.3 | Add scenario 5 and congestion costs | Isabel Flores |
| 07/16/2008 | 2.0 | Add scenarios 3a, 3b, 3c, 3d, 3e | Jeff Billo |

Table of Contents

2009 CSC Study	1

1.	Background	1

2.	2009 Significant Changes to the ERCOT grid	1

3.	Transfer Study	1

4.	Evaluation of Current Congestion Events	2

5.	Projection of Future Congestion	4

6.	Cluster Analysis	5

6.1.	Scenario 1	6

6.2.	Scenario 2	7

6.3.	Scenario 3	8

6.4.	Scenario 3a	9

6.5.	Scenario 3b	10

6.6.	Scenario 3c	11

6.7.	Scenario 3d	12

6.8.	Scenario 3e	13

6.9.	Scenario 4	14

6.10.	Scenario 5	15

6.11.	Cluster Analysis Discussion	15

# 2009 CSC Determination Study

# Background

Protocol Section 7.2.1 requires ERCOT Staff to conduct an annual analysis to determine the upcoming year’s Commercially Significant Constraints (CSCs).  This analysis may include a transfer study, an evaluation of past congestion costs, and a projection of congestion costs for the upcoming year; ERCOT’s analysis includes all of these features.

# 2009 Significant Changes to the ERCOT grid

Per the May 2008 TPIT, these are the significant transmission projects scheduled to go in-service by the end of 2009:

- Jack Creek 345/138-kV substation and associated projects (Sept. 2008)

- Brownwood-Goldthwaite 138-kV line reconductor (Dec. 2008)

- Singleton Switch (May 2009)

- Waller-Prairie View-Seaway-Macedonia 138-kV line upgrade (Sept. 2009)

- West Levee-Norwood 345-kV line (Dec. 2009)

- Leon-Flat Creek 138-kV line upgrade (Dec. 2009)

Generation projects scheduled to go in-service by the end of 2009:

- Victoria Power Station (July 2008)

- Bosque Expansion (Mar. 2009)

- Dansby 3 (Apr. 2009)

- VH Braunig Peakers (May 2009)

- Oak Grove 1 (July 2009)

- Sandow 5 (July 2009)

- Winchester (July 2009)

- Sandhill Peakers (Nov. 2009)

- 7981 MW (total) of west Texas wind, 173 MW of north Texas wind, and 590 MW of south Texas wind scheduled to be in-service by the end of 2008

- 8206 MW of west Texas wind, 173 MW of north Texas wind, and 688 MW of south Texas wind scheduled to be in-service by September 2009

# Transfer Study

The Steady State Working Group (SSWG) 2009 Data Set A 2009 summer peak base case was used for the transfer analysis.  A congestion management (CM) zone to CM zone transfer analysis was performed by mapping all generators to their respective 2008 CM zones.  New generation units were mapped to their assumed CM zone.

Transfer analysis was performed for the following zone to zone generation transfers:

- West to North

- South to North

- North to South

- North to Houston

- North to West

The Singleton Switch Station was included in the base case because it is scheduled to be in-service by May 2009.  However, since it will not be in-service for all of 2009 a second transfer analysis was performed.  The base case was modified by removing the Singleton Switch Station and replacing the connected branches with the existing branch data for the Jewett-Tomball, Jewett-TH Wharton, Gibbons Creek-Roans Prairie, and Gibbons Creek-Obrien 345-kV lines.  The North to Houston transfer study was rerun on the modified base case.

The results of the transfer studies are presented in the attached spreadsheet:

# Evaluation of Current Congestion Events

The table below is an estimate of costs assigned to contingency and overloaded elements based on those identified when determining CSC limits:

| CSC | Contingency | Overloaded Element | Costs | % of total |
| --- | --- | --- | --- | --- |
| N_H | DCKT Jewett - TH Wharton & Tomball 345kV | Watson Chapel - Robertson 138kV | $59,822,113.66 | 66.52% |
| N_S | DCKT Temple Creek - Trading House & Temple Switch - Lake Creek 345kV DCKT Temple Switch – Lake Creek & Temple Pecan Creek 345 kV | Watson Chapel - Robertson 138kV Temple Pecan Creek – Temple 138kV | $30,914,645.57 | 42.48% |
| N_S | DCKT Temple Creek - Trading House & Temple Switch - Lake Creek 345kV | Lorena - Waco West 69 kV | $6,175,256.24 | 8.49% |
| N_S | DCKT Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345kV | Watson Chapel - Robertson 138kV | $3,497,318.90 | 4.81% |
| N_S | DCKT Temple Switch - Lake Creek & Temple Pecan Creek 345 kV | Temple Pecan Creek - Temple 138kV | $ 2,999,633.29 | 4.12% |
| N_S | DCKT Temple Creek - Trading House & Temple Switch - Lake Creek 345kV | Waco - Waco West 69kV | $1,615,205.93 | 2.22% |
| N_S | DCKT Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek 345kV | Waco West - Waco Woodway 138kV | $1,415,734.42 | 1.95% |
| N_S | DCKT Temple Creek - Trading House & Temple Switch - Lake Creek 345kV | Temple Creek - Temple Switch 138kV | $932,185.42 | 1.28% |
| N_S | DCKT Sandow - Temple 345 kV | Killeen Clark Road – Copperas Cove 138kV | $932,185.42 | 1.28% |
| N_S | DCKT Austrop - Sandow SW 345kV | Sandow SW - Salty 138kV | $90,688.89 | 0.12% |
| N_S | DCKT Temple Creek - Trading House & Temple Switch - Lake Creek 345kV | Waco Woodway - Waco West 138kV | $ 63,462.48 | 0.09% |
| N_W | SCKT San Angelo Red Creek - Comanche Switch 345kV | Flat Creek - Leon Switch 138kV | $6,125,626.21 | 52.43% |
| N_W | DCKT Comanche Switch - San Angelo Red Creek 345kV | Flat Creek - Leon Switch 138kV | $1,608,457.00 | 13.77% |
| N_W | DCKT Graham - Benbrook & Parker 345kV | Flat Creek - Leon Switch 138kV | $1,263,529.13 | 10.82% |
| S_N | DCKT Zorn - Austrop & Lytton Spring 345kV | Canyon - Rohr 138kV | $(13,486,519.15) | 73.81% |
| W_N | SCKT Fisher Road - Oklaunion & Bowman 345kV | Graham - Long Creek 345kV | $47,774,440.25 | 64.36% |
| W_N | SCKT Fisher Rd - Bowman 345kV | Abilene South - Putnam 138kV | $7,498,835.67 | 10.10% |
| W_N | SCKT Fisher Rd - Oklaunion & Bowman 345kV | Graham -Murray 138kV | $2,227,997.54 | 3.00% |
| W_N | DCKT Graham - Sweetwater & Long Creek 345kV | Abilene South - Putnam 138kV | $1,755,511.34 | 2.36% |
| W_N | SCKT Fisher Road - Oklaunion & Bowman 345kV | Bomarton - Seymour 69kV | $1,258,758.69 | 1.70% |
| W_N | SCKT Tonkawa Switch - Graham 345kV | Abilene South - Putnam 138kV | $630,863.91 | 0.85% |

This year for the January through May timeframe these are the top congested contingency and overloaded element pairs:

| Contingency | Overloaded Element | total - ytd |
| --- | --- | --- |
| Comanche Peak SES- Decordova SES & Wolf Hollow - Rocky Creek 345KV | Concord 345/138KV Autotransformer | 8 |
| Menard - Gillespie 138KV | Menard autotransformer 1 | 7 |
| North Edinburg - Rio Hondo 345kV | South McAllen - Stewart Road 138kV | 7 |
| Temple Switch - Killeen Switch & Sandow Switch 345kV | Killeen Switch - Harker Heights South | 7 |
| Austrop 345/138kV auto #2 | Austrop 345/138kV Auto #1 | 6 |
| Decker - McNeil & Dessau - Daffin 138KV | Decker - Sprinkle 138KV | 6 |
| Matador – Paducah Clare Street 69kV | Girard Tap – DKEC Jayton 69kV | 6 |
| Matador - Paducah Clare Street/ SPUR 69kV | Matador - Paducah REA Tap 69kV | 6 |
| Morgan Creek SES – Quail SW & Odessa EHV 345kv | Big Springs SW – Big Spring West 138kV | 6 |
| North Edinburg - Rio Hondo 345kV | South McAllen - Las Milpas 138kV | 6 |
| Odessa EHV - Morgan Creek SES - Quail Switch 345kV | Morgan Creek SES - Cal Energy 345kV | 6 |
| San Angelo Red Creek 345/138kV Auto #1 | San Angelo Red Creek 345/138kV Auto #2 | 6 |
| Spur 138/69kV Auto #1 | Spur - Girard Tap 69kV | 6 |

Note: counts provided are for the number of days these pairs appeared as congested.

For the period January through June, 2008, these are the top ten congested contingency and overload element pairs thus far:

| Contingency | Overloaded Element | Estimated Cost |
| --- | --- | --- |
| Moss - Holt 138kV | Odessa North - North Cowden 69kV | $992,273 |
| Menard - Gillespie 138kV | Menard 138/69KV Transformer | $918,948 |
| Austrop – Sandow 345kV | Milano-Minerva area potential voltage collapse | $630,529 |
| Temple Pecan Creek - Tradinghouse - Lake Creek 345kV | Ridge - Watson Chapel 138kV | $563,443 |
| Calaveras - Skyline & Walzem Road 138kV | Calaveras – Ball Park 138kV | $562,468 |
| Morgan Creek SES - CAL Energy 345kV | Big Springs Switch - Big Spring West 138kV | $512,003 |
| Trinidad - Stryker Creek & Mt. Enterprise 345kV | Athens – Elkton 138kV | $479,106 |
| San Angelo Red Creek – Bluff Creek 345kV | Abilene Mulberry Creek East Reactor Series 138kV | $445,831 |
| Fisher Road – Oklaunion & Bowman 345kV | Lake Pauline Autotransformer 138/69kV | $386,078 |
| Austrop 345/138kV Autotransformer #1 | Austrop 345/138kV Autotransformer #2 | $343,624 |

Note: dollars shown are estimates and not Settlement quality.

# Projection of Future Congestion

The attached spreadsheet contains the 2009 annual congestion report from the 2007 Five-Year Plan.  The elements are sorted based on shadow price.

# Cluster Analysis

Cluster analysis was performed on the base case and the modified base case with the Singleton Switch Station removed.  Below are the scenarios studied.

## Scenario 1

Scenario 1 was clustered using the modified base case with the Singleton Switch Station removed.  The 2008 CSCs were used and the model was clustered into four zones.

## Scenario 2

Scenario 2 was clustered using the base case (with Singleton Switch Station).  The 2008 CSCs were used with the exception that the North to Houston CSC was represented by the Jewett-Singleton 345-kV double circuit.  The model was clustered into four zones.

## Scenario 3

Scenario 3 was clustered using the base case (with Singleton Switch Station).  The 2008 CSCs were used with the exception that the North to Houston CSC was represented by the Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit.  The model was clustered into four zones.

## Scenario 3a

Scenario 3a was clustered using the base case (with Singleton Switch Station).  The 2008 CSCs were used with the following exceptions: (1) the North to Houston CSC was represented by the Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit; (2) a West-South CSC was represented using the Goldthwaite-Evant 138-kV line.  The Goldthwaite-Evant 138-kV line was chosen since it is the only section of the Brownwood-Lampasas 138-kV line that is not scheduled to be upgraded by the end of 2008.  The model was clustered into four zones.

## Scenario 3b

Scenario 3b was clustered using the base case (with Singleton Switch Station).  The 2008 CSCs were used with the following exceptions: (1) the North to Houston CSC was represented by the Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit; (2) the North to South/ South to North CSCs were represented using the Lake Creek-Temple/ Tradinghouse-Temple Pecan Creek 345-kV double circuit.  The model was clustered into four zones.

## Scenario 3c

Scenario 3c was clustered using the base case (with Singleton Switch Station).  The 2008 CSCs were used with the following exceptions: (1) the North to Houston CSC was represented by the Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit; (2) the North to South/ South to North CSCs were represented using the Lake Creek-Temple/ Tradinghouse-Temple Pecan Creek 345-kV double circuit; (3) a West-South CSC was represented using the Goldthwaite-Evant 138-kV line.  The model was clustered into four zones.

## Scenario 3d

Scenario 3d was clustered using the base case (with Singleton Switch Station).  The 2008 CSCs were used with the following exceptions: (1) the North to Houston CSC was represented by the Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit; (2) the North to West/ West to North CSCs were represented using the Sweetwater-Long Creek/ Abilene Mulberry Creek-Long Creek 345-kV double circuit.  The model was clustered into four zones.

## Scenario 3e

Scenario 3e was clustered using the base case (with Singleton Switch Station).  The 2008 CSCs were used with the following exceptions: (1) the North to Houston CSC was represented by the Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit; (2) the North to West/ West to North CSCs were represented using the Sweetwater-Long Creek/ Abilene Mulberry Creek-Long Creek 345-kV double circuit; (3) a West-South CSC was represented using the Goldthwaite-Evant 138-kV line.  The model was clustered into four zones.

## Scenario 4

Scenario 4 was clustered using the base case (with Singleton Switch Station).  The 2008 CSCs were used with the exception that the North to Houston CSC was removed and the model was clustered into three zones.

## Scenario 5

Scenario 5 is a five zone cluster using the base case (with Singleton Switch Station).

## Cluster Analysis Discussion

When compared to the 2008 CM zone bus mapping, no generator buses changed zones in scenarios 1 and 3.  In scenario 2, Gibbons Creek, Dansby, Atkins, Texas A&M, and Frontier shift from the North zone to the Houston zone.  Additionally, all of Bryan and College Station shift from the North zone to the Houston zone in scenario 2.

In scenario 4 the Houston and South zones merged together.  Besides this merge no generator buses changed zones from the 2008 CM zone bus mapping.  Some buses (load serving only) located in the North zone in 2008 moved to the South zone in the scenario 4 clustering.

An additional CRE test was performed on scenario 4 to see if the Singleton-Obrien and Singleton-TH Wharton 345-kV lines would qualify as North-South CREs.  It was found that both lines passed the Protocol requirements to be North-South CREs.

The following buses changed CM zones in scenario 1 when compared to the 2008 CM zone bus mapping:

| Bus Number | Bus Name | Load MW | 2009 Scenario 1CM Zone | 2008 CM Zone |
| --- | --- | --- | --- | --- |
| 291 | DELEON | 1.18 | West | North |
| 616 | CARTER | 3.84 | North | West |
| 631 | NEWPORT | 1.13 | North | West |
| 1470 | NEWPRT_P |  | North | West |
| 1471 | CARTR_P8 |  | North | West |
| 1633 | DELEON_9 | 6.45 | West | North |
| 5560 | BAYCITYS | 5.1 | Houston | South |
| 6376 | CRM1TP2A |  | South | West |
| 6377 | CRM12A | 3.8 | South | West |
| 46220 | PETERS__ |  | Houston | South |
| 46230 | PETERS__ | 2.03 | Houston | South |

The following are select Impact Matrices for scenarios 3 and 4:

| Impact Matrix Scenario 3 N-H |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | North | South | Houston | West |
| North | 0.000 | 0.238 | 0.338 | 0.029 |
| South | -0.238 | 0.000 | 0.100 | -0.209 |
| Houston | -0.338 | -0.100 | 0.000 | -0.309 |
| West | -0.029 | 0.209 | 0.309 | 0.000 |

| Impact Matrix Scenario 3 N-S |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | North | South | Houston | West |
| North | 0.000 | 0.365 | 0.228 | 0.004 |
| South | -0.365 | 0.000 | -0.137 | -0.361 |
| Houston | -0.228 | 0.137 | 0.000 | -0.224 |
| West | -0.004 | 0.361 | 0.224 | 0.000 |

| Impact Matrix Scenario 4 N-S |  |  |  |
| --- | --- | --- | --- |
|  | North | South | West |
| North | 0.000 | 0.295 | 0.004 |
| South | -0.295 | 0.000 | -0.291 |
| West | -0.004 | 0.291 | 0.000 |

The following are the generators that changed CM zones in scenarios 3d and 3e when compared to the 2008 CM zone bus mapping:

| Bus Number | Bus Name | Gen MW | 2008 CM Zone | Scenario 3d CM Zone | Scenario 3e CM Zone |
| --- | --- | --- | --- | --- | --- |
| 344 | MRSSHPRD | 12 | West | North | North |
| 345 | MRSSHPRD | 12 | West | North | North |
| 1432 | GRHAMSES | 366 | West | North | North |
| 1433 | GRHAMSES | 242 | West | North | North |
| 1437 | MESQUITW | 400 | West | North | North |
| 1438 | MESQUITW | 236 | West | North | North |
| 1479 | WFCOGEN_ | 40 | West | North | North |
| 1482 | WFCOGEN_ | 40 | West | North | North |
| 1600 | BARTNWND | 120 | West | North | North |

The following spreadsheet contains the bus-CM zone mapping for scenarios 1, 3, 3a, 3b, 3c, 3d, 3e, and 4: