2705 West Lake Drive

Taylor, Texas 76574

(512) 248-6800

HTTP://WWW.ERCOT.COM

SIG0002 White Paper

Private Use Networks

v0.23

Kenneth Ragsdale

07/01/08

Revision History

| Revision | Comments | Date | Author |
| --- | --- | --- | --- |
| v0.10 | Initial Version | 04/15/2008 | Kenneth Ragsdale |
| v0.20 | Incorporated comments from the 4-15-08 meeting and also comments from Haso that he provided after that meeting. Added implementation schedule and EDS 4 dates. Added the “5-16-08” comments from Haso Peljto (highlighted in yellow). These comments explicitly describe the LMP calculation for PUN Resource Node. Solution design is complete. | 05/21/08 | Kenneth Ragsdale |
| V0.21 | Removed sections after the Solution Design section. | 5/27/2008 | Kenneth Ragsdale |
| V0.22 | Incorporated feedback from Market Participants | 6/17/2008 | Kenneth Ragsdale |
| V0.23 | Incorporated additional feedback from Market Participants | 07/01/2008 | Kenneth Ragsdale |

Table of Contents

1 - Problem Statement	4

2 - Solution Design	4

1 - Problem Statement

There are some significant differences between the nodal market and the current zonal market on how Private Use Networks (PUNs) are represented and considered by ERCOT systems in various analyses.  There is also a difference in how Market Participants with PUNs participate in the ERCOT market.

In general, ERCOT systems in the nodal market will require more detailed and granular information about the PUNs than what is currently required in the zonal market.  The ERCOT systems in nodal will be considering load information and specific information for each of the individual Resources in the PUN and providing Base Points and instructions to the individual Resources  The Resources in the PUN will participate in the Nodal market differently than how they currently do in the zonal market.

This document presents the key aspects of a “go-live” approach that is to be implemented for the start of the nodal market.

The document also provides a description of how data should be submitted by the QSE’s representing PUNs and how certain analysis should be performed by the ERCOT systems.   Integration issues and settlement issues are also addressed.

One other issue that has surfaced is the need to develop and provide more specific training for PUNs and QSE’s representing PUNs.

# 2 - Solution Design

Key Driving Points:

- The Nodal Protocols specify that certain data shall be provided about the PUN network, PUN load and PUN Resources in order to facilitate proper Market Operations and to ensure adequate system reliability.

- The Resources of the PUN shall be able to participate in the energy and ancillary service markets.

- Settlement of PUN Resources and PUN load shall be performed as specified in the protocols.

- Due to timeline and budget constraints, the design can not include time consuming or expensive changes to the applications currently being delivered and tested.

Design:

| Function Name | Design Decisions |
| --- | --- |
| Registration | - PUN generators and loads offering energy or ancillary services to the Nodal Market shall go through the same registration process of any other generators and loads. Full capabilities of the generators shall be provided during the registration process. Low Reasonability Limit must be set to zero and High Reasonability Limit set to the physical generator high reasonability limit. As with all other Resources, the Normal Ramp Rate and the Emergency Ramp Rate curves shall be provided as a function of gross MW output of the Resource. [ Reliant’s understanding is that all ramp rate curves are in Net Mw, in the case of a Resource on a PUN the units limits must be in net too so the HSL and LSLs etc are in net. Using gross does not work. Now if this means the net of the Resource not counting any net load in the PUN that is not ERCOT load, such would be OK, but this statement is confusing.] - Through the Resource Asset Registration Form (RARF), Load Schedules for each physical load within a PUN that is represented in the network model shall be provided for each typical day type. [seems like we need to make some provision to do this easier. What controls will ERCOT have in place to make sure these loads are indeed correct over time.] |
| NMMS | - An additional attribute shall be defined for loads and generators to flag them as Private Use Network. The transmission elements, loads and generators of the same Private Use Network shall be linked. - PUN loads shall be modeled as Non ERCOT non-conforming loads and Load Schedules should be provided. - The Network Model shall include PUN Resource Nodes and Resource Nodes for PUN Resources. The Principles for Resource Node Definition shall be followed when locating the PUN Resource Nodes and Resource Nodes for PUN Resources. |
| Mid Term/Long Term Forecast Module | PUN loads shall not be included in the ERCOT Weather Zone load in the load forecast model building process nor are these loads considered ERCOT load from any respect. If there is a net import to the PUN, that load will be considered ERCOT Load. |
| EMS Real Time | - SE shall use the telemetries at the interface points and within PUN (MW, MVAR, kV) as regular measurements. - SE shall use the estimated values of PUN loads to fine tune the PUN load schedules using a load adaptation algorithm similar to that used for the rest of the loads. The same approach shall be used to adapt the PUN generation schedules. [why is the generation not telemetered or is this referring to some other non-Resource generation?] - In the cases where PUN generator and PUN load telemetries are not available, but the interchange telemetries are available, one of the options is that the generators are assumed to be generating at their full capacities and the behind the meter load will be adjusted based on this and the telemetered interface flow. The other option is to set the PUN load as per the PUN load schedule as a pseudo measurement and adjust the PUN generation pseudo measurement to match the PUN load and telemetered interface flow if available. In the cases where the interchange telemetries and PUN generator and PUN load telemetries are not available, then set the PUN generator and load as per the PUN generator and load schedules as pseudo measurements. [is this not a Protocol violation is this telemetry is not available at least from the TSP?] - For the purposes of Bus Load Adaptation algorithm, both ERCOT Loads and PUN Loads shall be initialized with typical day schedules (provided by the PUN) prior to bus load adaptation. Bus Load Forecast function should provide typical day schedules for both ERCOT Loads and PUN Loads. - In the event that the PUN is a net load, the ERCOT load to be used in the SE (for obtaining pseudo load measurements) shall be adjusted by subtracting the net amount. PUN load received from ERCOT should be treated as a net interchange to the PUN, Is that what is occurring here, Please clarify.] - RLC shall compute the LDL and HDL for each Resource based on ramp rates determined by the ramp rate curves (ramp rates as a function of gross output) and gross resource MW telemetry.[same comment as before. Must use net gen excluding any pun load that is not ERCOT Load] |
| EMS Study Mode ( Outage Evaluation, Power Flow Studies, Stability Studies, etc) | {insert: From a principle perspective, if any load on the PUN comes from ERCOT generation, then that load is part of ERCOT load for all purposes. To the extent any PUN load is served by PUN generation, that load is not considered ERCOT load. PUN load served by ERCOT must be charged for AS just as any other retail load on the ERCOT System.} - Each forecasted ERCOT Weather Zone load is first adjusted for the net PUN load by subtracting form it the adapted PUN generation schedule minus the PUN load schedule. This adjusted load forecast shall be distributed amongst loads within the Weather Zone based on a set of defined Load Distribution Factors. This distribution process shall skip the PUN Loads. - The Bus Load Forecasting function shall use the typical day PUN load schedules as the projected PUN loads during both near term and long term study time periods. - For near term study (less than 7 days), PUN generator statuses from COP shall be used. In the cases where generators statuses data are not available from COP, it is assumed that those generators are OUT by default. The generation dispatch pattern shall be computed as designed by EMS so as to fully serve PUN Load by PUN generation. If PUN generation cannot meet its own PUN Load, then ERCOT generation shall serve the balance. - For longer term study (greater than 7 days), the process in a), b) and c) above shall be followed except that equipment status shall be determined by normal status and outage schedules instead of using COP data. |
| CRR | - PUN Resource Nodes could be used as CRR sinks and sources. - Resource Nodes within a PUN could also be used as CRR sinks and sources. - CCU Resource Nodes within a PUN could also be used as CRR sinks and sources. - Logical CCP Resource Nodes within a PUN can not be used as CRR sinks and sources. |
| OS | No special handling will be required. PUN shall report generation outages in Outage Scheduler and COP. PUN must also report transmission outages in Outage Scheduler. |
| COP | - For the “go-live” approach, only generation unit capacities that are available to ERCOT markets, i.e. the surplus that is available after covering the PUN loads should be represented in COP. PUN generating units that self-serve PUN loads are shown in COP as online and available with LSL equal to zero and HSL representing capacity exceeding self-served PUN load. This is net capacity of PUN generating unit that is available and could be offered into ERCOT energy and ancillary service markets. PUN generating units that are fully used for self-serving PUN load will have LSL= HSL = 0 MW. For PUN generating units whose entire capacity is available to ERCOT markets, this capacity should be reported in COP with appropriate status and with physical LSL and HSL i.e. no netting of PUN load. - In addition to statuses and generation unit net limits, the ancillary services and other PUN Resource parameters should be submitted into COP as for any other Resource. |
| DAM | - QSE’s could submit PUN Resource specific energy offers only for the portion of the unit capacity that is not used to self-serve PUN load. If PUN Resource is not used to self-serve PUN load then the three part offer for the whole unit capacity could be submitted into DAM. - This QSE could submit a Resource specific ancillary service offers for ancillary service markets in DAM and SASM. The energy and ancillary service Resource specific offers will be co-optimized in competition with ERCOT resources. - The QSE could also submit DAM Energy Only offers at interconnection points (PUN Resource Nodes) that are not Resource specific. |
| SCED | - SCED receives current net generation and net LASL/HASL and net LDL/HDL. Generation-To-Be-Dispatched (GTBD) incorporates PUN net generation into ERCOT. The PUN generating units are dispatched using real-time energy offers for net capacities of PUN generators. Resulting Base Points are sent to PUN units. - Instead of real-time energy offers, QSE’s could submit net output schedules for PUN generation units. If the QSE does not submit either an offer curve or an output schedule, then the Base Point for the PUN generating unit will follow the generation net output telemetry. - Transmission constraints for the ERCOT system will be enforced and will include PUN generators as control resources. Constraints within PUN network will not be enforced by any MMS process. - The DAM and SCED LMPs will be calculated in standard way for Settlement Points at both PUN Resource Nodes and Resource Nodes within PUN. The Real-Time SPPs at PUN Resource Nodes are calculated as time weighted average of SCED LMPs because there are no physical Resources mapped to PUN Resource Nodes. |
| RUC | - All PUN generation units should be represented in COP. RUC shall consider all Resources shown as offline and available as potential Resources to commit to serve ERCOT Load - only net capacity of PUN Generation Resources remaining after self-serving PUN loads is considered by RUC (as provided in COP). Therefore, PUN loads excluding any ERCOT load delivered to the PUN will not be considered by the RUC process. - If QSE does not submit a DAM offer for a PUN Resource and the Resource is shown as offline and available, then ERCOT shall create a proxy three part offer for RUC purposes. For such a PUN Resource, ERCOT shall use 150% of any approved verifiable startup cost and minimum energy cost (or 150% of generic if verifiable have not been approved) in the selection process. Settlements would not use the 150% values but instead use the verifiable or the generic costs. - For the “go-live” approach PUN loads will not be considered by RUC due to netting of PUN generation and self-served PUN loads. There are a few implications with the above “go-live” approach. The RUC process is reliability unit commitment that ensures adequate capacity to cover ERCOT Load Forecast + DC Tie Exports and anticipated contingencies. ERCOT load forecast does not include PUN Loads, i.e. the RUC process sets the PUN load to 0 MW. The PUN Resource capacities are modeled as the net surplus (positive only) into the ERCOT grid. This approach is deficient due to the following reasons but it has been determined to be acceptable for starting the Nodal Market. - RUC analysis assumes that PUN Load is always covered by PUN generation and this assumption is incorrect in the event that PUN generation is less than PUN load. - If DAM Energy Only Bids are awarded within PUN facility, there is potential of under commitment during RUC analysis as PUN load is not included in RUC. - RUC Contingency analysis will not capture scenarios where a contingency causes ERCOT to serve PUN load since PUN Load MW value is zero. This is an area prime for enhancement after “go-live”. Most likely the enhancements to be implemented after “go-live” will have PUN loads represented by their schedules as Non ERCOT non-conforming loads. These enhancements after go-live would allow representation of the full capacities of PUN generating units in COP, complete contingency analysis and reactive power consideration. |
| S&B | - DAM settlements for CRRs, energy and ancillary services are performed in the standard way, i.e. DAM awarded quantities are settled at DAM clearing prices. There are no differences between the settlement PUN Resources and other Resources in ERCOT. - RUC settlement is the same for PUN Resources and other Resources as well. The same rules and calculations apply for make whole payments for DAM/RUC commitments. - Real time energy settlement for QSEs representing PUNs is based on methodology developed for net-metering schemes. The EPS meters are located at all tie-lines between ERCOT system and PUN. The fifteen-minute settlement prices for PUN EPS meters are calculated in the standard way using the SCED LMPs and SCED Base Points. More details on net-metering scheme settlements can be found in Section 6 of the Nodal Protocols. - The DAM Settlement Prices for the PUN Resource Nodes shall be essentially the DAM LMPs for their electrical buses. The 15 minute Settlement Prices for the PUN Resource Nodes shall be calculated following the approach specified in section 6.6.1.1. Prices for the settlement EPS meters shall be calculated as described in Section 6.6.3.1 paragraph 3. |
| PUNs | - Private Use Networks shall telemeter flows at the ERCOT interconnection point(s), voltage at the interconnection point(s), and power output (gross generation output and net generation output with respect to serving PUN Load) of individual PUN generators in real time. - The status of each PUN Generation Resource shall be submitted to ERCOT through the COP for the next 7 operating days. - Generating Unit outages shall be reported to ERCOT in the Outage Scheduler and COP. - Transmission Equipment outages shall be reported to ERCOT in the Outage Scheduler. - Full capacities of the generating resources shall be provided during the registration process. - COP data for PUN generation resources shall be provided. |
| Training | Additional course material needs to be prepared and presented to both QSEs representing PUN Resources and to PUN owners. The material should focus on what is needed and planned for the “go-live” approach. |