## Slide 1: Renner Dynamic Reactive Project
James Teixeira
Manager, Regional Planning

## Slide 2: Description of Project
300 MVAr of dynamic reactive capability
Renner Station identified as a suitable site
Proposed capability in service by 2010 peak
Estimated cost : $35 M

## Slide 3: Location of Project

## Slide 4: Reliability Need for Project
UVLS Schemes Trip Over 2400 MW of Firm Load without Project:
  2010 peak load conditions
  All expected DFW area generation in service
  600 MVAr SVC assumed in service at Parkdale
  NERC category C contingency

## Slide 5: Independent Review Results
300 MVAr Dynamic Reactive Device at Renner
  Mitigates identified actuation of UVLS
  Addresses a fundamental need for dynamic reactive support in the DFW area
  Provides some locational diversity of DFW area dynamic reactive resources along with the Parkdale SVC
  Does not eliminate voltage collapse risk following the critical NERC category C contingency under all single unit outage scenarios

## Slide 6: Independent Review Results
Investigated additional impacts
  Faster fault clearing times may improve system response.
  Slow voltage recovery and potential voltage collapse are exacerbated by peak load conditions and the unavailability of DFW area generation resources.
  Simulation results are highly sensitive to the assumed percentage of motor load. Higher percentages of motor load increase the likelihood of fast voltage collapse following system faults.

## Slide 7: RPG Review
RPG Comment Period
  May 2, 2008 through May 23, 2008
  No dissenting comments submitted

## Slide 8: ERCOT Support for the Project
  The installation of dynamic reactive devices at Renner and Parkdale address a fundamental need for dynamic reactive support in the DFW area and provide some locational diversity.
Additional Recommendations
  Oncor should pursue system improvements that would reduce the severity of critical contingencies in order to delay additional investments for dynamic reactive capability in the DFW area.
ERCOT supports the need for this project and will seek approval by the Board

## Slide 9: Questions
QUESTIONS?