ERCOT Operations Report

July 2008 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 7/10/2008 22:03 | 59.859 | 78 | Unit Trip with 463 MW online |
| 7/27/2008 9:11 | 59.89 | 35 | Unit Trip with 589 MW online |
| 7/27/2008 12:15 | 59.898 | 7 | Unit Trip with 800 MW online |
| 7/28/2008 20:55 | 59.882 | 9 | Unit Trip with 750 MW online |
| 7/28/2008 22:11 | 60.103 | 36 | Out of URS. SCE change + 500 MW in 10 min |
| 7/29/2008 14:32 | 59.853 | 42 | Unit Trip with 710 MW online |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time of deployed | Stop Time | Duration | Max deployed | Details |
| --- | --- | --- | --- | --- |
| 7/04 23:02:08 | 7/04 23:26:12 | 0:24:04 | 343.74 | Load did not drop as expected & Out of URS |
| 7/06 21:04:16 | 7/06 21:19:22 | 0:15:06 | 348.94 | Held interval after ramp had begun. Out of URS due to Input Error. |
| 7/06 22:01:02 | 7/06 22:07:18 | 0:06:16 | 317.69 | Base power schedule drop by 4300 MW & SCE change - 800 MW in 5m |
| 7/08 19:32:52 | 7/08 19:50:24 | 0:17:32 | 333.33 | Out of URS & SCE change - 700 MW in 15m |
| 7/09 07:05:56 | 7/09 07:31:34 | 0:25:38 | 328.10 | Overshot Down balancing while recovering down regulation |
| 7/10 22:03:33 | 7/10 22:17:52 | 0:14:19 | 578.09 |  |
| 7/12 15:16:56 | 7/12 15:27:38 | 0:10:42 | 348.94 | Unit Trip |
| 7/19 00:19:48 | 7/19 00:29:39 | 0:09:51 | 343.74 | DC Tie curtailment & Unit Trip |
| 7/23 08:38:40 | 7/23 08:45:07 | 0:06:27 | 359.35 | SCE change - 520 MW in 15m followed by a Unit Trip |
| 7/27 09:11:46 | 7/27 09:28:32 | 0:16:46 | 635.38 |  |
| 7/27 12:15:33 | 7/27 12:23:51 | 0:08:18 | 380.18 |  |
| 7/28 20:55:44 | 7/28 21:05:25 | 0:09:41 | 458.31 |  |
| 7/29 14:32:20 | 7/29 14:49:33 | 0:17:13 | 609.34 |  |

Day-Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- | --- |
| Austin | 0 | 1 | 12 | 4 | 17 |
| Bryan Area | 0 | 0 | 2 | 0 | 2 |
| Corpus | 0 | 0 | 1 | 1 | 2 |
| DFW | 0 | 12 | 2 | 15 | 29 |
| E RIO | 0 | 1 | 0 | 0 | 1 |
| Houston | 0 | 5 | 38 | 11 | 54 |
| Laredo | 87 | 0 | 0 | 0 | 87 |
| North | 0 | 26 | 24 | 7 | 57 |
| Northeast | 0 | 1 | 0 | 1 | 2 |
| San Antonio | 0 | 0 | 7 | 5 | 12 |
| South | 0 | 0 | 1 | 0 | 1 |
| W RIO | 0 | 0 | 0 | 0 | 0 |
| Western | 0 | 1 | 3 | 11 | 15 |
|  | 87 | 47 | 90 | 55 | 279 |

| Historical Totals | Jul-07 | Jun-08 | Jul-08 |
| --- | --- | --- | --- |
| Austin | 33 | 70 | 17 |
| Bryan Area | 4 | 10 | 2 |
| Corpus | 0 | 0 | 2 |
| DFW | 19 | 13 | 29 |
| E RIO | 1 | 19 | 1 |
| Houston | 3 | 67 | 54 |
| Laredo | 86 | 81 | 87 |
| North | 36 | 56 | 57 |
| Northeast | 0 | 5 | 2 |
| San Antonio | 8 | 69 | 12 |
| South | 7 | 15 | 1 |
| W RIO | 0 | 3 | 0 |
| Western | 0 | 136 | 15 |
| Total | 197 | 544 | 279 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Trinidad -Stryker Creek and Mount Enterprise 345kV | Elkton - Athens | 16 |
| Austrop 345/138kV Auto #2 | Austrop 345/138kV Auto #1 | 15 |
| Lytton Spring - Zorn and Austrop 345kV | Canyon - Rohr 138kV | 10 |
| West Denton 345/138KV transformer | Collin - Frisco 138KV | 7 |
| Austrop 345/138 KV autotransformer 1 | Austrop 345/138 KV autotransformer 2 | 6 |
| Greenville Steam Transformer 1 138/69KV | Greenville Steam Transformer 2 138/69KV | 5 |
| Bosque - Whitney TU 138KV | Lake Whitney - Whitney TU 138KV | 4 |
| Enterprise -Trinidad & Martin Lake -Stryker Creek 345kV | Nacogdoches autotransformer #1 | 6 |
| Dyann - East Bernard 138KV | Lane City - South Lane City 138KV | 4 |
| Morgan Creek - Quail Switch - Longshore Switch 345KV | Stanton East - Big Spring West 138KV | 3 |
| North Denton Auto 1 138/69KV | North Denton Auto 2 138/69KV | 3 |
| West Levee Switch 345/138KV Autotransformer #1 | West Levee Switch 345/138KV Autotransformer #2 | 3 |
| Temple Pecan Creek - Tradinghouse SES and Temple Switch - Lake Creek SES 345KV | Ridge - Watson Chapel 138KV | 3 |
| Odessa EHV 138/69 KV autotransformer 1 | Odessa EHV 138/69 KV autotransformer 2 | 3 |
| Menard - Gillespie 138KV | Menard 138/69KV Transformer 1 | 2 |
| Trinidad - Stryker Creek SES and Mount Enterprise 345kV | Stryker Creek - Cherokee POI 138KV | 2 |
| Hamilton - Sonora 138kV | Sonora - Fries Ranch 69kV | 2 |
| Big Brown - Venus 345kV | Big Brown - Jewett 345kV | 2 |
| Odessa EHV 138/69 KV autotransformer 2 | Odessa EHV 138/69 KV autotransformer 1 | 2 |
| West Denton 345/138kV autotransformer | Airport - West Denton 138kV | 2 |
| San Angelo Red Creek 345/138kV Transformer T1 | San Angelo Red Creek 345/138kV Transformer T2 | 2 |
| Lytton - Zorn - Austrop 345kV | Goforth - Turnersville 138kV | 2 |
| Graham - Long Creek 345kV | Abilene South - Potosi Tap 138kV | 1 |
| Elkton - Stryker Creek 138KV | Troup Auto #1 | 1 |
| Sandow Switch - Austrop 345kV | Butler - Elgin Switch 138kV | 1 |
| Fort Mason 138/69KV Transformer 1 | Menard 138/69KV Transformer 1 | 1 |
| Brenham - Salem 138kv | Mill Creek - Gay Hill 138KV | 1 |
| Moss Switch - Holt Switch 138kV | Odessa North - North Cowden 69kV | 1 |
| Lytton Springs - Zorn - Austrop 345kV | Rohr - Goforth 138kV | 1 |
| Watermill - Tricorner & Trinidad SES 345kV | Big Brown SES - Jewett 345kV | 1 |
| Austrop - Lost Pines 345kV | Fayette 345/138kV autotransformer 26AT2 | 1 |
| Gibbons Creek - Twin Oak 345kV | Ridge - Watson Chapel | 1 |
| Post Oak College Station - College Station 138kV | Gibbons Creek - Greens Prairie 138kV | 1 |
| Comanche Peak SES - Decordova SES & Wolf Hollow - Rocky Creek 345kV | Concord 345/138kV autotransformer | 1 |
| West Levee T2 345/138KV Auto | West Levee T1 345/138KV auto | 1 |
| North Edinburg - Lon Hill 345kV | MVEC Weslaco - MVEC Heidelberg 138kV | 1 |
| Sonora - Friend Ranch 138kV | San Angelo Concho - San Angelo Nasworthy 69kV | 1 |
| Morgan Creek SES - Quail Switch & Longshore Switching Station 345kV | Midland East - Stanton East Switching Station 138kV | 1 |
| Collin T1 345/138KV transformer | Allen Switch - Plano Custer 138KV | 1 |
| Watermill - Tricorner & Trinidad SES 345kV | Seagoville - Seagoville Switch 138kV | 1 |
| Denton 138/69kV autotransformer | Spencer- King Co 69kV | 1 |
| Watermill Switch - West Levee Switch & Sargent Road 345kV | Cedar Hill Switch 345/138kV autotransformer | 1 |
| Allen Switch - Royse Switch - Monticello 345kV | Collin - Anna Switch 345kV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North-West | 1 |
| North-South | 5 |
| West-North | 11 |

New RAP (Date indicates last update of RAP not implementation date.)

7/30 	Sandow - Elgin Switch 138 kV Single Circuit RAP.

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 07/24/2008 | Transmission and Security Desk V 3 Rev 94 | 381 |
| 07/24/2008 | Frequency Control Desk V 3 Rev 68 | 380 |
| 07/24/2008 | Shift Supervisor Desk V 3 Rev 49 | 379 |

## Blackout/Load Shed Incidences

7/24     14:03	Requested 34 MW of Load Shed for Public Utility of Brownsville (PUB) due to Hurricane Dolly.

7/24     14:06	Requested 6 MW of Load Shed for Magic Valley Electric Co-operative (MVEC) due to Hurricane Dolly.

EECP

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

7/08     Held IE 01:30 real-time balancing deployments for IE 01:45 - IE 0230, resumed with the IE 02:45 deployments.

Communication

None

## ERCOT peak (Unofficial)

07/31 	   17:00 61,077 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2005 | 2006 | 2007 | 2008 |
| January | 5.02 | 4.79 | 4.55 | 3.30 |
| February | 3.47 | 4.81 | 3.75 | 3.59 |
| March | 3.41 | 4.95 | 2.70 | 3.29 |
| April | 3.37 | 5.59 | 3.00 | 2.45 |
| May | 4.21 | 3.59 | 3.22 | 3.01 |
| June | 3.91 | 2.65 | 4.46 | 2.81 |
| July | 5.22 | 2.62 | 4.29 | 2.55 |
| Annual Average | 4.56 | 3.79 | 3.55 | 3.00 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 7/3/08 | 9:23 | 14:00 | Alert issued for capacity shortage for HE 1500 -1900. |
| 7/3/08 | 4:15 | 14:00 | OCN issued for capacity shortage for hours ending 1600 -1900. |
| 7/9/08 | 11:00 | 13:30 | OCN issued for projected capacity shortage from HE 15:00 - 18:00. |
| 7/11/08 | 4:00 | 10:30 | OCN for possible capacity shortage for HE 17:00. |
| 7/12/08 | 15:36 | 19:45 | Advisory ARR below 3000 MW. |
| 7/14/08 | 15:10 | 19:14 | Advisory ARR below 3000 MW. |
| 7/19/08 | 15:40 | 19:50 | Advisory ARR below 3000 MW. |
| 7/19/08 | 6:00 | 9:00 | Alert issued due to projected capacity shortage for HE 14:00-19:00. |
| 7/19/08 | 4:00 | 6:00 | OCN issued due to projected capacity shortage for HE 15:00-17:00. |
| 7/20/08 | 8:00 | 12:00 | Alert issued due to projected capacity shortage for HE 15:00-19:00. |
| 7/20/08 | 9:00 | 9:45 | ERCOT opened an Adjustment Period RPRS Market due to Alert for projected capacity shortage. |
| 7/20/08 | 5:24 | 8:00 | OCN issued for projected capacity shortage for hours 15:00 - 18:00. |
| 7/21/08 | 7:00 | 17:00 | OCN issued for projected capacity shortage for HE 1700. |
| 7/22/08 | 5:30 | 14:30 | OCN issued for projected capacity shortage for HE 1600 -1700. |
| 7/22/08 | 21:10 | 23:30 | Advisory ARR below 3000 MW. |
| 7/23/08 | 14:24 | 18:35 | Advisory ARR below 3000 MW. |
| 7/26/08 | 17:15 | 19:00 | Advisory ARR below 3000 MW. |
| 7/27/08 | 9:00 | 11:00 | Alert issued for a projected capacity shortage for HE 16:00 - 19:00. |
| 7/27/08 | 8:00 | 9:00 | OCN issued for a projected capacity shortage for HE 16:00 - 18:00. |
| 7/27/08 | 16:25 | 18:00 | Advisory ARR below 3000 MW. |
| 7/28/08 | 16:41 | 18:30 | Advisory ARR below 3000 MW. |
| 7/29/08 | 14:59 | 16:20 | Alert for projected capacity shortage for He 17:00 |
| 7/29/08 | 14:40 | 18:50 | Advisory ARR below 3000 MW. |
| 7/30/08 | 6:00 | 10:45 | Alert issued for projected capacity shortage for HE 1600 - 1900. |
| 7/30/08 | 15:30 | 18:45 | Deployed NSRS in all zones due to projected depletion of UBES. |
| 7/30/08 | 3:25 | 10:45 | OCN issued for projected capacity shortage for HE 1600 - 1900. |
| 7/30/08 | 15:08 | 18:52 | Advisory ARR below 3000 MW. |
| 7/31/08 | 6:15 | 17:10 | Alert issued for projected capacity shortage for HE 1600 - 2000. |
| 7/31/08 | 14:50 | 19:30 | Deployed NSRS in all zones due to projected depletion of UBES. |
| 7/31/08 | 3:25 | 17:10 | OCN issued for projected capacity shortage for HE 1600 - 2000. |
| 7/31/08 | 9:51 | 10:15 | Advisory ARR below 3000 MW. |
| 7/31/08 | 15:00 | 19:32 | Advisory ARR below 3000 MW. |

Transmission

7/15     15:30	Emergency Notice was issued due to local congestion management techniques were unsuccessful. North – South zonal techniques were used to control.

7/27     20:00	Emergency Notice was issued due to BLT of 2 MW for Turkey area was initiated from ERCOT to SPP due to forced outage.

7/28     18:10	Emergency Notice was issued due to Zonal congestion management techniques being unsuccessful in controlling the North - South CSC congestion. Local techniques were utilized.

Weather

7/22     09:00	OCN issued for Tropical Storm Dolly

7/22     16:00	Alert issued due to Hurricane Dolly.

7/23     00:15	Alert issued due to Hurricane Dolly.

7/23     16:03	Emergency Notice issued due to Hurricane Dolly causing damage in Brownsville area.

7/24     00:15	Alert issued due to Hurricane Dolly.

7/24     00:15	Emergency Notice issued due to Hurricane Dolly causing damage in Brownsville area.

7/24     00:30	OCN issued due to Tropical Storm Dolly and expected heavy rainfall amounts.

7/25     00:15	Emergency Notice issued due to Hurricane Dolly causing damage in Brownsville area.

Texas RE Event Analysis

7/27     20:00	Loss of three 69 kV lines to the Matador substation disconnecting an SPS related unit. AEP had to order a 2 MW BLT for Turkey area and on the 28th.  Under preliminary analysis.

Other

7/06	Held IE 21:00 real-time balancing deployment for IE 21:15, resumed with IE 21:30.

7/12     21:00	BLT of 3 MW was initiated to ERCOT from SPP due to Storm Damage. BLT required due to storm damage at Union substation.

7/24 	Held IE 13:15 balancing deployments and resumed with IE 13:45 balancing deployments.

7/30     15:00	Emergency Notice was issued due to not able to meet the Day Ahead market close time.