## Slide 1: Purpose of the Unannounced Unit Testing
Knowing how well the units can actually reach their planned Resource Plan HSL when they are requested to do so, ERCOT performs unannounced unit testing where units are asked to deliver at their resource plan HSL and maintain it for 30 minutes.
Since it is difficult to test all units in a short period, sampling statistics are applied to approximate the true mean of the whole population.

## Slide 2: Data Description
A unit’s ability to reach its planned HSL is dependant on temperature. According to our current practice, we categorize the measurements by temperature:
Based on measurement results, a new variable is defined to represent the percent relative error between the tested and planned HSL MWs.
  Tested_MW: 30-minutes sustained MW
  Planned_HSL_MW: HSL MW from resource plan.
  Percent Relative Error: % relative error between the tested and planned MW.
Temperature Range | Total # of Tests | HSL reached and sustained | HSL not sustained
T < 85 F | 17 | 11 | 6
85 F ≤ T ≤ 95 F | 31 | 13 | 18
T> 95 F | 13 | 5 | 8

## Slide 3: Statistical Approach
ERCOT uses the Student Distribution for a number of samples less than 30 and the Normal Distribution for a number greater or equal to 30 .
The Student Distribution makes two assumptions:
  1. Normal population.
  2. Random sampling.
The Normal Distribution uses the Central Limit Theorem and therefore does not have to assume normal population.

## Slide 4: Statistical Approach
For our analysis, the computed confidence interval means: We are (confidence level %) sure that the true “percent relative error” mean for all units will be somewhere between the inferior and superior limits.
Since we are more concerned with the cases when we are unable to reach the planned HSL, we should use the inferior limit to guide our requirements.
Keep in mind that the true mean could be anywhere within the interval. However, the worst case scenario for us is if the mean actually equals the inferior limit. This limit represent the highest possible “negative mean” when on average the units would be short.

## Slide 5: Results Summary
Temperature greater than 95 F |  | 
Confidence Level | Inferior Limit | Superior Limit
90% | -1.31% | 0.49%
95% | -1.51% | 0.69%
99% | -1.95% | 1.13%
Using the 13 measurements at temperatures greater than 95 F, we can be 99% sure that the true value of the population mean will be somewhere between -1. 95% and 1.13%.
Using the 31 measurements at temperatures greater or equal to 85 F and less than or equal 95 F, we can be 99% sure that the true value of the population mean will be somewhere between -1.01% and 0.23%.
Temperature greater or equal to 85 F and less than or equal 95 F |  | 
Confidence Level | Inferior Limit | Superior Limit
90% | -0.78% | 0.01%
95% | -0.86% | 0.08%
99% | -1.01% | 0.23%

## Slide 6: Conclusion
Using a confidence level of 99%, ERCOT makes the following recommendations:
  Temperature range: 85 F ≤ T ≤ 95 F
    Test results indicate that the RDF can be reduced from 5% to 1%
    Using a Normal Distribution to characterize sampling fluctuations.
    Reduce RDF from 4% to 1% for the less than 85 F temperature range.
  Temperature range: T > 95 F
    Test results indicate that the RDF can be reduced from 7% to 2%
    Using a Student Distribution to characterize sampling fluctuations.
ERCOT will continue testing units and bring new recommendations as test results indicate.

## Slide 7: Unannounced Testing Summary
Date of Test: | QSE | CONFIGURATION | # OF UNITS | Ambient Temp | MW at Start of Test (MW) | Seasonal HSL(MW) | Resource Plan HSL (MW) | 30 Minute sustained (MW) | HSL Reached and Sustained | HSL Reached but not Sustained | HSL not Reached
Temperature less than 85 F |  |  |  |  |  |  |  |  |  |  | 
4/4/08 | QSEA | UNIT | 1 | 68 | 552 | 553 | 553 | 552 |  |  | Y
5/15/08 | QSEB | UNIT | 1 | 70 | 197 | 250 | 222 | 227 | Y |  | 
5/15/08 | QSEB | UNIT | 1 | 70 | 205 | 250 | 220 | 227 | Y |  | 
5/15/08 | QSEB | UNIT | 1 | 70 | 205 | 250 | 228 | 228 | Y |  | 
5/15/08 | QSEB | UNIT | 1 | 70 | 232 | 250 | 232 | 233 | Y |  | 
5/12/08 | QSEA | UNIT | 1 | 72 | 71 | 412 | 412 | 417 | Y |  | 
5/27/08 | QSEL | CCY | 3 | 72 | 642 | 707 | 675 | 666 |  | Y | 
5/16/08 | QSEC | UNIT | 1 | 73 | 201 | 502 | 502 | 506 | Y |  | 
4/17/08 | QSEC | UNIT | 1 | 74 | 288 | 530 | 530 | 519 |  |  | Y
5/15/08 | QSED | CCY | 3 | 74 | 300 | 525 | 522 | 519 |  | Y | 
5/15/08 | QSEE | CCY | 3 | 75 | 308 | 491 | 498 | 498 | Y |  | 
4/3/08 | QSEF | UNIT | 1 | 75.8 | 430 | 543 | 559 | 537 |  |  | Y
4/11/08 | QSEG | CCY | 7 | 76 | 325 | 571 | 510 | 482 |  |  | Y
5/14/08 | QSEH | CCY | 3 | 79.34 | 370 | 487 | 424 | 430 | Y |  | 
4/7/08 | QSEB | UNIT | 1 | 82 | 313 | 413 | 413 | 428 | Y |  | 
5/14/08 | QSEI | UNIT | 1 | 83 | 55 | 347 | 347 | 347 | Y |  | 
5/13/08 | QSEJ | CCY | 2 | 83.2 | 331 | 546 | 528 | 530 | Y |  | 

## Slide 8: Unannounced Testing Summary
Date of Test: | QSE | CONFIGURATION | # OF UNITS | Ambient Temp | MW at Start of Test (MW) | Seasonal HSL (MW) | Resource Plan HSL (MW) | 30 Minute sustained (MW) | HSL Reached and Sustained | HSL Reached but not Sustained | HSL not Reached
Temperature between 85 F and 95 F |  |  |  |  |  |  |  |  |  |  | 
6/6/08 | QSEA | UNIT | 1 | 87 | 421 | 439 | 439 | 424 |  |  | Y
6/22/08 | QSEP | CCY | 3 | 87 | 174 | 210 | 212 | 214 | Y |  | 
8/6/08 | QSEW | CCY | 3 | 87 | 471 | 492 | 492 | 489 |  |  | Y
7/18/08 | QSET | CCY | 4 | 88 | 140 | 179 | 173 | 172 |  |  | Y
8/7/08 | QSEE | CCY | 3 | 87.2 | 463 | 495 | 481 | 484 | Y |  | 
5/28/08 | QSEM | UNIT | 1 | 89 | 55 | 110 | 110 | 109 |  |  | Y
7/7/08 | QSEJ | UNIT | 1 | 89 | 319 | 395 | 396 | 396 | Y |  | 
8/6/08 | QSEF | UNIT | 1 | 89 | 51 | 79 | 79 | 79 | Y |  | 
8/6/08 | QSEF | UNIT | 1 | 89 | 51 | 80 | 80 | 80 | Y |  | 
6/6/08 | QSEF | UNIT | 1 | 90 | 100 | 174 | 172 | 169 |  |  | Y
5/9/08 | QSED | UNIT | 1 | 91 | 96 | 330 | 329 | 323 |  |  | Y
6/4/08 | QSEN | CCY | 3 | 91 | 340 | 389 | 361 | 364 | Y |  | 
7/9/08 | QSEC | UNIT | 1 | 91 | 317 | 515 | 524 | 523 |  | Y | 
7/15/08 | QSEN | UNIT | 1 | 91 | 29 | 40 | 46 | 47 | Y |  | 
8/1/08 | QSEH | UNIT | 1 | 91 | 147 | 174 | 174 | 171 |  | Y | 
8/6/08 | QSET | CCY | 3 | 91 | 492 | 574 | 590 | 577 |  |  | Y

## Slide 9: Unannounced Testing Summary
Date of Test: | QSE | CONFIGURATION | # OF UNITS | Ambient Temp | MW at Start of Test (MW) | Seasonal HSL (MW) | Resource Plan HSL (MW) | 30 Minute sustained (MW) | HSL Reached and Sustained | HSL Reached but not Sustained | HSL not Reached
Temperature between 85 F and 95 F |  |  |  |  |  |  |  |  |  |  | 
5/15/08 | QSEK | CCY | 3 | 92 | 92 | 467 | 454 | 458 | Y |  | 
5/20/08 | QSEF | UNIT | 1 | 92 | 610 | 745 | 749 | 735 |  |  | Y
8/5/08 | QSED | UNIT | 1 | 92 | 190 | 333 | 333 | 332 |  |  | Y
8/7/08 | QSEV | UNIT | 1 | 92 | 117 | 214 | 208 | 205 |  |  | Y
7/8/08 | QSEF | UNIT | 1 | 93 | 430 | 543 | 543 | 530 |  |  | Y
7/19/08 | QSEC | UNIT | 1 | 93 | 264 | 375 | 375 | 374 |  | Y | 
7/21/08 | QSEA | UNIT | 1 | 93 | 160 | 210 | 210 | 212 | Y |  | 
7/18/08 | QSEA | UNIT | 1 | 94 | 267 | 409 | 409 | 408 |  |  | Y
8/5/08 | QSEI | UNIT | 1 | 94 | 142 | 156 | 155 | 153 |  |  | Y
8/5/08 | QSEI | UNIT | 1 | 94 | 142 | 165 | 155 | 153 |  |  | Y
8/7/08 | QSEW | CCY | 3 | 94 | 567 | 617 | 560 | 569 | Y |  | 
6/27/08 | QSEQ | UNIT | 1 | 94.5 | 78 | 106 | 90 | 91 | Y |  | 
7/16/08 | QSES | CCY | 3 | 95 | 215 | 230 | 242 | 244 | Y |  | 
7/22/08 | QSEA | UNIT | 1 | 95 | 113 | 203 | 211 | 214 | Y |  | 
8/7/08 | QSEA | UNIT | 1 | 95 | 446 | 551 | 552 | 546 |  |  | Y

## Slide 10: Unannounced Testing Summary
Date of Test: | QSE | CONFIGURATION | # OF UNITS | Ambient Temp | MW at Start of Test (MW) | Seasonal HSL(MW) | Resource Plan HSL (MW) | 30 Minute Sustained (MW) | HSL Reached and Sustained | HSL Reached but not Sustained | HSL not Reached
Temperature Greater than 95 F |  |  |  |  |  |  |  |  |  |  | 
7/20/08 | QSEF | UNIT | 1 | 96 | 437 | 745 | 745 | 743 |  |  | Y
7/28/08 | QSEU | UNIT | 1 | 96 | 626 | 634 | 632 | 629 |  | Y | 
6/24/08 | QSEO | CCY | 4 | 97 | 722 | 728 | 750 | 762 | Y |  | 
6/26/08 | QSEI | UNIT | 1 | 97 | 100 | 165 | 155 | 155 | Y |  | 
7/10/08 | QSER | CCY | 4 | 97 | 631 | 942 | 838 | 855 | Y |  | 
7/25/08 | QSEF | UNIT | 1 | 97 | 177 | 227 | 200 | 194 |  |  | Y
7/17/08 | QSET | CCY | 3 | 98 | 621 | 682 | 650 | 648 |  |  | Y
7/26/08 | QSEC | UNIT | 1 | 98 | 231 | 388 | 388 | 370 |  |  | Y
7/22/08 | QSEV | UNIT | 1 | 99 | 108 | 118 | 110 | 111 | Y |  | 
7/18/08 | QSEJ | UNIT | 1 | 99.1 | 350 | 565 | 568 | 567 |  |  | Y
8/3/08 | QSED | UNIT | 1 | 100 | 200 | 425 | 425 | 424 |  | Y | 
7/28/08 | QSEJ | UNIT | 1 | 101 | 51 | 118 | 119 | 120 | Y |  | 
7/21/08 | QSEC | UNIT | 1 | 106 | 434 | 502 | 502 | 494 |  | Y | 

## Slide 11: Overall Summary
Temperature Range | Total # of Tests | HSL reached and sustained | HSL not sustained
T < 85 F | 17 | 11 | 6
85 F ≤ T ≤ 95 F | 31 | 13 | 18
T> 95 F | 13 | 5 | 8
There are four retest measurements not included in this summary two of them were in the less than 85 F temperature range and the other two were in 85 F to 95 F temperature range.