| PRR Number | 771 | PRR Title | Ramp Rate Limitation of 10% per minute of On-Line Installed Capability for Wind-powered Generation Resources |
| --- | --- | --- | --- |
| Date Posted |  | July 25, 2008 |  |
| Protocol Section Requiring Revision |  | 6.5.13, WGR Ramp Rate Limitations (new) 6.6, Selection Methodology 6.6.1, Qualified Scheduling Entity Rights and Obligations to Self-Arrange Ancillary Service Resources |  |
| Requested Resolution |  | Normal |  |
| Revision Description |  | This Protocol Revision Request (PRR) proposes a requirement for Wind-powered Generation Resources (WGRs) to limit the ramp rate to 10% per minute of On-line installed capability. |  |
| Overall Market Benefit |  | The intent of this PRR is to maintain system reliability as it allows ERCOT to avoid frequency spikes due to the WGRs ability to ramp up or ramp down almost instantaneously. |  |
| Overall Market Impact |  | Minimal. There should be market impact in reducing the rate of increase in regulation service procured to compensate for rapid changes in WGR output. ERCOT does not have these effects quantified. |  |
| Consumer Impact |  | None. |  |
| Credit Implications |  | To be determined. |  |
| Relevance to Nodal Market |  | Yes. Similar changes need to be made to the Nodal Protocols. |  |
| Nodal Protocol Section(s) Requiring Revision |  |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 | . |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Not known | Not known. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | May improve reliability | Not known. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | John Dumas on behalf of the Reliability and Operations Subcommittee (ROS) |
| Email Address | jdumas@ercot.com |
| Company | ERCOT ISO |
| Phone Number | (512) 248-3195 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jonathan Levine |
| E-Mail Address | jlevine@ercot.com |
| Phone Number | 512-248-6464 |

Proposed Protocol Language Revision

6.5.13 	WGR Ramp Rate Limitations

Each Wind-powered Generating Resource (WGR) shall limit its ramp rate to 10% per minute of its online installed capability when responding to or released from an ERCOT deployment.6.6	Selection Methodology