| PRR Number | 771 | PRR Title | Ramp Rate Limitation of 10% per minute of On-Line Installed Capability for Wind-powered Generation Resources |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | August 21, 2008 |  |  |
| Protocol Sections Requiring Revision |  | 6.5.13, WGR Ramp Rate Limitations (new) 6.6, Selection Methodology 6.6.1, Qualified Scheduling Entity Rights and Obligations to Self-Arrange Ancillary Service Resources |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This Protocol Revision Request (PRR) proposes a requirement for Wind-powered Generation Resources (WGRs) to limit the ramp rate to ten percent (10%) per minute of On-line installed capability. |  |  |
| Overall Market Benefit |  | The intent of this PRR is to maintain system reliability as it allows ERCOT to avoid frequency spikes due to the WGRs ability to ramp up or ramp down almost instantaneously. |  |  |
| Overall Market Impact |  | Minimal. There should be market impact in reducing the rate of increase in regulation service procured to compensate for rapid changes in WGR output. ERCOT does not have these effects quantified. |  |  |
| Consumer Impact |  | None. |  |  |
| Credit Impacts |  | To be determined. |  |  |
| Procedural History |  | - On 7/25/08, PRR771 was posted. - On 8/4/06, Luminant Energy comments were posted. - On 8/6/08, Texas Regional Entity (TRE) comments were posted. - On 8/18/08, Wind Coalition comments were posted. - On 8/21/08, PRS considered PRR771. |  |  |
| PRS Decision |  | On 8/21/08, PRS unanimously voted to table PRR771. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 8/21/08, ERCOT Staff explained the background of PRR771 and noted that it was in response to and increase in CPS1 violations due to the rapid movement of WGRs. PRR771’s purpose is to improve ERCOT’s CPS1 performance. ERCOT Staff stated that the ramp rate could be adjusted once there is more data if, as TRE comments suggest, the proposed ramp rate of ten percent (10%) per minute of On-line installed capability is insufficient. Participants noted that a workshop is scheduled for August 22, 2008 at which the technical specifications and compliance issues associated with this proposed Protocol revision will be discussed. It was suggested that PRS table PRR771 until after the workshop. |  |  |

ERCOT/Market Segment Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 | . |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Not known | Not known. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | May improve reliability | Not known. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Luminant Energy 080408 | Requests that PRS refer PRR771 to ROS and WMS for clarification of the definition of “on-line installed capability” as it relates to a WGR. |
| TRE 080608 | States that proposed ramp rate may be too conservative, but it should be implemented as soon as possible while further study is conducted. |
| Wind Coalition 081808 | Suggests changing “on-line installed capability” to “rated net MW capacity” to deal with concerns expressed in Luminant Energy 080408 comments. |

| Original Sponsor |  |
| --- | --- |
| Name | John Dumas on behalf of the Reliability and Operations Subcommittee (ROS) |
| Company | ERCOT ISO |
| Market Segment | Not applicable |

Proposed Protocol Language Revision

6.5.13 	WGR Ramp Rate Limitations

Each Wind-powered Generating Resource (WGR) shall limit its ramp rate to 10% per minute of its online installed capability when responding to or released from an ERCOT deployment.6.6	Selection Methodology