## Sheet1
West to North Transfer Stability Limit
Effective: June 26, 2008
Scenarios of West Zone Generation Units In-Service
|  | A | B | C | D | E | F
Transmission Line Outages
| All lines in-service | 1700~1960 | 1700~1960 | 1600~1860 | 1500~1760 | 1400~1660 | 1350~1610
| Abilene MulBerry Creek – Oklaunion | 1700~1960 | 1670~1930 | 1570~1830 | 1530~1790 | 1330~1590 | 1290~1550
| Graham – Bowman | 1700~1960 | 1670~1930 | 1550~1810 | 1520~1780 | 1340~1600 | 1270~1530
| Abilene MulBerry Creek – Bluff Creek | 1700~1960 | 1670~1930 | 1530~1790 | 1520~1780 | 1330~1590 | 1260~1520
| Morgan Creek – Sweetwater | 1630~1890 | 1560~1820 | 1400~1660 | 1350~1610 | 1200~1460 | 1140~1400
| Bowman – Fish Road | 1600~1860 | 1560~1820 | 1420~1680 | 1350~1610 | 1210~1470 | 1110~1370
| Morgan Creek – Quail Switch | 1630~1890 | 1520~1780 | 1360~1620 | 1250~1510 | 1075~1335 | 950~1210
| Morgan Creek – Tonkawa | 1620~1880 | 1515~1775 | 1330~1590 | 1255~1515 | 1100~1360 | 1000~1260
| Jacksboro – Bowman | 1620~1880 | 1570~1830 | 1415~1675 | 1340~1600 | 1180~1440 | 1200~1460
| Graham – Long Creek | 1600~1860 | 1570~1830 | 1420~1680 | 1350~1610 | 1215~1475 | 1110~1370
| Abilene MulBerry Creek – Bitter Creek | 1500~1760 | 1430~1690 | 1260~1520 | 1170~1430 | 1030~1290 | 945~1205
| Morgan Creek – Gasconades Creek | 1450~1710 | 1400~1660 | 1210~1470 | 1110~1370 | 1000~1260 | 920~1180
| CmcheSS – Compeak | 1460~1720 | 1420~1680 | 1260~1520 | 1210~1470 | 1050~1310 | 950~1210
| Oklaunion – Fisher Road | 1430~1690 | 1350~1610 | 1220~1480 | 1140~1400 | 1030~1290 | 920~1180
| Sweetwater – Long Creek | 1440~1700 | 1380~1640 | 1230~1490 | 1160~1420 | 1000~1260 | 950~1210
| CmcheSS – SARedCk | 1310~1570 | 1260~1520 | 1120~1380 | 1050~1310 | 910~1170 | 850~1110
| Willow Creek – Jacksboro | 1260~1520 | 1200~1460 | 1070~1330 | 1000~1260 | 900~1160 | 800~1060
| Graham – Jacksboro | 1210~1470 | 1150~1410 | 1000~1260 | 920~1180 | 790~1050 | 680~940
| Graham – Parker, Graham – Benbrook | 950~1210 | 870~1130 | 770~1030 | 680~940 | 570~830 | 480~740
| Willow Creek – Parker | 940~1200 | 840~1100 | 730~990 | 650~910 | 530~790 | 440~700
Notes:
1 | The generation scenarios reflect different combinations of generators in-service. It is assumed that a Power System Stabilizaer is operational if the unit is in-service. If a unit is in service without a PSS, the limit associated with that unit being out of service is applicable.
2 | The transfer limit will increase up to 260MW if units without PSS are out of service. The range of transfer given for each combination of generation scenario and transmission line outage reflects this range.
3 | If no conventional units are in service in the west there is no stability limit based on small signal criterion.