| OGRR Number | 211 | OGRR Title | Deletion of References to Back-to-Back Import Capacity |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | August 14, 2008 |  |  |

| Operating Guides Section Requiring Revision | 4.5.3.3, EECP Steps |
| --- | --- |
| Proposed Effective Date | October 1, 2008 |
| Priority and Rank Assigned | Not applicable. |
| Revision Description | This Operating Guide Revision Request (OGRR) deletes obsolete references to Back-to-Back (BtB) import capacity from the list of tasks ERCOT is responsible for under Emergency Electric Curtailment Plan (EECP) Step 1. It also replaces references to a “unit” in the EECP Steps with the defined term “Resource,” and makes minor language corrections consistent with previous revisions to the ERCOT Protocols made pursuant to Protocol Revision Request (PRR) 726, DC Tie Scheduling Clarifications, which became effective on October 1, 2007. |
| Overall Market Benefit | Consistency of Operating Guides and ERCOT Protocols. |
| Overall Market Impact | None. |
| Consumer Impact | None. |
| Procedural History | - On 5/22/08, OGRR211 and its Impact Analysis were posted. - On 6/17/08, the Operating Guides Revision Task Force (OGRTF) comments were posted. - On 6/18/08, the Operations Working Group (OWG) considered OGRR211. - On 7/16/08, the OWG considered the OWG Recommendation Report and Impact Analysis for OGRR211. - On 8/14/08, ROS considered the OWG Recommendation Report and Impact Analysis for OGRR211. |
| OWG Decision | On 6/18/08, the OWG was in consensus to recommend approval of OGRR211 as submitted. On 7/16/08, the OWG was in consensus to forward the OWG Recommendation Report and Impact Analysis to ROS for approval. |
| Summary of OWG Discussion | On 6/18/08, there was no discussion. On 7/16/08, there was no discussion. |
| ROS Decision | On 8/14/08, ROS unanimously voted to recommend approval of OGRR211 as recommended by OWG and endorse the Impact Analysis. All Market Segments were present for the vote. |
| Summary of ROS Discussion | On 8/14/08, it was noted that the OGRTF was in consensus in recommending approval of OGRR211. |

ERCOT/Market Segment Impacts and Benefits

| Assumptions | 1 | No changes in practice are intended; only deleting obsolete language to align Operating Guides with current ERCOT Protocols. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None expected. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Consistency of Operating Guides and ERCOT Protocols. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | H. Steven Myers |
| E-mail Address | smyers@ercot.com |
| Company | ERCOT |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| OGRTF 061708 | Recommends that OGRR211 be approved as submitted. |

Proposed Guide Language Revision

#### 4.5.3.3	EECP Steps

Step 1 – Maintain ERCOT Physical Responsive Capability (PRC) on Resources plus RRS MW provided from LaaR Equal To 2300 Mw

| OPERATOR | ACTION |
| --- | --- |
| ERCOT | - Utilize available DC Tie capability that is not already being used by the market. - Notify the Southwest Power Pool Security Coordinator. - Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency. - Inquire about availability of Block Load Transfers. |
| QSE | - Notify ERCOT of any Resources uncommitted but available in the timeframe of the emergency. - Immediately update the HSL of any On-line Resource that is capable of providing extra capacity within thirty (30) minutes. The extra capacity must already be part of the QSE’s Up Balancing bid curve in order for SPD to utilize the updated Resource Plan. |

Step 2 – Maintain ERCOT Physical Responsive Capability (PRC) on Resources plus RRS MW Provided from LaaR Equal To 1750 MW

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures associated with STEP 1 |
| ERCOT | - Instruct TDSPs to reduce Customers’ Load by using distribution voltage reduction measures, if deemed beneficial by the TDSP. - Instruct QSEs to deploy all Responsive Reserve, which is supplied from Load acting as a Resource (LaaRs) (controlled by high-set under-frequency relays) - With approval of the affected Non-ERCOT control area, may instruct TDSPs to implement Block Load Transfers (BLTs), which transfer Load from the ERCOT control area to Non-ERCOT control areas. - Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation. |

Step 3 - Maintain System Frequency At 60 Hz

| OPERATOR | ACTION |
| --- | --- |
|  | Following deployment of the measures under STEPS 1 and 2. |
| ERCOT | Deploy all available EILS Resources as a single block via a single Verbal Dispatch Instruction to all QSEs providing EILS. |

Step 4 - Maintain System Frequency At 59.8 Hz Or Greater

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1, 2 and 3. |
| ERCOT | Direct all TDSPs and their agents to shed firm Load, in one hundred (100) megawatt (MW) blocks, distributed as agreed and documented in the ERCOT Operation procedures in order to maintain a steady state system frequency of 59.8 Hertz (Hz). ERCOT may take this action prior to the expiration of the ten (10) minute EILS Resource deployment period if ERCOT, in its sole discretion, believes that shedding firm Load is necessary to maintain the stability of the ERCOT System. If, due to ERCOT System conditions, EILS Resources are not deployed prior to this action, ERCOT shall deploy EILS Resources as soon as possible following this action. |
|  | In addition to measures under STEPS 1 and 2. |
| TDSPs | Keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TDSPs shall not manually drop Load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan. |

Obligation for Load shed is by DSP.  Load shedding obligations need to be represented by an Entity with 7x24 operations and hotline communications with ERCOT and control over breakers.  [Use Transmission Operators (TOs) as list of Entities.]

ERCOT Load Shed Table

| Transmission Operator | 2006 Total Transmission Operator Load (MW) |
| --- | --- |
| American Electric Power | 9.27 |
| Austin Energy | 3.89 |
| Brazos Electric Power Cooperative | 4.12 |
| CenterPoint Energy | 24.34 |
| City of Bryan | 0.54 |
| City of College Station | 0.29 |
| City of Denton | 0.50 |
| City of Garland | 0.95 |
| CPS Energy | 7.22 |
| Lower Colorado River Authority | 5.19 |
| Magic Valley Electric Cooperative | 0.56 |
| Public Utility Board of Brownsville | 0.40 |
| Rayburn Country Electric Cooperative | 0.99 |
| South Texas Electric Coop-Medina Electric Coop | 0.65 |
| Texas New Mexico Power | 2.28 |
| Tex-La | 0.15 |
| Oncor | 38.66 |
| ERCOT Total | 100.00 |