## Slide 1: Nacogdoches to Lufkin SS 345 kV Line Project
James Teixeira
Manager, Regional Planning

## Slide 2: Description of Project
Add new conductor to existing structures for 13 miles from Nacogdoches Southeast to Herty North
Build new 10 mile double circuit capable with one circuit in place 345 kV line on new ROW from Herty North to Lufkin Switch
Needed in service ASAP (estimated 2012 peak)
Estimated cost : $29.2 M

## Slide 3: Location of Project
Existing Structures/ROW
New Structures/ROW

## Slide 4: Reliability/Economic Needs for Project
Solves overloading/congestion at Nacogdoches Southeast 345/138 kV autotransformer
Adds 2nd 345 kV source to Nacogdoches and Lufkin
Allows exit of existing Mt. Enterprise SPS
Identified as economic in the 2007 Five-Year Plan with production costs savings of $ 13.4 M in 2012

## Slide 5: Alternative Considered
Move the Mount Enterprise to Martin Lake 345 kV circuit off of the Mount Enterprise to Trinidad 345 kV circuit structures so that single tower outage does not cause loss of both circuits
Reconfigure Mount Enterprise Switch Station so that single breaker failure does not cause loss of both circuits
Solves overloading/congestion on Nacogdoches Southeast 345/138 kV autotransformer for one contingency but not all
Production cost savings of $ 7.2 M in 2012
Capital cost estimates were not calculated

## Slide 6: RPG Review
RPG Comment Period
  July 25, 2008 through August 15, 2008
  No dissenting comments submitted

## Slide 7: ERCOT Support for the Project
ERCOT will be requesting that this project be endorsed by the ERCOT Board Of Directors.

## Slide 8: Questions
QUESTIONS?