## Slide 1: DWG RRS/LaaRs STUDY
STATUS SUMMARY
9/11/08

## Slide 2: DWG RRS/LaaRs Study Status Summary
Study Progress Highlights
Remaining Work
Conclusion

## Slide 3: DWG RRS/LaaRs Study Study Progress Highlights
Completed Initial Flat Starts for Peak and Off-Peak Cases.
Completed Network Data Preparation for Peak and Off-Peak Cases
  Selection of generating units for participation in 2800 MW RRS.
  Established blocks of spinning reserves between 25% and 100% of 2800 MW RRS in 5% increments. Detailed modeling of combined cycle trains made this much less of a straight-forward process in comparison to previous studies without such modeling.
  Redispatch participating units per defined schedules, maintaining case load and generation balance.
  For provision of benchmarking, repeated the process for the 2300 MW RRS scenario.

## Slide 4: DWG RRS/LaaRs Study Study Progress Highlights
Completed Dynamic Data Preparation Complimentary to Network Data Preparation.
Completed Base Dynamic Data Preparation for Modeling of Various Percentages of LaaRs.
Completed Tuning of Generic Governor Models for Use With the Participating Generator Units.
  Used EMS data from two actual events.
  Modified network cases to model pre-disturbance and post-disturbance periods for each of the two events.
  Used two governor models, one for simple cycle machines and the other is the new combined cycle governor model.
  Varied governor model parameters to obtain simulation frequency response approximate to actual event frequency response.
  The result is two generic governor models to be used with RRS participating units, aggregate response of which is a conservative representation of actual system response.

## Slide 5: DWG RRS/LaaRs Study Study Progress Highlights
As of 9/11/08, several rounds of simulations have been completed for the 59.7 Hz tier. Through careful planning and setup of these simulations, the results have afforded substantial headway towards the objective of identifying an acceptable LaaRs percentage at the 59.7 Hz tier.
As expected, frequency overshoot during light load conditions is the limiting factor in identifying acceptable LaaRs percentages.
As we anticipated, the volume of simulations is large due to the amount of variables involved. A variable of particular interest is the LaaRs relay frequency setpoints. Practical LaaRs frequency settings can range from 59.70-59.79 Hz in 0.01 Hz increments. The impact of relatively small changes in these settings is more significant than predicted. This unforeseen result has steered the simulations into more of an iterative process than planned.

## Slide 6: DWG RRS/LaaRs Study Status Summary
Study Progress Highlights
Remaining Work
Conclusion

## Slide 7: DWG RRS/LaaRs Study Remaining Work
More simulations at the 59.7 Hz tier are needed. Variables that may need further testing/verification include:
  LaaRs relay trip delays
  Geographical lumping of LaaRs
  Tripping generation at alternate locations
  Ratio of combined cycle reserve to simple cycle reserve in the RRS pool.
  Response from reserve not participating in RRS.
Conduct simulations at the 59.8 (and 59.9 Hz ??) tier(s). This process is expected to go much faster than that for the 59.7 Hz tier.
Final interpretation of results, write draft report. To be done by the DWG.
Finalize report after review period. To be done by the DWG.

## Slide 8: DWG RRS/LaaRs Study Status Summary
Study Progress Highlights
Remaining Work
Conclusion
  An estimated 75% of the total study tasks have been completed.