## Slide 1: Wind Operations Task Force
For ROS vote, 11 Sept 2008
Issue #3a – Wind Generation Ramp Rates
Background: The ROS endorsed the draft PRR on ramp rates on 7/10, except for the single condition of increasing wind output during natural speed increases (ie. endorsed the draft PRR - now PRR 771 - for dispatch conditions only). That part concerning natural changes was remanded back to WOTF.
Recommendation: The WOTF discussed this and found that limiting wind farm ramp up rates (either by unit or by site) will not address the problem of controlling the frequency as seen in recent events. The WOTF recommends no further action on limiting wind generation ramp rates.
However, the WOTF did find other possible means of controlling frequency when many wind farms do experience sustained increased output over several intervals (as discussed at WW2), such as:
Designing a response for wind farms much like a governor
Reg Down deployments
High frequency relays
The WOTF seeks permission to open a new issue for exploring such solutions, including combinations of the methods identified.