| PRR Number | 771 | PRR Title | Ramp Rate Limitation of 10% per minute of On-Line Installed Capability for Wind-powered Generation Resources |
| --- | --- | --- | --- |
| Date | September 18, 2008 |
| Submitter’s Information |
| Name | Walter Reid |
| E-mail Address | w.j.reid@ieee.org |
| Company | Wind Coalition |
| Phone Number | 512-335-0664 |
| Cell Number | 512-335-0664 |
| Market Segment | N/A – coalition with members in several Market Segments |

Comments

| Overall Market Benefit | Increased reliability by reducing frequency excursions due to rapid ramping capability of wind generation in response to dispatch orders from ERCOT |
| --- | --- |
| Overall Market Impact | Will reduce wind generation output somewhat, will require a combination of modest operational changes and capital investments by wind generators, will reduce likelihood of major system impacts resulting in significant costs and possible new Ancillary Service costs |
| Consumer Impact | None |

A number of Market Participants were concerned that there was no clear standard for compliance.  The original discussion of the wording recognized that each Wind-powered Generation Resource (WGR) would have different compliance capabilities and that each WGR would have technology specific procedures.  The wording below makes that understanding explicit.

One WGR recognized that release from a Special Protection Scheme (SPS) can also be a “step” increase in generation.  Wording has been added to include ramp rate limits when released from Remedial Action Plans (RAPs) and SPSs.

Revised Proposed Protocol Language

6.5.13 	WGR Ramp Rate Limitations

Each Wind-powered Generating Resource (WGR) shall limit its ramp rate to 10% per minute of its  rated name plate net MW capacity when responding to or released from an ERCOT deployment; including release from SPS operations and release from RAP deployments.  The operation of an SPS and the initiation of a RAP will be in accordance with their design and this WGR ramp rate limit shall not apply. Each WGR shall submit a compliance plan to ERCOT by December 1, 2008.  The compliance plan for each WGR shall specify the procedures to be put in place by the WGR to comply with this section 6.5.13 WGR Ramp Rate Limitation; such procedure to be within the capabilities of the WGR’s installed facilities.  ERCOT shall review compliance plans and may disapprove any plans that are not deemed to be using the actual capability of the existing WGR equipment and control systems.