| PRR Number | 771 | PRR Title | Ramp Rate Limitation of 10% per minute of On-Line Installed Capability for Wind-powered Generation Resources |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | September 24, 2008 |  |  |
| Protocol Sections Requiring Revision |  | 6.5.13, WGR Ramp Rate Limitations (new) 6.6, Selection Methodology 6.6.1, Qualified Scheduling Entity Rights and Obligations to Self-Arrange Ancillary Service Resources |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Revision Description |  | This Protocol Revision Request (PRR) proposes a requirement for Wind-powered Generation Resources (WGRs) to limit the ramp rate to ten percent (10%) per minute of On-line installed capability. |  |  |
| Overall Market Benefit |  | The intent of this PRR is to maintain system reliability as it allows ERCOT to avoid frequency spikes due to the WGRs ability to ramp up or ramp down almost instantaneously. |  |  |
| Overall Market Impact |  | Minimal. There should be market impact in reducing the rate of increase in regulation service procured to compensate for rapid changes in WGR output. ERCOT does not have these effects quantified. |  |  |
| Consumer Impact |  | None. |  |  |
| Credit Impacts |  | To be determined. |  |  |
| Procedural History |  | - On 7/25/08, PRR771 was posted. - On 8/4/06, Luminant Energy comments were posted. - On 8/6/08, Texas Regional Entity (TRE) comments were posted. - On 8/15/08, Wind Coalition comments were posted. - On 8/21/08, PRS considered PRR771. - On 9/11/08, ERCOT comments were posted. - On 9/16/08, Reliability and Operations Subcommittee (ROS) comments were posted. - On 9/18/08, a second set of Wind Coalition comments were posted. - On 9/19/08, FPL Energy comments were posted. - On 9/23/08, Invenergy comments were posted. - On 9/24/08, PRS again considered PRR771. |  |  |
| PRS Decision |  | On 8/21/08, PRS unanimously voted to table PRR771. All Market Segments were present for the vote. On 9/24/08, PRS voted to recommend approval of PRR771 as amended by ERCOT comments. There were two opposing votes from the Investor Owned Utility (IOU) and the Independent Generator Market Segments and one abstention from the Independent Power Marketer (IPM) Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 8/21/08, ERCOT Staff explained the background of PRR771 and noted that it was in response to an increase in CPS1 violations due to the rapid movement of WGRs. PRR771’s purpose is to improve ERCOT’s CPS1 performance. ERCOT Staff stated that the ramp rate could be adjusted once there is more data if, as TRE comments suggest, the proposed ramp rate of ten percent (10%) per minute of On-line installed capability is insufficient. Participants noted that a workshop is scheduled for August 22, 2008 at which the technical specifications and compliance issues associated with this proposed Protocol revision will be discussed. It was suggested that PRS table PRR771 until after the workshop. On 9/24/08, ERCOT Staff explained that the purpose for PRR771 was to control near-instantaneous ramping by WGRs that are responding to an ERCOT deployment instruction. Various comments that have been filed were discussed. Some participants expressed agreement with Luminant’s comment that the term “on-line installed capability” be more clearly defined. Others agreed with the Wind Coalition’s comments dated September 18, 2008 that proposed amendments to clarify compliance standards. It was also noted that ROS’s comments endorsed PRR771 as submitted and recommended that the issue of WGR ramp rates due to natural wind increases and decreases be addressed via a separate PRR. One participant expressed concern that there are technological limitations that make compliance with the provision added by PRR771 problematic and recommended that the PRR be remanded to ROS or another group to address these issues. Other participants indicated that they were opposed to remanding PRR771 and supported implementing a solution now, even if it needs to be revised later. ERCOT Staff agreed that it would be better to put the new provision in place now since it addresses most of the relevant issues. |  |  |

ERCOT/Market Segment Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 | . |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Not known | Not known. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | May improve reliability | Not known. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Luminant Energy 080408 | Requests that PRS refer PRR771 to ROS and WMS for clarification of the definition of “on-line installed capability” as it relates to a WGR. |
| TRE 080608 | States that proposed ramp rate may be too conservative, but it should be implemented as soon as possible while further study is conducted. |
| Wind Coalition 081508 | Suggests changing “on-line installed capability” to “rated net MW capacity” to deal with concerns expressed in Luminant Energy 080408 comments. |
| ERCOT 091108 | Proposes to restore the language of Section 6.6.1, which was accidentally marked as a proposed deletion in PRR771 as submitted. |
| ROS 091608 | Indicates that ROS unanimously voted to approve a motion that no further changes be made to PRR771 with no further comment in regard to natural wind increase ramp rates, and with the caution that this action does not address large ramps due to wind increases. |
| Wind Coalition 091808 | Proposes revisions to clarify compliance standards, include ramp rate limits when WGRs are released from Remedial Action Plan (RAP) deployments and Special Protection Scheme (SPS) operations, and require that WGRs submit a compliance plan by December 1, 2008. |
| FPL Energy 091908 | Agrees that clarification of the definition of “on-line installed capability” is needed. States that ramp rate limitation(s) should take into consideration differences in unit capabilities among units of varying vintages and manufacturers. Expresses concern with respect to compliance where an ERCOT deployment instruction coincides with dramatic changes in wind or ERCOT specifically requests rapid drops of wind generation. Suggests an exception for Force Majeure Events. |
| Invenergy 092308 | Notes that there is currently no available off-the-shelf control system solution that would allow compliance with PRR771 as written. Expresses concern with respect to compliance where an ERCOT deployment instruction coincides with dramatic changes in wind. Agrees with revision proposed in Wind Coalition 091808 comments requiring WGRs to submit a compliance plan but states that the deadline for submitting a compliance plan must be at least 120 days after PRR771 takes effect. |

| Original Sponsor |  |
| --- | --- |
| Name | John Dumas on behalf of ROS |
| Company | ERCOT ISO |
| Market Segment | Not applicable |

Proposed Protocol Language Revision

6.5.13 	WGR Ramp Rate Limitations

Each Wind-powered Generating Resource (WGR) shall limit its ramp rate to 10% per minute of its online installed capability when responding to or released from an ERCOT deployment.6.6	Selection Methodology

6.6	Selection Methodology

6.6.1	Qualified Scheduling Entity Rights and Obligations to Self-Arrange Ancillary Service Resources

(1)	QSEs may self-arrange only Regulation Up, Regulation Down, Responsive Reserve Services, and Non-Spinning Reserve Services.

(2)	A QSE may self-arrange Resources by indicating the amount of each Ancillary Services that will be self-arranged in each hour of the Operating Day.

(3)	The quantity self-arranged specified by a QSE at 1100 in the Day Ahead shall not be changed for the Day Ahead Obligation, unless ERCOT allows schedules to be updated at 1300 in accordance with Section 4.4.10, QSE Submittal of Updated Balancing Energy Schedules.

(4)	The quantity of Self-Arranged AS specified by a QSE in response to a Notice by ERCOT to obtain additional AS in the Adjustment Period cannot be greater than the allocated additional AS amount and cannot be changed once committed to ERCOT.

(5)	QSEs may schedule with ERCOT to provide Ancillary Services on another QSE’s behalf by notifying ERCOT consistent with the requirements of Section 4, Scheduling.