## Notes
Notes:
The SSWG 2009 summer peak case was used as the base case for the analysis
The areas in the case were modified to be the 2009 CM zones
PTDF Sheets:
There is a PTDF Sheet for North-South, West-North, and North-Houston CSCs
South-North and North-West PTDFs will be the same as North-South and West-North respectively, but with the opposite sign
PTDFs were calculated for the CSC and all CREs in the base case (n-0) and under the contingency of the CSC and each CRE
PTDFs were calculated by defining a CM zone to CM zone transfer - only "moveable" units were used in the transfer calculation
The 3 plants that had the highest shift factor in each direction across the CREs was calculated for the base case (n-0) and for the contingency of the CSC and CRE
Column A is a reference contingency number - see the Contingency sheets for definitions of the contingencies
Column B is the monitored element
Column C is the long name of the contingency
Column D is the Power Transfer Distribution Factor (PTDF) given as a percentage
Column F is the name of the plant that has the highest shift factor in the positive direction on the element for the given contingency
Column G is the shift factor of the plant listed in column F on the element for the given contingency
Column H is the name of the plant that has the second highest shift factor in the positive direction on the element for the given contingency
Column I is the shift factor of the plant listed in column H on the element for the given contingency
Column J is the name of the plant that has the third highest shift factor in the positive direction on the element for the given contingency
Column K is the shift factor of the plant listed in column J on the element for the given contingency
Column L is the name of the plant that has the highest shift factor in the negative direction on the element for the given contingency
Column M is the shift factor of the plant listed in column L on the element for the given contingency
Column N is the name of the plant that has the second highest shift factor in the negative direction on the element for the given contingency
Column O is the shift factor of the plant listed in column N on the element for the given contingency
Column P is the name of the plant that has the third highest shift factor in the negative direction on the element for the given contingency
Column Q is the shift factor of the plant listed in column P on the element for the given contingency

## W-N CSC_1 PTDFs
Contingency # | Element | Contingency | PTDF
base case | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | Base Case | 17.4
base case | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | Base Case | -21.4
base case | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | Base Case | 15.2
base case | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | Base Case | 17.4
base case | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | Base Case | 17
base case | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | Base Case | 2.3
base case | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | Base Case | 3.7
base case | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | Base Case | -13.9
base case | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | Base Case | 11.1
base case | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | Base Case | -8.2
base case | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | Base Case | 8.5
base case | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | Base Case | -1.3
base case | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | Base Case | -9.8
base case | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | Base Case | -10.7
base case | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | Base Case | 15.3
base case | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | Base Case | 14.7
base case | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | Base Case | -16.1
base case | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | Base Case | 3.1
base case | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | Base Case | -17.7
base case | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | Base Case | 7.4
base case | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | Base Case | 18.3
base case | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | Base Case | 16.2
base case | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | Base Case | -17.6
base case | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | Base Case | 2.4
base case | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | Base Case | 3.3
base case | CSC_1_ORAN1_8_BARTON_8_1571_1599 | Base Case | -2.8
base case | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | Base Case | -3.1
base case | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | Base Case | 3
base case | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | Base Case | 2.8
base case | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | Base Case | -2.8
base case | CSC_1_MURRY_P8_PAIP4B_1371_6169 | Base Case | -3.7
base case | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | Base Case | -19.2
base case | CSC_1_OKLA7A_ABMULCW7_6100_6235 | Base Case | -7.9
base case | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | Base Case | -16.7
base case | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | Base Case | -8.4
1 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 2.1
1 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -31.2
1 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 14.8
1 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 16.9
1 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 20.1
1 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 2.7
1 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 4
1 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -13.5
1 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 10.8
1 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -8.5
1 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 8.5
1 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -0.9
1 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -10.1
1 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -10.5
1 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 0
1 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 21.7
1 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -15.5
1 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 3.1
1 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -15
1 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 7.2
1 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 15.5
1 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 17.2
1 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -14.8
1 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 2.3
1 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 3.3
1 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -2.7
1 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -3.1
1 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 3.1
1 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 2.8
1 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -2.8
1 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -4
1 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -26.2
1 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -8
1 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -17.8
1 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | -10.6
2 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 22.8
2 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -13.6
2 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 15.1
2 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 17.3
2 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 19.7
2 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 2.7
2 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 3.8
2 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -13.7
2 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 10.9
2 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -7.3
2 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 8.1
2 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -1.7
2 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -8.8
2 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -10.6
2 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 20.7
2 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 0
2 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -16.2
2 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 3.1
2 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -16.5
2 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 7.3
2 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 17.2
2 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 16.6
2 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -16.5
2 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 2.3
2 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 3.3
2 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -2.7
2 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -3.1
2 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 3
2 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 2.8
2 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -2.8
2 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -3.8
2 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -4.5
2 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -6.6
2 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -17.1
2 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | -12.4
3 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 22.6
3 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -26.5
3 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 14.2
3 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 16.1
3 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 0
3 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 2.7
3 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 4.3
3 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -13.2
3 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 10.5
3 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -10.1
3 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 9
3 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 0.3
3 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -11.9
3 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -10.2
3 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 20.6
3 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 20.6
3 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -14.5
3 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 3
3 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -22.9
3 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 7
3 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 23.5
3 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 18.4
3 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -22.8
3 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 2.3
3 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 3.2
3 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -2.7
3 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -3
3 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 3.2
3 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 2.9
3 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -2.9
3 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -4.3
3 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -25.1
3 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -9.6
3 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -19
3 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | -9.4
4 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 17.7
4 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -21.3
4 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 15.3
4 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 17.4
4 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 17.3
4 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 0
4 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 3.3
4 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -13.9
4 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 11.1
4 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -8.1
4 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 8.4
4 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -1.4
4 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -9.7
4 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -10.7
4 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 15.7
4 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 15.2
4 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -16.1
4 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 3.1
4 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -17.8
4 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 7.4
4 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 18.5
4 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 16.3
4 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -17.7
4 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 2.3
4 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 3.2
4 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -2.7
4 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -3.1
4 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 3
4 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 2.7
4 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -2.7
4 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -3.3
4 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -19.7
4 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -8
4 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -16.8
4 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | -8.5
5 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 17.7
5 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -22.4
5 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 15.2
5 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 17.3
5 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 17.5
5 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 1.8
5 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 0
5 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -13.8
5 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 11
5 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -8.7
5 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 8.5
5 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -1.2
5 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -10.5
5 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -10.7
5 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 15.7
5 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 14.8
5 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -16
5 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 2.7
5 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -18.4
5 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 7.4
5 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 19
5 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 16.5
5 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -18.3
5 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 2.3
5 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 2.9
5 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -2.4
5 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -2.7
5 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 3
5 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 2.7
5 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -2.7
5 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 0
5 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -19.3
5 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -8
5 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -17
5 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_MURRY_P8_GRHAMSES1_8 | -8.4
6 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 17.2
6 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -21
6 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 17.9
6 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 21.8
6 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 16.8
6 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 2.3
6 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 3.7
6 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 0
6 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -2.8
6 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -7.5
6 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 5.8
6 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 0.1
6 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -9.3
6 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -15.3
6 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 15.2
6 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 14.6
6 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -9.5
6 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 3.4
6 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -17.5
6 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 4.3
6 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 18.1
6 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 17.1
6 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -17.4
6 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 2.7
6 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 3.6
6 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -3.1
6 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -3.4
6 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 3.3
6 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 3
6 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -3
6 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -3.7
6 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -19
6 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -7.4
6 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -17.5
6 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | -7.9
7 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_WILLOWCK_5_PARKER_5 | 17.3
7 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_WILLOWCK_5_PARKER_5 | -21.1
7 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_WILLOWCK_5_PARKER_5 | 17.3
7 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_WILLOWCK_5_PARKER_5 | 20.9
7 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_WILLOWCK_5_PARKER_5 | 16.9
7 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_WILLOWCK_5_PARKER_5 | 2.3
7 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_WILLOWCK_5_PARKER_5 | 3.7
7 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_WILLOWCK_5_PARKER_5 | -2.8
7 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_WILLOWCK_5_PARKER_5 | 0
7 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_WILLOWCK_5_PARKER_5 | -7.7
7 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_WILLOWCK_5_PARKER_5 | 6.4
7 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_WILLOWCK_5_PARKER_5 | -0.1
7 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_WILLOWCK_5_PARKER_5 | -9.4
7 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_WILLOWCK_5_PARKER_5 | -14.4
7 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_WILLOWCK_5_PARKER_5 | 15.2
7 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_WILLOWCK_5_PARKER_5 | 14.6
7 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_WILLOWCK_5_PARKER_5 | -10.8
7 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_WILLOWCK_5_PARKER_5 | 3.3
7 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_WILLOWCK_5_PARKER_5 | -17.5
7 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_WILLOWCK_5_PARKER_5 | 4.9
7 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_WILLOWCK_5_PARKER_5 | 18.1
7 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_WILLOWCK_5_PARKER_5 | 16.9
7 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_WILLOWCK_5_PARKER_5 | -17.4
7 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_WILLOWCK_5_PARKER_5 | 2.6
7 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_WILLOWCK_5_PARKER_5 | 3.5
7 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_WILLOWCK_5_PARKER_5 | -3
7 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_WILLOWCK_5_PARKER_5 | -3.3
7 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_WILLOWCK_5_PARKER_5 | 3.2
7 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_WILLOWCK_5_PARKER_5 | 3
7 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_WILLOWCK_5_PARKER_5 | -3
7 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_WILLOWCK_5_PARKER_5 | -3.7
7 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_WILLOWCK_5_PARKER_5 | -19.1
7 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_WILLOWCK_5_PARKER_5 | -7.5
7 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_WILLOWCK_5_PARKER_5 | -17.3
7 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_WILLOWCK_5_PARKER_5 | -8
8 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 17.5
8 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -23.4
8 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 15.2
8 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 17.4
8 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 17.5
8 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 2.2
8 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 3.9
8 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -13.3
8 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 10.5
8 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 0
8 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 6.7
8 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -3.6
8 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -6.3
8 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -10.3
8 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 15.5
8 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 14.2
8 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -16.9
8 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 3.1
8 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -18.8
8 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 7.2
8 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 19.4
8 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 16.6
8 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -18.7
8 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 2.5
8 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 3.3
8 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -2.8
8 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -3.1
8 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 3.1
8 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 2.9
8 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -2.9
8 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -3.9
8 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -18.7
8 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -4.8
8 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -17.1
8 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | -8
9 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 17.4
9 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -22
9 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 15.9
9 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 18.5
9 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 17.2
9 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 2.2
9 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 3.7
9 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -11.9
9 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 9.1
9 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -6.6
9 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 0
9 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 4.5
9 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -8.5
9 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -9.6
9 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 15.3
9 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 14.5
9 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -21.4
9 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 3.2
9 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -18
9 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 6.8
9 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 18.6
9 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 16.6
9 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -17.9
9 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 2.7
9 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 3.5
9 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -2.9
9 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -3.2
9 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 3.2
9 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 2.9
9 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -2.9
9 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -3.7
9 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -19
9 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -6.7
9 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -17
9 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_BOWMAN_5_JACKSBRO_5 | -8.1
10 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 17.4
10 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -21.2
10 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 15.4
10 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 17.5
10 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 17
10 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 2.3
10 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 3.7
10 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -13.7
10 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 10.9
10 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -8.5
10 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 7.7
10 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 0
10 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -10.1
10 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -10.6
10 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 15.3
10 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 14.7
10 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -16.6
10 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 3.1
10 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -17.6
10 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 7.4
10 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 18.2
10 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 16.2
10 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -17.5
10 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 2.3
10 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 3.3
10 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -2.8
10 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -3.1
10 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 3
10 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 2.8
10 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -2.8
10 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -3.7
10 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -19.2
10 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -8.1
10 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -16.7
10 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | -8.4
11 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_FISHRDSS1_5_OKLA7A | 17.7
11 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_FISHRDSS1_5_OKLA7A | -26.8
11 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_FISHRDSS1_5_OKLA7A | 15.3
11 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_FISHRDSS1_5_OKLA7A | 17.5
11 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_FISHRDSS1_5_OKLA7A | 18.3
11 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_FISHRDSS1_5_OKLA7A | 2.2
11 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_FISHRDSS1_5_OKLA7A | 4.3
11 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_FISHRDSS1_5_OKLA7A | -12.9
11 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_FISHRDSS1_5_OKLA7A | 10.1
11 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_FISHRDSS1_5_OKLA7A | 0.3
11 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_FISHRDSS1_5_OKLA7A | 5.1
11 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_FISHRDSS1_5_OKLA7A | -6.1
11 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_FISHRDSS1_5_OKLA7A | 0
11 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_FISHRDSS1_5_OKLA7A | -10.2
11 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_FISHRDSS1_5_OKLA7A | 15.7
11 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_FISHRDSS1_5_OKLA7A | 13.3
11 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_FISHRDSS1_5_OKLA7A | -17.9
11 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_FISHRDSS1_5_OKLA7A | 3.1
11 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_FISHRDSS1_5_OKLA7A | -20.6
11 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_FISHRDSS1_5_OKLA7A | 7
11 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_FISHRDSS1_5_OKLA7A | 21.2
11 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_FISHRDSS1_5_OKLA7A | 17.3
11 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_FISHRDSS1_5_OKLA7A | -20.5
11 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_FISHRDSS1_5_OKLA7A | 2
11 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_FISHRDSS1_5_OKLA7A | 3.3
11 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_FISHRDSS1_5_OKLA7A | -2.8
11 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_FISHRDSS1_5_OKLA7A | -3.1
11 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_FISHRDSS1_5_OKLA7A | 3.1
11 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_FISHRDSS1_5_OKLA7A | 2.9
11 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_FISHRDSS1_5_OKLA7A | -2.9
11 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_FISHRDSS1_5_OKLA7A | -4.3
11 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_FISHRDSS1_5_OKLA7A | -17.7
11 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_FISHRDSS1_5_OKLA7A | 0.5
11 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_FISHRDSS1_5_OKLA7A | -17.8
11 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_FISHRDSS1_5_OKLA7A | -7.2
12 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_JACKSBRO_5_W_DENT_5 | 17.3
12 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_JACKSBRO_5_W_DENT_5 | -21.1
12 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_JACKSBRO_5_W_DENT_5 | 16.9
12 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_JACKSBRO_5_W_DENT_5 | 19.5
12 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_JACKSBRO_5_W_DENT_5 | 16.9
12 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_JACKSBRO_5_W_DENT_5 | 2.3
12 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_JACKSBRO_5_W_DENT_5 | 3.7
12 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_JACKSBRO_5_W_DENT_5 | -19
12 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_JACKSBRO_5_W_DENT_5 | 16.2
12 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_JACKSBRO_5_W_DENT_5 | -7.8
12 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_JACKSBRO_5_W_DENT_5 | 6.8
12 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_JACKSBRO_5_W_DENT_5 | -0.5
12 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_JACKSBRO_5_W_DENT_5 | -9.5
12 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_JACKSBRO_5_W_DENT_5 | 0
12 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_JACKSBRO_5_W_DENT_5 | 15.2
12 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_JACKSBRO_5_W_DENT_5 | 14.6
12 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_JACKSBRO_5_W_DENT_5 | -12.2
12 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_JACKSBRO_5_W_DENT_5 | 3.4
12 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_JACKSBRO_5_W_DENT_5 | -17.5
12 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_JACKSBRO_5_W_DENT_5 | 7.8
12 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_JACKSBRO_5_W_DENT_5 | 18.1
12 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_JACKSBRO_5_W_DENT_5 | 16.8
12 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_JACKSBRO_5_W_DENT_5 | -17.4
12 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_JACKSBRO_5_W_DENT_5 | 2.7
12 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_JACKSBRO_5_W_DENT_5 | 3.6
12 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_JACKSBRO_5_W_DENT_5 | -3.1
12 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_JACKSBRO_5_W_DENT_5 | -3.4
12 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_JACKSBRO_5_W_DENT_5 | 3.2
12 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_JACKSBRO_5_W_DENT_5 | 3
12 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_JACKSBRO_5_W_DENT_5 | -3
12 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_JACKSBRO_5_W_DENT_5 | -3.7
12 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_JACKSBRO_5_W_DENT_5 | -19.1
12 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_JACKSBRO_5_W_DENT_5 | -7.6
12 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_JACKSBRO_5_W_DENT_5 | -17.2
12 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_JACKSBRO_5_W_DENT_5 | -8
13 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 17.1
13 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -20
13 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 18.3
13 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 21.9
13 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 16.6
13 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 2.3
13 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 3.7
13 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -7.7
13 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 4.9
13 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -9.2
13 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 15.1
13 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -6.4
13 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -10.7
13 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -7.4
13 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 15.1
13 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 14.7
13 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 0
13 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 3.5
13 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -16.9
13 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 5.6
13 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 17.5
13 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 17
13 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -16.8
13 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 2.4
13 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 3.6
13 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -3.1
13 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -3.5
13 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 3.2
13 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 3
13 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -3
13 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -3.7
13 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -19.2
13 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -8.6
13 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -17.5
13 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | -8
14 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 17.4
14 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -21.3
14 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 15.6
14 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 17.8
14 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 17
14 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 2.2
14 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 3.5
14 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -14.2
14 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 11.4
14 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -8.2
14 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 8.7
14 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -1.3
14 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -9.8
14 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -11
14 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 15.3
14 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 14.7
14 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -16.5
14 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 0
14 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -17.7
14 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 7.6
14 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 18.3
14 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 16.3
14 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -17.6
14 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 2.5
14 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 1.1
14 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -0.6
14 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 0
14 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 3.2
14 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 2.9
14 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -2.9
14 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -3.5
14 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -19.2
14 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -7.8
14 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -16.9
14 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | -8.3
15 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 15.3
15 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -15.7
15 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 14.5
15 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 16.5
15 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 19.4
15 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 2.4
15 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 4.2
15 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -13.5
15 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 10.7
15 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -10.2
15 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 9.1
15 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 0.3
15 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -12
15 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -10.4
15 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 13.2
15 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 13.5
15 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -14.8
15 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 3.1
15 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 0
15 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 7.2
15 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 28.2
15 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 17.8
15 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -27.5
15 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 2.4
15 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 3.3
15 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -2.7
15 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -3.1
15 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 3.1
15 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 2.9
15 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -2.9
15 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -4.2
15 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -18
15 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -9.9
15 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -18.3
15 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | -6.9
16 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_PARKER_5_BENBRK_A_T5 | 17.4
16 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_PARKER_5_BENBRK_A_T5 | -21.3
16 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_PARKER_5_BENBRK_A_T5 | 16.8
16 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_PARKER_5_BENBRK_A_T5 | 16.4
16 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_PARKER_5_BENBRK_A_T5 | 17
16 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_PARKER_5_BENBRK_A_T5 | 2.3
16 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_PARKER_5_BENBRK_A_T5 | 3.7
16 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_PARKER_5_BENBRK_A_T5 | -12.9
16 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_PARKER_5_BENBRK_A_T5 | 10.1
16 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_PARKER_5_BENBRK_A_T5 | -8.1
16 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_PARKER_5_BENBRK_A_T5 | 8.2
16 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_PARKER_5_BENBRK_A_T5 | -1.1
16 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_PARKER_5_BENBRK_A_T5 | -9.8
16 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_PARKER_5_BENBRK_A_T5 | -10.8
16 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_PARKER_5_BENBRK_A_T5 | 15.3
16 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_PARKER_5_BENBRK_A_T5 | 14.7
16 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_PARKER_5_BENBRK_A_T5 | -15.5
16 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_PARKER_5_BENBRK_A_T5 | 3.1
16 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_PARKER_5_BENBRK_A_T5 | -17.6
16 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_PARKER_5_BENBRK_A_T5 | 0
16 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_PARKER_5_BENBRK_A_T5 | 18.3
16 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_PARKER_5_BENBRK_A_T5 | 16.3
16 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_PARKER_5_BENBRK_A_T5 | -17.6
16 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_PARKER_5_BENBRK_A_T5 | 2.4
16 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_PARKER_5_BENBRK_A_T5 | 3.3
16 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_PARKER_5_BENBRK_A_T5 | -2.8
16 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_PARKER_5_BENBRK_A_T5 | -3.1
16 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_PARKER_5_BENBRK_A_T5 | 3.1
16 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_PARKER_5_BENBRK_A_T5 | 2.8
16 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_PARKER_5_BENBRK_A_T5 | -2.8
16 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_PARKER_5_BENBRK_A_T5 | -3.7
16 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_PARKER_5_BENBRK_A_T5 | -19.1
16 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_PARKER_5_BENBRK_A_T5 | -7.8
16 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_PARKER_5_BENBRK_A_T5 | -16.8
16 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_PARKER_5_BENBRK_A_T5 | -8.3
17 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_LONCREK2_5_COKFIELD_5 | 15.1
17 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_LONCREK2_5_COKFIELD_5 | -15.5
17 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_LONCREK2_5_COKFIELD_5 | 14.4
17 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_LONCREK2_5_COKFIELD_5 | 16.4
17 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_LONCREK2_5_COKFIELD_5 | 19.5
17 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_LONCREK2_5_COKFIELD_5 | 2.4
17 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_LONCREK2_5_COKFIELD_5 | 4.2
17 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_LONCREK2_5_COKFIELD_5 | -13.5
17 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_LONCREK2_5_COKFIELD_5 | 10.7
17 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_LONCREK2_5_COKFIELD_5 | -10.3
17 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_LONCREK2_5_COKFIELD_5 | 9.1
17 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_LONCREK2_5_COKFIELD_5 | 0.3
17 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_LONCREK2_5_COKFIELD_5 | -12.1
17 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_LONCREK2_5_COKFIELD_5 | -10.4
17 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_LONCREK2_5_COKFIELD_5 | 13.1
17 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_LONCREK2_5_COKFIELD_5 | 13.5
17 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_LONCREK2_5_COKFIELD_5 | -14.7
17 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_LONCREK2_5_COKFIELD_5 | 3.1
17 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_LONCREK2_5_COKFIELD_5 | -28
17 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_LONCREK2_5_COKFIELD_5 | 7.1
17 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_LONCREK2_5_COKFIELD_5 | 0
17 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_LONCREK2_5_COKFIELD_5 | 17.8
17 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_LONCREK2_5_COKFIELD_5 | 0.7
17 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_LONCREK2_5_COKFIELD_5 | 2.4
17 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_LONCREK2_5_COKFIELD_5 | 3.3
17 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_LONCREK2_5_COKFIELD_5 | -2.7
17 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_LONCREK2_5_COKFIELD_5 | -3.1
17 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_LONCREK2_5_COKFIELD_5 | 3.2
17 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_LONCREK2_5_COKFIELD_5 | 2.9
17 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_LONCREK2_5_COKFIELD_5 | -2.9
17 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_LONCREK2_5_COKFIELD_5 | -4.2
17 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_LONCREK2_5_COKFIELD_5 | -17.9
17 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_LONCREK2_5_COKFIELD_5 | -10
17 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_LONCREK2_5_COKFIELD_5 | -18.3
17 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_LONCREK2_5_COKFIELD_5 | -6.9
18 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 18.8
18 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -25.4
18 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 17.8
18 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 20.3
18 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 18.8
18 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 2.3
18 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 4.1
18 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -16.2
18 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 13.4
18 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -9.5
18 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 9.9
18 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -1.2
18 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -11.3
18 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -12
18 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 16.7
18 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 15.3
18 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -18.4
18 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 3.4
18 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -20.4
18 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 8.6
18 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 21.1
18 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 0
18 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -20.4
18 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 2.6
18 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 3.6
18 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -3.1
18 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -3.4
18 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 2.9
18 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 2.6
18 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -2.6
18 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -4.1
18 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -19.8
18 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -9.1
18 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -7.4
18 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | -12.9
19 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 15.2
19 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -15.8
19 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 14.5
19 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 16.5
19 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 19.4
19 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 2.4
19 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 4.2
19 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -13.5
19 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 10.7
19 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -10.2
19 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 9.1
19 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 0.3
19 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -12
19 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -10.4
19 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 13.2
19 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 13.5
19 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -14.8
19 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 3.1
19 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -27.6
19 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 7.2
19 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 0.7
19 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 17.8
19 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 0
19 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 2.4
19 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 3.3
19 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -2.7
19 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -3.1
19 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 3.1
19 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 2.9
19 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -2.9
19 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -4.2
19 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -18
19 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -9.9
19 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -18.3
19 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | -7
20 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 17.4
20 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -21.4
20 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 15.6
20 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 17.8
20 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 17
20 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 2.3
20 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 3.7
20 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -14.3
20 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 11.5
20 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -8.5
20 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 9.2
20 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -0.6
20 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -9.6
20 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -11.1
20 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 15.3
20 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 14.6
20 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -16.2
20 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 3.3
20 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -17.7
20 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 7.6
20 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 18.3
20 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 16.3
20 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -17.6
20 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 0
20 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 3.5
20 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -3
20 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -3.3
20 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 3.1
20 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 2.8
20 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -2.8
20 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -3.7
20 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -19.1
20 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -7.7
20 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -16.8
20 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | -8.3
21 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_GRAHAMSW_8_BARTON_8 | 17.4
21 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_GRAHAMSW_8_BARTON_8 | -21.3
21 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_GRAHAMSW_8_BARTON_8 | 15.8
21 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_GRAHAMSW_8_BARTON_8 | 18
21 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_GRAHAMSW_8_BARTON_8 | 17
21 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_GRAHAMSW_8_BARTON_8 | 2.2
21 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_GRAHAMSW_8_BARTON_8 | 3.5
21 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_GRAHAMSW_8_BARTON_8 | -14.4
21 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_GRAHAMSW_8_BARTON_8 | 11.6
21 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_GRAHAMSW_8_BARTON_8 | -8.3
21 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_GRAHAMSW_8_BARTON_8 | 8.8
21 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_GRAHAMSW_8_BARTON_8 | -1.2
21 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_GRAHAMSW_8_BARTON_8 | -9.8
21 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_GRAHAMSW_8_BARTON_8 | -11.1
21 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_GRAHAMSW_8_BARTON_8 | 15.3
21 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_GRAHAMSW_8_BARTON_8 | 14.7
21 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_GRAHAMSW_8_BARTON_8 | -16.6
21 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_GRAHAMSW_8_BARTON_8 | 0.1
21 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_GRAHAMSW_8_BARTON_8 | -17.7
21 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_GRAHAMSW_8_BARTON_8 | 7.6
21 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_GRAHAMSW_8_BARTON_8 | 18.3
21 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_GRAHAMSW_8_BARTON_8 | 16.4
21 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_GRAHAMSW_8_BARTON_8 | -17.6
21 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_GRAHAMSW_8_BARTON_8 | 2.6
21 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_GRAHAMSW_8_BARTON_8 | 0
21 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_GRAHAMSW_8_BARTON_8 | 0.5
21 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_GRAHAMSW_8_BARTON_8 | -0.1
21 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_GRAHAMSW_8_BARTON_8 | 3.3
21 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_GRAHAMSW_8_BARTON_8 | 3.1
21 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_GRAHAMSW_8_BARTON_8 | -3.1
21 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_GRAHAMSW_8_BARTON_8 | -3.5
21 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_GRAHAMSW_8_BARTON_8 | -19.2
21 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_GRAHAMSW_8_BARTON_8 | -7.8
21 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_GRAHAMSW_8_BARTON_8 | -16.9
21 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_GRAHAMSW_8_BARTON_8 | -8.3
22 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_BARTON_8_ORAN1_8 | 17.4
22 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_BARTON_8_ORAN1_8 | -21.4
22 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_BARTON_8_ORAN1_8 | 15.7
22 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_BARTON_8_ORAN1_8 | 17.9
22 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_BARTON_8_ORAN1_8 | 17
22 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_BARTON_8_ORAN1_8 | 2.2
22 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_BARTON_8_ORAN1_8 | 3.5
22 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_BARTON_8_ORAN1_8 | -14.3
22 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_BARTON_8_ORAN1_8 | 11.5
22 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_BARTON_8_ORAN1_8 | -8.3
22 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_BARTON_8_ORAN1_8 | 8.8
22 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_BARTON_8_ORAN1_8 | -1.2
22 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_BARTON_8_ORAN1_8 | -9.8
22 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_BARTON_8_ORAN1_8 | -11
22 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_BARTON_8_ORAN1_8 | 15.3
22 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_BARTON_8_ORAN1_8 | 14.7
22 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_BARTON_8_ORAN1_8 | -16.5
22 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_BARTON_8_ORAN1_8 | 0.5
22 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_BARTON_8_ORAN1_8 | -17.7
22 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_BARTON_8_ORAN1_8 | 7.6
22 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_BARTON_8_ORAN1_8 | 18.3
22 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_BARTON_8_ORAN1_8 | 16.4
22 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_BARTON_8_ORAN1_8 | -17.6
22 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_BARTON_8_ORAN1_8 | 2.6
22 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_BARTON_8_ORAN1_8 | 0.5
22 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_BARTON_8_ORAN1_8 | 0
22 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_BARTON_8_ORAN1_8 | -0.5
22 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_BARTON_8_ORAN1_8 | 3.3
22 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_BARTON_8_ORAN1_8 | 3
22 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_BARTON_8_ORAN1_8 | -3
22 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_BARTON_8_ORAN1_8 | -3.5
22 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_BARTON_8_ORAN1_8 | -19.2
22 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_BARTON_8_ORAN1_8 | -7.8
22 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_BARTON_8_ORAN1_8 | -16.9
22 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_BARTON_8_ORAN1_8 | -8.3
23 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 17.4
23 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -21.3
23 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 15.6
23 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 17.8
23 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 17
23 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 2.2
23 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 3.5
23 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -14.2
23 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 11.4
23 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -8.2
23 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 8.7
23 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -1.3
23 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -9.8
23 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -11
23 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 15.3
23 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 14.7
23 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -16.5
23 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 0
23 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -17.7
23 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 7.6
23 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 18.3
23 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 16.3
23 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -17.6
23 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 2.5
23 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 1.1
23 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -0.6
23 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 0
23 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 3.2
23 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 2.9
23 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -2.9
23 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -3.5
23 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -19.2
23 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -7.8
23 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -16.9
23 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | -8.3
24 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_LEONSW_8_FLATCRK_T8 | 17.4
24 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_LEONSW_8_FLATCRK_T8 | -21.6
24 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_LEONSW_8_FLATCRK_T8 | 15.7
24 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_LEONSW_8_FLATCRK_T8 | 17.9
24 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_LEONSW_8_FLATCRK_T8 | 17.1
24 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_LEONSW_8_FLATCRK_T8 | 2.2
24 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_LEONSW_8_FLATCRK_T8 | 3.7
24 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_LEONSW_8_FLATCRK_T8 | -14.2
24 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_LEONSW_8_FLATCRK_T8 | 11.5
24 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_LEONSW_8_FLATCRK_T8 | -8.4
24 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_LEONSW_8_FLATCRK_T8 | 8.8
24 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_LEONSW_8_FLATCRK_T8 | -1.2
24 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_LEONSW_8_FLATCRK_T8 | -9.9
24 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_LEONSW_8_FLATCRK_T8 | -10.9
24 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_LEONSW_8_FLATCRK_T8 | 15.4
24 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_LEONSW_8_FLATCRK_T8 | 14.7
24 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_LEONSW_8_FLATCRK_T8 | -16.4
24 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_LEONSW_8_FLATCRK_T8 | 3.3
24 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_LEONSW_8_FLATCRK_T8 | -17.8
24 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_LEONSW_8_FLATCRK_T8 | 7.7
24 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_LEONSW_8_FLATCRK_T8 | 18.4
24 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_LEONSW_8_FLATCRK_T8 | 16.1
24 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_LEONSW_8_FLATCRK_T8 | -17.7
24 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_LEONSW_8_FLATCRK_T8 | 2.4
24 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_LEONSW_8_FLATCRK_T8 | 3.6
24 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_LEONSW_8_FLATCRK_T8 | -3.1
24 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_LEONSW_8_FLATCRK_T8 | -3.3
24 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_LEONSW_8_FLATCRK_T8 | 0
24 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_LEONSW_8_FLATCRK_T8 | -0.3
24 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_LEONSW_8_FLATCRK_T8 | 0.3
24 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_LEONSW_8_FLATCRK_T8 | -3.7
24 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_LEONSW_8_FLATCRK_T8 | -19.1
24 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_LEONSW_8_FLATCRK_T8 | -7.9
24 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_LEONSW_8_FLATCRK_T8 | -17.1
24 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_LEONSW_8_FLATCRK_T8 | -8.2
25 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 17.4
25 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -21.6
25 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 15.6
25 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 17.8
25 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 17.1
25 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 2.2
25 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 3.7
25 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -14.2
25 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 11.4
25 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -8.3
25 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 8.7
25 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -1.2
25 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -9.9
25 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -10.9
25 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 15.4
25 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 14.7
25 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -16.4
25 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 3.3
25 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -17.8
25 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 7.7
25 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 18.4
25 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 16.1
25 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -17.7
25 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 2.4
25 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 3.6
25 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -3
25 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -3.3
25 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 0.3
25 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 0
25 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 0
25 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -3.7
25 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -19.1
25 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -7.9
25 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -17.1
25 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | -8.2
26 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 17.4
26 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -21.6
26 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 15.6
26 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 17.8
26 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 17.1
26 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 2.2
26 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 3.7
26 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -14.2
26 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 11.4
26 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -8.3
26 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 8.7
26 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -1.2
26 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -9.9
26 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -10.9
26 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 15.4
26 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 14.7
26 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -16.4
26 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 3.3
26 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -17.8
26 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 7.7
26 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 18.4
26 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 16.1
26 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -17.7
26 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 2.4
26 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 3.6
26 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -3
26 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -3.3
26 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 0.3
26 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 0
26 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 0
26 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -3.7
26 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -19.1
26 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -7.9
26 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -17.1
26 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | -8.2
27 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_PAIP4B_MURRY_P8 | 17.7
27 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_PAIP4B_MURRY_P8 | -22.4
27 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_PAIP4B_MURRY_P8 | 15.2
27 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_PAIP4B_MURRY_P8 | 17.3
27 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_PAIP4B_MURRY_P8 | 17.5
27 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_PAIP4B_MURRY_P8 | 1.8
27 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_PAIP4B_MURRY_P8 | 0
27 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_PAIP4B_MURRY_P8 | -13.8
27 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_PAIP4B_MURRY_P8 | 11
27 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_PAIP4B_MURRY_P8 | -8.7
27 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_PAIP4B_MURRY_P8 | 8.5
27 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_PAIP4B_MURRY_P8 | -1.2
27 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_PAIP4B_MURRY_P8 | -10.5
27 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_PAIP4B_MURRY_P8 | -10.7
27 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_PAIP4B_MURRY_P8 | 15.7
27 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_PAIP4B_MURRY_P8 | 14.8
27 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_PAIP4B_MURRY_P8 | -16
27 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_PAIP4B_MURRY_P8 | 2.7
27 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_PAIP4B_MURRY_P8 | -18.4
27 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_PAIP4B_MURRY_P8 | 7.4
27 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_PAIP4B_MURRY_P8 | 19
27 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_PAIP4B_MURRY_P8 | 16.5
27 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_PAIP4B_MURRY_P8 | -18.3
27 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_PAIP4B_MURRY_P8 | 2.3
27 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_PAIP4B_MURRY_P8 | 2.9
27 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_PAIP4B_MURRY_P8 | -2.4
27 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_PAIP4B_MURRY_P8 | -2.7
27 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_PAIP4B_MURRY_P8 | 3
27 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_PAIP4B_MURRY_P8 | 2.7
27 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_PAIP4B_MURRY_P8 | -2.7
27 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_PAIP4B_MURRY_P8 | 0
27 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_PAIP4B_MURRY_P8 | -19.3
27 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_PAIP4B_MURRY_P8 | -8
27 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_PAIP4B_MURRY_P8 | -17
27 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_PAIP4B_MURRY_P8 | -8.4
28 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 24.4
28 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -11.3
28 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 15.1
28 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 17.2
28 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 20.5
28 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 2.9
28 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 3.8
28 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -13.6
28 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 10.8
28 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -7
28 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 8
28 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -1.9
28 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -8.4
28 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -10.5
28 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 22.4
28 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -4.5
28 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -16.2
28 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 3.1
28 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -16.2
28 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 7.3
28 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 16.8
28 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 16.7
28 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -16.1
28 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 2.3
28 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 3.3
28 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -2.7
28 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -3.1
28 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 3
28 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 2.7
28 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -2.7
28 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -3.8
28 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 0
28 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -6.2
28 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -17.2
28 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_ABMULCW7_L_BITTCR5_1N | -13.7
29 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_ABMULCW7_OKLA7A | 17.5
29 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_ABMULCW7_OKLA7A | -25.8
29 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_ABMULCW7_OKLA7A | 15.3
29 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_ABMULCW7_OKLA7A | 17.5
29 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_ABMULCW7_OKLA7A | 17.9
29 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_ABMULCW7_OKLA7A | 2.4
29 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_ABMULCW7_OKLA7A | 3.8
29 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_ABMULCW7_OKLA7A | -13.2
29 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_ABMULCW7_OKLA7A | 10.4
29 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_ABMULCW7_OKLA7A | -2.1
29 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_ABMULCW7_OKLA7A | 6.1
29 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_ABMULCW7_OKLA7A | -4.7
29 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_ABMULCW7_OKLA7A | -2.9
29 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_ABMULCW7_OKLA7A | -10.3
29 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_ABMULCW7_OKLA7A | 15.4
29 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_ABMULCW7_OKLA7A | 13.3
29 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_ABMULCW7_OKLA7A | -17.5
29 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_ABMULCW7_OKLA7A | 3.1
29 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_ABMULCW7_OKLA7A | -20
29 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_ABMULCW7_OKLA7A | 7.2
29 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_ABMULCW7_OKLA7A | 20.6
29 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_ABMULCW7_OKLA7A | 17
29 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_ABMULCW7_OKLA7A | -19.9
29 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_ABMULCW7_OKLA7A | 2.1
29 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_ABMULCW7_OKLA7A | 3.2
29 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_ABMULCW7_OKLA7A | -2.7
29 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_ABMULCW7_OKLA7A | -3.1
29 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_ABMULCW7_OKLA7A | 3.1
29 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_ABMULCW7_OKLA7A | 2.8
29 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_ABMULCW7_OKLA7A | -2.8
29 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_ABMULCW7_OKLA7A | -3.8
29 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_ABMULCW7_OKLA7A | -17.8
29 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_ABMULCW7_OKLA7A | 0
29 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_ABMULCW7_OKLA7A | -17.5
29 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_ABMULCW7_OKLA7A | -7.3
30 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_SARC7A_COMCHESS1_5 | 19.4
30 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_SARC7A_COMCHESS1_5 | -26.9
30 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_SARC7A_COMCHESS1_5 | 18.4
30 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_SARC7A_COMCHESS1_5 | 21
30 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_SARC7A_COMCHESS1_5 | 19.5
30 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_SARC7A_COMCHESS1_5 | 2.5
30 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_SARC7A_COMCHESS1_5 | 4.2
30 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_SARC7A_COMCHESS1_5 | -16.7
30 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_SARC7A_COMCHESS1_5 | 13.9
30 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_SARC7A_COMCHESS1_5 | -9.9
30 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_SARC7A_COMCHESS1_5 | 10.1
30 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_SARC7A_COMCHESS1_5 | -1.4
30 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_SARC7A_COMCHESS1_5 | -11.8
30 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_SARC7A_COMCHESS1_5 | -12.4
30 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_SARC7A_COMCHESS1_5 | 17.3
30 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_SARC7A_COMCHESS1_5 | 15.6
30 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_SARC7A_COMCHESS1_5 | -19
30 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_SARC7A_COMCHESS1_5 | 3.6
30 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_SARC7A_COMCHESS1_5 | -21.5
30 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_SARC7A_COMCHESS1_5 | 9.1
30 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_SARC7A_COMCHESS1_5 | 22.1
30 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_SARC7A_COMCHESS1_5 | 3.6
30 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_SARC7A_COMCHESS1_5 | -21.4
30 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_SARC7A_COMCHESS1_5 | 2.7
30 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_SARC7A_COMCHESS1_5 | 3.8
30 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_SARC7A_COMCHESS1_5 | -3.2
30 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_SARC7A_COMCHESS1_5 | -3.6
30 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_SARC7A_COMCHESS1_5 | 3.8
30 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_SARC7A_COMCHESS1_5 | 3.6
30 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_SARC7A_COMCHESS1_5 | -3.6
30 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_SARC7A_COMCHESS1_5 | -4.2
30 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_SARC7A_COMCHESS1_5 | -20.1
30 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_SARC7A_COMCHESS1_5 | -9.7
30 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_SARC7A_COMCHESS1_5 | 0
30 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_SARC7A_COMCHESS1_5 | -15.5
31 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_BLF_CRK7A_ABMULCE7 | 18.7
31 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_BLF_CRK7A_ABMULCE7 | -17.8
31 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_BLF_CRK7A_ABMULCE7 | 14.6
31 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_BLF_CRK7A_ABMULCE7 | 16.7
31 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_BLF_CRK7A_ABMULCE7 | 17.4
31 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_BLF_CRK7A_ABMULCE7 | 2.3
31 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_BLF_CRK7A_ABMULCE7 | 3.7
31 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_BLF_CRK7A_ABMULCE7 | -13.3
31 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_BLF_CRK7A_ABMULCE7 | 10.5
31 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_BLF_CRK7A_ABMULCE7 | -7.6
31 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_BLF_CRK7A_ABMULCE7 | 8
31 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_BLF_CRK7A_ABMULCE7 | -1.4
31 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_BLF_CRK7A_ABMULCE7 | -9.1
31 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_BLF_CRK7A_ABMULCE7 | -10.3
31 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_BLF_CRK7A_ABMULCE7 | 16.6
31 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_BLF_CRK7A_ABMULCE7 | 17.8
31 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_BLF_CRK7A_ABMULCE7 | -15.5
31 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_BLF_CRK7A_ABMULCE7 | 3
31 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_BLF_CRK7A_ABMULCE7 | -16.6
31 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_BLF_CRK7A_ABMULCE7 | 7.1
31 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_BLF_CRK7A_ABMULCE7 | 17.2
31 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_BLF_CRK7A_ABMULCE7 | 18.1
31 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_BLF_CRK7A_ABMULCE7 | -16.5
31 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_BLF_CRK7A_ABMULCE7 | 2.3
31 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_BLF_CRK7A_ABMULCE7 | 3.2
31 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_BLF_CRK7A_ABMULCE7 | -2.7
31 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_BLF_CRK7A_ABMULCE7 | -3
31 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_BLF_CRK7A_ABMULCE7 | 2.9
31 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_BLF_CRK7A_ABMULCE7 | 2.7
31 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_BLF_CRK7A_ABMULCE7 | -2.7
31 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_BLF_CRK7A_ABMULCE7 | -3.7
31 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_BLF_CRK7A_ABMULCE7 | -22.3
31 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_BLF_CRK7A_ABMULCE7 | -7.1
31 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_BLF_CRK7A_ABMULCE7 | -18.9
31 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_BLF_CRK7A_ABMULCE7 | 0
32 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 0
32 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -32.5
32 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 14.7
32 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 16.8
32 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 20.5
32 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 2.7
32 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 4
32 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -13.5
32 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 10.7
32 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -8.6
32 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 8.5
32 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -0.8
32 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -10.2
32 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -10.4
32 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -2.1
32 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 22.6
32 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -15.4
32 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 3.1
32 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -14.6
32 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 7.2
32 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 15.2
32 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 17.4
32 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -14.5
32 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 2.3
32 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 3.3
32 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -2.7
32 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -3.1
32 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 3.1
32 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 2.8
32 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -2.8
32 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -4
32 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -27.1
32 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -8
32 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -17.9
32 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_SWEETWTR_5_LONCREK2_5 | -10.9
33 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_Single_ABMULCE7_LONGCREK_5 | 26.1
33 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_Single_ABMULCE7_LONGCREK_5 | 0
33 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_Single_ABMULCE7_LONGCREK_5 | 13.9
33 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_Single_ABMULCE7_LONGCREK_5 | 15.8
33 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_Single_ABMULCE7_LONGCREK_5 | 19.7
33 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_Single_ABMULCE7_LONGCREK_5 | 2.2
33 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_Single_ABMULCE7_LONGCREK_5 | 4.5
33 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_Single_ABMULCE7_LONGCREK_5 | -13.3
33 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_Single_ABMULCE7_LONGCREK_5 | 10.5
33 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_Single_ABMULCE7_LONGCREK_5 | -12.5
33 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_Single_ABMULCE7_LONGCREK_5 | 9.9
33 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_Single_ABMULCE7_LONGCREK_5 | 1.8
33 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_Single_ABMULCE7_LONGCREK_5 | -14.5
33 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_Single_ABMULCE7_LONGCREK_5 | -10.2
33 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_Single_ABMULCE7_LONGCREK_5 | 24
33 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_Single_ABMULCE7_LONGCREK_5 | 5.8
33 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_Single_ABMULCE7_LONGCREK_5 | -13.7
33 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_Single_ABMULCE7_LONGCREK_5 | 3
33 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_Single_ABMULCE7_LONGCREK_5 | -11.3
33 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_Single_ABMULCE7_LONGCREK_5 | 7
33 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_Single_ABMULCE7_LONGCREK_5 | 12
33 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_Single_ABMULCE7_LONGCREK_5 | 18.8
33 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_Single_ABMULCE7_LONGCREK_5 | -11.3
33 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_Single_ABMULCE7_LONGCREK_5 | 2.4
33 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_Single_ABMULCE7_LONGCREK_5 | 3.3
33 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_Single_ABMULCE7_LONGCREK_5 | -2.7
33 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_Single_ABMULCE7_LONGCREK_5 | -3
33 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_Single_ABMULCE7_LONGCREK_5 | 3.3
33 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_Single_ABMULCE7_LONGCREK_5 | 3
33 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_Single_ABMULCE7_LONGCREK_5 | -3
33 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_Single_ABMULCE7_LONGCREK_5 | -4.5
33 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_Single_ABMULCE7_LONGCREK_5 | -10.3
33 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_Single_ABMULCE7_LONGCREK_5 | -12.5
33 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_Single_ABMULCE7_LONGCREK_5 | -19.3
33 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_Single_ABMULCE7_LONGCREK_5 | -3.2
34 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 2.1
34 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -23.6
34 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 14.3
34 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 16.3
34 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 26.8
34 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 3.8
34 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 4.3
34 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -13
34 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 10.2
34 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -7.1
34 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 7.8
34 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -1.4
34 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -8.4
34 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -10.1
34 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 0
34 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 0
34 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -15.3
34 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 3
34 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -11.2
34 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 6.9
34 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 11.8
34 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 18.5
34 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -11
34 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 2.2
34 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 3.2
34 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -2.7
34 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -3
34 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 3
34 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 2.8
34 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -2.8
34 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -4.3
34 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -4.5
34 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -5.8
34 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -19.1
34 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | -19.1
35 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 2.1
35 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -22.1
35 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 14.2
35 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 16.2
35 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 28.2
35 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 4
35 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 4.4
35 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -12.9
35 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 10.1
35 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -6.8
35 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 7.7
35 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -1.6
35 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -8.1
35 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -10
35 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 0
35 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -4.5
35 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -15.2
35 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 3
35 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -10.4
35 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 6.9
35 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 11
35 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 18.7
35 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -10.3
35 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 2.2
35 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 3.2
35 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -2.7
35 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -3
35 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 3
35 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 2.8
35 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -2.8
35 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -4.4
35 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 0
35 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -5.4
35 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -19.4
35 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | -20.9
36 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 0
36 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -24.6
36 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 14.2
36 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 16.2
36 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 27.5
36 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 3.9
36 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 4.4
36 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -12.9
36 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 10.1
36 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -7.1
36 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 7.8
36 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -1.4
36 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -8.4
36 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -10.1
36 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -2.1
36 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 0
36 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -15.2
36 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 3
36 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -10.7
36 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 6.9
36 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 11.2
36 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 18.7
36 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -10.5
36 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 2.2
36 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 3.2
36 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -2.7
36 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -3
36 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 3.1
36 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 2.8
36 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -2.8
36 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -4.4
36 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -4.5
36 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -5.7
36 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -19.3
36 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | -19.8
37 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 17.7
37 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -26.8
37 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 15.3
37 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 17.5
37 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 18.3
37 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 2.2
37 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 4.3
37 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -12.9
37 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 10.1
37 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 0
37 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 5.2
37 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -6
37 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 0
37 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -10.2
37 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 15.7
37 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 13.3
37 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -17.9
37 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 3.1
37 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -20.6
37 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 7.1
37 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 21.2
37 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 17.3
37 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -20.5
37 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 2
37 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 3.3
37 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -2.8
37 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -3.1
37 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 3.1
37 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 2.9
37 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -2.9
37 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -4.3
37 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -17.7
37 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 0.5
37 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -17.8
37 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | -7.2
38 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 7.4
38 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 4.7
38 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 11.6
38 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 13.1
38 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 28.1
38 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 2.8
38 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 5.8
38 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -12.1
38 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 9.3
38 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -17.5
38 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 11.4
38 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 5.8
38 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -19.9
38 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -9.4
38 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 5.4
38 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 9.2
38 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -10
38 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 2.9
38 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 0
38 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 6.1
38 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 0
38 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 23.4
38 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 0.7
38 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 2.4
38 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 3.2
38 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -2.7
38 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -2.9
38 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 3.5
38 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 3.3
38 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -3.3
38 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -5.8
38 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -13.7
38 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -17.5
38 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -24
38 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | -1.6
39 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 7.6
39 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 4.2
39 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 11.7
39 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 13.2
39 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 27.9
39 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 2.8
39 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 5.8
39 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -12.1
39 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 9.4
39 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -17.3
39 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 11.4
39 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 5.7
39 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -19.7
39 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -9.4
39 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 5.6
39 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 9.3
39 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -10.2
39 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 2.9
39 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 0
39 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 6.1
39 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 0.7
39 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 23.3
39 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 0
39 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 2.4
39 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 3.2
39 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -2.7
39 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -2.9
39 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 3.5
39 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 3.3
39 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -3.3
39 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -5.8
39 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -13.8
39 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -17.4
39 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -23.8
39 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | -1.8
40 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 16.9
40 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -19.7
40 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 0
40 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 21.8
40 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 16.3
40 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 2.3
40 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 3.7
40 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -16.6
40 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 13.8
40 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -7.9
40 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 9.5
40 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -3.1
40 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -9.7
40 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -13.7
40 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 14.8
40 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 14.5
40 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -20.8
40 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 3.8
40 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -16.6
40 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 0
40 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 17.2
40 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 18.3
40 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -16.5
40 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 2.9
40 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 4
40 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -3.5
40 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -3.8
40 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 3.6
40 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 3.4
40 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -3.4
40 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -3.7
40 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -19
40 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -7.8
40 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -18.6
40 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | -7.2
41 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 16.3
41 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -17.6
41 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 0
41 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 0
41 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 15.5
41 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 2.3
41 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 3.6
41 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -28.8
41 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 26
41 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -8
41 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 13.4
41 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -7.1
41 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -10
41 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -17.9
41 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 14.2
41 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 14.4
41 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -33.3
41 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 4.7
41 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -15.3
41 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 12.1
41 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 15.9
41 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 20.6
41 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -15.2
41 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 3.5
41 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 4.9
41 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -4.4
41 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -4.7
41 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 4.2
41 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 3.9
41 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -3.9
41 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -3.6
41 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -18.9
41 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -8.1
41 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -20.7
41 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | -5.9
42 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 0
42 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 0
42 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 11.4
42 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 12.8
42 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 29.6
42 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 3
42 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 6
42 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -11.9
42 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 9.2
42 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -17.7
42 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 11.4
42 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 6
42 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -20.1
42 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -9.2
42 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -2.1
42 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 12.6
42 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -9.7
42 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 2.9
42 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 1.6
42 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 6
42 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -1.1
42 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 23.9
42 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 1.8
42 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 2.4
42 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 3.2
42 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -2.7
42 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -2.9
42 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 3.6
42 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 3.3
42 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -3.3
42 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -6
42 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -17.1
42 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -17.6
42 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -24.5
42 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | -2.7
43 | CSC_1_SWEETWTR_5 _LONCREK2_5 _1420_1439 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 0
43 | CSC_1_LONGCREK_5 _ABMULCE7 _1435_6230 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -23
43 | CSC_1_GRHAMSES1_5_BENBRK_5_1430_1873 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 14.1
43 | CSC_1_GRHAMSES1_5_PARKER_5_1430_1436 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 16.1
43 | CSC_1_TONKAWAWI_5_GRHAMSES1_5_1048_1430 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 28.9
43 | CSC_1_CHINAGRV_8_RADIUMMT_8_1318_1398 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 4.1
43 | CSC_1_MURRY_P8_GRHAMSES1_8_1371_1431 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 4.4
43 | CSC_1_WILLOWCK_5_JACKSBRO_5_1421_1429 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -12.8
43 | CSC_1_WILLOWCK_5_PARKER_5_1421_1436 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 10
43 | CSC_1_BOWMAN_5_FISHRDSS1_5_1422_1425 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -6.8
43 | CSC_1_BOWMAN_5_JACKSBRO_5_1422_1429 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 7.7
43 | CSC_1_BOWMAN_5_GRHAMSES1_5_1422_1430 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -1.5
43 | CSC_1_FISHRDSS1_5_OKLA7A_1425_6100 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -8.1
43 | CSC_1_W_DENT_5_JACKSBRO_5_988_1429 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -10
43 | CSC_1_MRGNCRK_5_SWEETWTR_5_1030_1420 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -2.1
43 | CSC_1_MRGNCRK_5_L_BITTCR5_1N_1030_71050 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -4.5
43 | CSC_1_JACKSBRO_5_GRHAMSES1_5_1429_1430 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -15.2
43 | CSC_1_GRHAMSES1_8_GRAHAME_8_1431_1601 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 3
43 | CSC_1_GRHAMSES1_5_LONGCREK_5_1430_1435 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -9.9
43 | CSC_1_PARKER_5_BENBRK_A_T5_1436_1869 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 6.8
43 | CSC_1_LONCREK2_5_COKFIELD_5_1439_1442 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 10.4
43 | CSC_1_COMCHESS1_5_COMCHPKW_5_1440_1900 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 18.9
43 | CSC_1_GRHAMSES1_5_COKFIELD_5_1430_1442 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -9.7
43 | CSC_1_LKAROWHD_8_NEWPRT_P8_1468_1470 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 2.2
43 | CSC_1_GRAHAMSW_8_BARTON_8_1596_1599 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 3.2
43 | CSC_1_ORAN1_8_BARTON_8_1571_1599 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -2.7
43 | CSC_1_GRAHAMSW_8_GRAHAME_8_1596_1601 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -3
43 | CSC_1_LEONSW_8_FLATCRK_T8_1624_1642 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 3
43 | CSC_1_LINGLVLL_P8_STPHNVIL_8_1640_1641 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 2.8
43 | CSC_1_LINGLVLL_P8_FLATCRK_T8_1640_1642 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -2.8
43 | CSC_1_MURRY_P8_PAIP4B_1371_6169 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -4.4
43 | CSC_1_ABMULCW7_L_BITTCR5_1N_6235_71050 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 0
43 | CSC_1_OKLA7A_ABMULCW7_6100_6235 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -5.3
43 | CSC_1_COMCHESS1_5_SARC7A_1440_6444 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -19.6
43 | CSC_1_ABMULCE7_BLF_CRK7A_6230_60040 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | -21.5

## S-N CSC_2 PTDFs
Contingency # | Element | Contingency | PTDF | Top one | SF | Second from Top | SF | Third from Top | SF | Third from Bottom | SF | Second from Bottom | SF | Bottom One | SF
Base Case | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | Base Case | -17.9
Base Case | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | Base Case | -19.6
Base Case | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | Base Case | -13.4
Base Case | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | Base Case | -14
Base Case | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | Base Case | 10.7
Base Case | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | Base Case | -9.1
Base Case | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | Base Case | -18.4
Base Case | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | Base Case | -18.5
Base Case | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | Base Case | -17.8
Base Case | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | Base Case | 2.6
Base Case | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | Base Case | -2.6
Base Case | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | Base Case | -1.9
Base Case | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | Base Case | -2.4
Base Case | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | Base Case | -18.4
Base Case | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | Base Case | -13.1
Base Case | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | Base Case | 18.3
Base Case | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | Base Case | -14.3
Base Case | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | Base Case | 2.7
Base Case | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | Base Case | 2.7
Base Case | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | Base Case | -3.1
1 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_VENUS_S5_THOUSE__5 | -16.2
1 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_VENUS_S5_THOUSE__5 | -17.9
1 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_VENUS_S5_THOUSE__5 | 0
1 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_VENUS_S5_THOUSE__5 | -20.6
1 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_VENUS_S5_THOUSE__5 | 9
1 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_VENUS_S5_THOUSE__5 | -7.7
1 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_VENUS_S5_THOUSE__5 | -17
1 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_VENUS_S5_THOUSE__5 | -17.1
1 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_VENUS_S5_THOUSE__5 | -16.2
1 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_VENUS_S5_THOUSE__5 | 2.5
1 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_VENUS_S5_THOUSE__5 | -2.5
1 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_VENUS_S5_THOUSE__5 | -1.8
1 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_VENUS_S5_THOUSE__5 | -2.2
1 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_VENUS_S5_THOUSE__5 | -17.2
1 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_VENUS_S5_THOUSE__5 | -12.5
1 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_VENUS_S5_THOUSE__5 | 17.1
1 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_VENUS_S5_THOUSE__5 | -13.5
1 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_VENUS_S5_THOUSE__5 | 2.9
1 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_VENUS_S5_THOUSE__5 | 2.9
1 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_VENUS_S5_THOUSE__5 | -3.4
2 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_VENUS_N5_THOUSE__5 | -16.2
2 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_VENUS_N5_THOUSE__5 | -17.9
2 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_VENUS_N5_THOUSE__5 | -20.3
2 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_VENUS_N5_THOUSE__5 | 0
2 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_VENUS_N5_THOUSE__5 | 8.9
2 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_VENUS_N5_THOUSE__5 | -7.6
2 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_VENUS_N5_THOUSE__5 | -16.9
2 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_VENUS_N5_THOUSE__5 | -17
2 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_VENUS_N5_THOUSE__5 | -16.1
2 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_VENUS_N5_THOUSE__5 | 2.5
2 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_VENUS_N5_THOUSE__5 | -2.5
2 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_VENUS_N5_THOUSE__5 | -1.8
2 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_VENUS_N5_THOUSE__5 | -2.2
2 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_VENUS_N5_THOUSE__5 | -17.2
2 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_VENUS_N5_THOUSE__5 | -12.5
2 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_VENUS_N5_THOUSE__5 | 17.1
2 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_VENUS_N5_THOUSE__5 | -13.5
2 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_VENUS_N5_THOUSE__5 | 2.9
2 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_VENUS_N5_THOUSE__5 | 2.9
2 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_VENUS_N5_THOUSE__5 | -3.4
3 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -18.9
3 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -18.4
3 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -13.2
3 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -13.8
3 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | 0
3 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -17.8
3 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -18.3
3 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -18.4
3 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -18.8
3 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | 2.5
3 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -2.5
3 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -1.9
3 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -2.4
3 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -18.3
3 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -13
3 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | 18.2
3 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -14.2
3 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | 2.7
3 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | 2.7
3 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | -3.1
4 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -18.7
4 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -18.7
4 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -13.3
4 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -13.8
4 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | 18.3
4 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | 0
4 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -18.3
4 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -18.4
4 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -18.6
4 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | 2.6
4 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -2.6
4 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -1.9
4 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -2.4
4 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -18.3
4 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -13
4 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | 18.2
4 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -14.3
4 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | 2.7
4 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | 2.7
4 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | -3.1
5 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -16.4
5 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -17.8
5 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -12.2
5 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -12.8
5 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_TEMPSSLT__5_SANDOW__5 | 10
5 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -8.5
5 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_TEMPSSLT__5_SANDOW__5 | 0
5 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -31.1
5 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -16.1
5 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_TEMPSSLT__5_SANDOW__5 | 2.8
5 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -2.7
5 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -1.9
5 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -3.5
5 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -16.5
5 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -12.3
5 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_TEMPSSLT__5_SANDOW__5 | 16.4
5 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -13
5 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_TEMPSSLT__5_SANDOW__5 | 2.8
5 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_TEMPSSLT__5_SANDOW__5 | 2.8
5 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_TEMPSSLT__5_SANDOW__5 | -3.2
6 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_TEMP_SS__5_SANDOW__5 | -16.4
6 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_TEMP_SS__5_SANDOW__5 | -17.8
6 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_TEMP_SS__5_SANDOW__5 | -12.2
6 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_TEMP_SS__5_SANDOW__5 | -12.8
6 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_TEMP_SS__5_SANDOW__5 | 10
6 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_TEMP_SS__5_SANDOW__5 | -8.5
6 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_TEMP_SS__5_SANDOW__5 | -31
6 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_TEMP_SS__5_SANDOW__5 | 0
6 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_TEMP_SS__5_SANDOW__5 | -16.1
6 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_TEMP_SS__5_SANDOW__5 | 2.8
6 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_TEMP_SS__5_SANDOW__5 | -2.7
6 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_TEMP_SS__5_SANDOW__5 | -1.9
6 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_TEMP_SS__5_SANDOW__5 | -3.6
6 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_TEMP_SS__5_SANDOW__5 | -16.5
6 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_TEMP_SS__5_SANDOW__5 | -12.3
6 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_TEMP_SS__5_SANDOW__5 | 16.4
6 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_TEMP_SS__5_SANDOW__5 | -13
6 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_TEMP_SS__5_SANDOW__5 | 2.8
6 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_TEMP_SS__5_SANDOW__5 | 2.8
6 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_TEMP_SS__5_SANDOW__5 | -3.2
7 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -1.9
7 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -30.7
7 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -12.1
7 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -12.7
7 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | 17.3
7 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -14.7
7 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -16.8
7 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -16.9
7 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | 0
7 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | 4.2
7 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -3.3
7 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -2.4
7 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -2.6
7 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -17.2
7 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -12.5
7 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | 17.1
7 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -13.5
7 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | 2.9
7 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | 2.9
7 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | -3.3
8 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -18
8 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -19.8
8 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -13.4
8 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -14
8 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | 10.7
8 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -9.1
8 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -18.4
8 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -18.5
8 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -18.1
8 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | 0
8 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -2.3
8 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -1.8
8 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -2.3
8 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -18.4
8 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -13.1
8 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | 18.3
8 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -14.3
8 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | 2.7
8 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | 2.7
8 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | -3.1
9 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -18.6
9 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -20.5
9 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -13.3
9 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -13.9
9 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | 10.3
9 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -8.8
9 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -18.4
9 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -18.5
9 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -18.3
9 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | 1.4
9 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | 0
9 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -2.3
9 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -2.2
9 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -18.4
9 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -13
9 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | 18.3
9 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -14.3
9 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | 2.7
9 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | 2.7
9 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | -3.1
10 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -18.3
10 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -20.1
10 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -13.4
10 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -14
10 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | 10.6
10 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -9
10 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -18.4
10 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -18.5
10 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -18.1
10 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | 2.3
10 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -3
10 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | 0
10 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -2.3
10 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -18.4
10 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -13
10 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | 18.3
10 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -14.3
10 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | 2.7
10 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | 2.7
10 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | -3.1
11 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -17.9
11 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -19.7
11 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -13.3
11 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -13.9
11 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | 10.6
11 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -9
11 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -19.2
11 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -19.3
11 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -18
11 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | 2.2
11 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -2.4
11 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -1.8
11 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | 0
11 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -18.3
11 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -13
11 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | 18.2
11 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -14.2
11 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | 2.7
11 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | 2.7
11 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | -3.1
12 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -16.8
12 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -18.4
12 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -12.5
12 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -13.1
12 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | 10.2
12 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -8.6
12 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -16.6
12 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -16.7
12 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -16.7
12 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | 2.6
12 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -2.6
12 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -1.9
12 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -2.3
12 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | 0
12 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -12.1
12 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | 30.9
12 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -12.4
12 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | 2.8
12 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | 2.8
12 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | -3.2
13 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -17.5
13 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -19.1
13 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -13
13 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -13.6
13 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | 10.5
13 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -8.9
13 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -17.7
13 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -17.8
13 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -17.4
13 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | 2.5
13 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -2.6
13 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -1.9
13 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -2.3
13 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -17.5
13 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | 0
13 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | 17.4
13 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -21.1
13 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | 2.7
13 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | 2.7
13 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | -3.1
14 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -16.8
14 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -18.4
14 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -12.5
14 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -13.1
14 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | 10.2
14 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -8.6
14 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -16.7
14 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -16.8
14 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -16.7
14 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | 2.6
14 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -2.6
14 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -1.9
14 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -2.3
14 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -31
14 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -12.1
14 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | 0
14 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -12.4
14 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | 2.8
14 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | 2.8
14 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | -3.2
15 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -17.5
15 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -19.2
15 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -13.1
15 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -13.7
15 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | 10.5
15 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -8.9
15 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -17.7
15 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -17.8
15 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -17.4
15 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | 2.6
15 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -2.6
15 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -1.9
15 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -2.3
15 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -17.4
15 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -17.2
15 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | 17.3
15 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | 0
15 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | 2.7
15 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | 2.7
15 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | -3.1
16 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -18.4
16 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -20.1
16 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -13.8
16 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -14.5
16 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | 11
16 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -9.3
16 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -18.6
16 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -18.7
16 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -18.3
16 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | 2.6
16 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -2.7
16 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -2
16 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -2.4
16 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -18.6
16 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -13.1
16 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | 18.5
16 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -14.5
16 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | 0
16 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | 0
16 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | -0.9
17 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -18.4
17 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -20.1
17 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -13.8
17 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -14.5
17 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | 11
17 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -9.3
17 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -18.6
17 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -18.7
17 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -18.3
17 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | 2.6
17 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -2.7
17 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -2
17 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -2.4
17 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -18.6
17 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -13.1
17 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | 18.5
17 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -14.5
17 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | 0
17 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | 0
17 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | -0.9
18 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -18.6
18 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -20.3
18 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -14
18 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -14.7
18 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | 11.1
18 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -9.4
18 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -18.7
18 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -18.8
18 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -18.4
18 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | 2.6
18 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -2.8
18 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -2
18 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -2.4
18 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -18.7
18 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -13.1
18 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | 18.6
18 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | -14.6
18 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | 0
18 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | 0
18 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | 0
19 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -11.1
19 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -12.9
19 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | 0
19 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | 0
19 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | 3.9
19 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -3.4
19 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -12.8
19 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -12.9
19 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -11.3
19 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | 2.1
19 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -2
19 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -1.5
19 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -1.7
19 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -13.7
19 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -10.7
19 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | 13.6
19 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -11.2
19 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | 3.7
19 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | 3.7
19 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | -4.2
20 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | 0
20 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -30.8
20 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -11.6
20 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -12.1
20 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | 31.7
20 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | 0
20 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -16.6
20 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -16.7
20 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -0.4
20 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | 3.2
20 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -3.7
20 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -2.7
20 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -2.4
20 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -17
20 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -12.4
20 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | 16.9
20 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -13.4
20 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | 2.9
20 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | 2.9
20 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | -3.4
21 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -8.1
21 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -8.2
21 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -5.7
21 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -6.4
21 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | 6.4
21 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -5.4
21 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | 0
21 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | 0
21 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -6.9
21 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | 3.9
21 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -2.9
21 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -2.1
21 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -9.8
21 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -6.2
21 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -8
21 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | 6.2
21 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -6
21 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | 3.4
21 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | 3.4
21 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | -3.9
22 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -4.7
22 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | 0
22 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -5.7
22 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -6.3
22 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | 6.3
22 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -5.2
22 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -9
22 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -9.1
22 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | 0
22 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | 10.2
22 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -8.5
22 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -6
22 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -3.3
22 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -11.3
22 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -9.7
22 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | 11.2
22 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -9.5
22 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | 3.9
22 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | 3.9
22 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | -4.5
23 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | 0
23 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | 0
23 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -4.9
23 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -5.5
23 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | 7.5
23 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -6.2
23 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -8.8
23 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -8.8
23 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -2
23 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | 7.6
23 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -10
23 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -6.9
23 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -2.9
23 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -10.9
23 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -9.5
23 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | 10.9
23 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -9.3
23 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | 4
23 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | 4
23 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | -4.7
24 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -10.9
24 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -11.7
24 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -7.5
24 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -8.2
24 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | 7.3
24 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -6.2
24 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -7.4
24 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -7.5
24 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -10.4
24 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | 2.5
24 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -2.3
24 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -1.7
24 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -1.5
24 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | 0
24 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -6.6
24 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | 0
24 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -1.8
24 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | 3.2
24 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | 3.2
24 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | -3.7
25 | CSC_2_THOUSE__5_TEMP_PEC__5_3405_3412 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -16.5
25 | CSC_2_LAKE_CRK1_5_TEMP_SS__5_3409_3414 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -18.1
25 | CSC_2_VENUS_S5_THOUSE__5_1906_3405 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -12.3
25 | CSC_2_VENUS_N5_THOUSE__5_1907_3405 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -12.8
25 | CSC_2_LAKE_CRK2_5_THOUSE__5_3402_3405 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | 10
25 | CSC_2_THOUSE__5_LAKE_CRK1_5_3405_3409 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -8.5
25 | CSC_2_TEMPSSLT__5_SANDOW__5_3413_3429 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -16.3
25 | CSC_2_TEMP_SS__5_SANDOW__5_3414_3429 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -16.4
25 | CSC_2_TEMP_PEC__5_TEMP_SS__5_3412_3414 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -16.4
25 | CSC_2_TEMP_SS__8_TEMP_PEC__8_3415_3420 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | 2.5
25 | CSC_2_LAKE_CRK1_8_TEMP_PEC__8_3410_3420 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -2.6
25 | CSC_2_WACOWOOD1_8_COTTONB_T_8_3591_13591 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -1.8
25 | CSC_2_TEMP_SS__8_ROGERS1A_8_3415_3675 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -2.2
25 | CSC_2_SANDOW__5_L_AUSTRO5_1Y_3429_7040 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -15.3
25 | CSC_2_L_AUSTRO5_1Y_L_ZORN__5_2Y_7040_7045 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | 0
25 | CSC_2_L_AUSTRO5_1Y_SAND_TXU_5_7040_13429 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | 15.2
25 | CSC_2_L_AUSTRO5_1Y_L_GARFIE5_1Y_7040_7048 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | 0
25 | CSC_2_L_ADAMSV8_1Y_L_EVANT_8_1Y_7066_7068 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | 2.8
25 | CSC_2_L_EVANT_8_1Y_L_GOLDTH8_1Y_7068_7070 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | 2.8
25 | CSC_2_BRNWDSW_8_L_GOLDTH8_1Y_1655_7070 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | -3.2

## N-H CSC_4 PTDFs
Contingency # | Element | Contingency | PTDF | Top one | SF | Second from Top | SF | Third from Top | SF | Third from Bottom | SF | Second from Bottom | SF | Bottom One | SF
Base Case | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | Base Case | 15.5
Base Case | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | Base Case | 17.1
Base Case | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | Base Case | 17.7
Base Case | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | Base Case | 16.2
Base Case | CSC_4_KING____345A_KUYDAL745005_40900_45971 | Base Case | -11.5
Base Case | CSC_4_KING____345A_KUYDAL755010_40900_45972 | Base Case | -16.2
Base Case | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | Base Case | -11.5
1 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_Single_GIBN_CREK_5_OBRIEN__345A | 0
1 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_Single_GIBN_CREK_5_OBRIEN__345A | 20
1 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_Single_GIBN_CREK_5_OBRIEN__345A | 20.3
1 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_Single_GIBN_CREK_5_OBRIEN__345A | 22.6
1 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_Single_GIBN_CREK_5_OBRIEN__345A | -12.5
1 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_Single_GIBN_CREK_5_OBRIEN__345A | -22.6
1 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_Single_GIBN_CREK_5_OBRIEN__345A | -12.5
2 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_Single_JEWETT_S5_T_H_W___345B | 19.7
2 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_Single_JEWETT_S5_T_H_W___345B | 0
2 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_Single_JEWETT_S5_T_H_W___345B | 22.1
2 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_Single_JEWETT_S5_T_H_W___345B | 19.9
2 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_Single_JEWETT_S5_T_H_W___345B | -14.1
2 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_Single_JEWETT_S5_T_H_W___345B | -19.9
2 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_Single_JEWETT_S5_T_H_W___345B | -14.1
3 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_Single_JEWETT_N5_TOMBAL__345B | 19.3
3 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_Single_JEWETT_N5_TOMBAL__345B | 21.5
3 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_Single_JEWETT_N5_TOMBAL__345B | 0
3 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_Single_JEWETT_N5_TOMBAL__345B | 21
3 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_Single_JEWETT_N5_TOMBAL__345B | -0.8
3 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_Single_JEWETT_N5_TOMBAL__345B | -21
3 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_Single_JEWETT_N5_TOMBAL__345B | -0.8
4 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_Single_ROANS___345C_KUYDAL755010 | 22.5
4 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_Single_ROANS___345C_KUYDAL755010 | 19.9
4 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_Single_ROANS___345C_KUYDAL755010 | 21.3
4 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_Single_ROANS___345C_KUYDAL755010 | 0
4 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_Single_ROANS___345C_KUYDAL755010 | -15.1
4 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_Single_ROANS___345C_KUYDAL755010 | 0
4 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_Single_ROANS___345C_KUYDAL755010 | -15.1
5 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_Single_KUYDAL745005_KING____345A | 16.1
5 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_Single_KUYDAL745005_KING____345A | 18
5 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_Single_KUYDAL745005_KING____345A | 13.8
5 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_Single_KUYDAL745005_KING____345A | 17.9
5 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_Single_KUYDAL745005_KING____345A | 0
5 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_Single_KUYDAL745005_KING____345A | -17.9
5 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_Single_KUYDAL745005_KING____345A | 0
6 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_Single_KUYDAL755010_KING____345A | 22.5
6 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_Single_KUYDAL755010_KING____345A | 19.9
6 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_Single_KUYDAL755010_KING____345A | 21.3
6 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_Single_KUYDAL755010_KING____345A | 0
6 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_Single_KUYDAL755010_KING____345A | -15.1
6 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_Single_KUYDAL755010_KING____345A | 0
6 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_Single_KUYDAL755010_KING____345A | -15.1
7 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_Single_TOMBAL__345B_KUYDAL745005 | 16.1
7 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_Single_TOMBAL__345B_KUYDAL745005 | 18
7 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_Single_TOMBAL__345B_KUYDAL745005 | 13.8
7 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_Single_TOMBAL__345B_KUYDAL745005 | 17.9
7 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_Single_TOMBAL__345B_KUYDAL745005 | 0
7 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_Single_TOMBAL__345B_KUYDAL745005 | -17.9
7 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_Single_TOMBAL__345B_KUYDAL745005 | 0
8 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_GIBN_CREK_5_ROANS___345C | 0
8 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_GIBN_CREK_5_ROANS___345C | 25.8
8 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_GIBN_CREK_5_ROANS___345C | 27.1
8 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_GIBN_CREK_5_ROANS___345C | 3.7
8 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_GIBN_CREK_5_ROANS___345C | -18.2
8 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_GIBN_CREK_5_ROANS___345C | -3.7
8 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_GIBN_CREK_5_ROANS___345C | -18.2
9 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_OBRIEN__345A_T_H_W___345B | 0
9 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_OBRIEN__345A_T_H_W___345B | 19.9
9 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_OBRIEN__345A_T_H_W___345B | 20.3
9 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_OBRIEN__345A_T_H_W___345B | 22.5
9 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_OBRIEN__345A_T_H_W___345B | -12.5
9 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_OBRIEN__345A_T_H_W___345B | -22.5
9 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_OBRIEN__345A_T_H_W___345B | -12.5
10 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_JEWETT_S5_T_H_W___345B_AND_JEWETT_N5_TOMBAL__345B | 26.2
10 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_JEWETT_S5_T_H_W___345B_AND_JEWETT_N5_TOMBAL__345B | 0
10 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_JEWETT_S5_T_H_W___345B_AND_JEWETT_N5_TOMBAL__345B | 0
10 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_JEWETT_S5_T_H_W___345B_AND_JEWETT_N5_TOMBAL__345B | 27.6
10 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_JEWETT_S5_T_H_W___345B_AND_JEWETT_N5_TOMBAL__345B | -0.7
10 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_JEWETT_S5_T_H_W___345B_AND_JEWETT_N5_TOMBAL__345B | -27.6
10 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_JEWETT_S5_T_H_W___345B_AND_JEWETT_N5_TOMBAL__345B | -0.7
11 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_JEWETT_S5_T_H_W___345B_AND_OBRIEN__345A_T_H_W___345B | 19.5
11 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_JEWETT_S5_T_H_W___345B_AND_OBRIEN__345A_T_H_W___345B | 0
11 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_JEWETT_S5_T_H_W___345B_AND_OBRIEN__345A_T_H_W___345B | 22.3
11 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_JEWETT_S5_T_H_W___345B_AND_OBRIEN__345A_T_H_W___345B | 20.1
11 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_JEWETT_S5_T_H_W___345B_AND_OBRIEN__345A_T_H_W___345B | -14.2
11 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_JEWETT_S5_T_H_W___345B_AND_OBRIEN__345A_T_H_W___345B | -20.1
11 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_JEWETT_S5_T_H_W___345B_AND_OBRIEN__345A_T_H_W___345B | -14.2
12 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_ROANS___345C_KUYDAL755010 | 29.9
12 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_ROANS___345C_KUYDAL755010 | 26.6
12 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_ROANS___345C_KUYDAL755010 | 0
12 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_ROANS___345C_KUYDAL755010 | 0
12 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_ROANS___345C_KUYDAL755010 | -2.7
12 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_ROANS___345C_KUYDAL755010 | 0
12 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_ROANS___345C_KUYDAL755010 | -2.7
13 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_TOMBAL__345B_KUYDAL745005 | 19.2
13 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_TOMBAL__345B_KUYDAL745005 | 21.5
13 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_TOMBAL__345B_KUYDAL745005 | 0
13 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_TOMBAL__345B_KUYDAL745005 | 21.1
13 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_TOMBAL__345B_KUYDAL745005 | 0
13 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_TOMBAL__345B_KUYDAL745005 | -21.1
13 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_TOMBAL__345B_KUYDAL745005 | 0
14 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_GIBN_CREK_5_ROANS___345C | 28.1
14 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_GIBN_CREK_5_ROANS___345C | 25.8
14 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_GIBN_CREK_5_ROANS___345C | 0
14 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_GIBN_CREK_5_ROANS___345C | 3.7
14 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_GIBN_CREK_5_ROANS___345C | -2.4
14 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_GIBN_CREK_5_ROANS___345C | -3.7
14 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_GIBN_CREK_5_ROANS___345C | -2.4
15 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_KUYDAL745005_KING____345A_AND_KUYDAL755010_KING____345A | 24.1
15 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_KUYDAL745005_KING____345A_AND_KUYDAL755010_KING____345A | 21.5
15 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_KUYDAL745005_KING____345A_AND_KUYDAL755010_KING____345A | 16.7
15 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_KUYDAL745005_KING____345A_AND_KUYDAL755010_KING____345A | 0
15 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_KUYDAL745005_KING____345A_AND_KUYDAL755010_KING____345A | 0
15 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_KUYDAL745005_KING____345A_AND_KUYDAL755010_KING____345A | 0
15 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_KUYDAL745005_KING____345A_AND_KUYDAL755010_KING____345A | 0
16 | CSC_4_GIBN_CREK_5_OBRIEN__345A_967_44500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_JEWETT_S5_T_H_W___345B | 0
16 | CSC_4_JEWETT_S5_T_H_W___345B_3390_45500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_JEWETT_S5_T_H_W___345B | 0
16 | CSC_4_JEWETT_N5_TOMBAL__345B_3391_46500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_JEWETT_S5_T_H_W___345B | 26.6
16 | CSC_4_ROANS___345C_KUYDAL755010_40600_45972 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_JEWETT_S5_T_H_W___345B | 29.2
16 | CSC_4_KING____345A_KUYDAL745005_40900_45971 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_JEWETT_S5_T_H_W___345B | -16
16 | CSC_4_KING____345A_KUYDAL755010_40900_45972 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_JEWETT_S5_T_H_W___345B | -29.2
16 | CSC_4_KUYDAL745005_TOMBAL__345B_45971_46500 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_JEWETT_S5_T_H_W___345B | -16

## W-N & N-W Contingencies
Contingency # | Contingency Name | From Bus | Name | To Bus | Name | From Bus | Name | To Bus | Name
1 | CTG_Single_MRGNCRK_5_SWEETWTR_5 | 1030 | MRGNCRK_5 | 1420 | SWEETWTR_5
2 | CTG_Single_MRGNCRK_5_L_BITTCR5_1N | 1030 | MRGNCRK_5 | 71050 | L_BITTCR5_1N
3 | CTG_Single_TONKAWAWI_5_GRHAMSES1_5 | 1048 | TONKAWAWI_5 | 1430 | GRHAMSES1_5
4 | CTG_Single_CHINAGRV_8_RADIUMMT_8 | 1318 | CHINAGRV_8 | 1398 | RADIUMMT_8
5 | CTG_Single_MURRY_P8_GRHAMSES1_8 | 1371 | MURRY_P8 | 1431 | GRHAMSES1_8
6 | CTG_Single_WILLOWCK_5_JACKSBRO_5 | 1421 | WILLOWCK_5 | 1429 | JACKSBRO_5
7 | CTG_Single_WILLOWCK_5_PARKER_5 | 1421 | WILLOWCK_5 | 1436 | PARKER_5
8 | CTG_Single_BOWMAN_5_FISHRDSS1_5 | 1422 | BOWMAN_5 | 1425 | FISHRDSS1_5
9 | CTG_Single_BOWMAN_5_JACKSBRO_5 | 1422 | BOWMAN_5 | 1429 | JACKSBRO_5
10 | CTG_Single_BOWMAN_5_GRHAMSES1_5 | 1422 | BOWMAN_5 | 1430 | GRHAMSES1_5
11 | CTG_Single_FISHRDSS1_5_OKLA7A | 1425 | FISHRDSS1_5 | 6100 | OKLA7A
12 | CTG_Single_JACKSBRO_5_W_DENT_5 | 1429 | JACKSBRO_5 | 988 | W_DENT_5
13 | CTG_Single_GRHAMSES1_5_JACKSBRO_5 | 1430 | GRHAMSES1_5 | 1429 | JACKSBRO_5
14 | CTG_Single_GRHAMSES1_8_GRAHAME_8 | 1431 | GRHAMSES1_8 | 1601 | GRAHAME_8
15 | CTG_Single_LONGCREK_5_GRHAMSES1_5 | 1435 | LONGCREK_5 | 1430 | GRHAMSES1_5
16 | CTG_Single_PARKER_5_BENBRK_A_T5 | 1436 | PARKER_5 | 1869 | BENBRK_A_T5
17 | CTG_Single_LONCREK2_5_COKFIELD_5 | 1439 | LONCREK2_5 | 1442 | COKFIELD_5
18 | CTG_Single_COMCHESS1_5_COMCHPKW_5 | 1440 | COMCHESS1_5 | 1900 | COMCHPKW_5
19 | CTG_Single_COKFIELD_5_GRHAMSES1_5 | 1442 | COKFIELD_5 | 1430 | GRHAMSES1_5
20 | CTG_Single_LKAROWHD_8_NEWPRT_P8 | 1468 | LKAROWHD_8 | 1470 | NEWPRT_P8
21 | CTG_Single_GRAHAMSW_8_BARTON_8 | 1596 | GRAHAMSW_8 | 1599 | BARTON_8
22 | CTG_Single_BARTON_8_ORAN1_8 | 1599 | BARTON_8 | 1571 | ORAN1_8
23 | CTG_Single_GRAHAME_8_GRAHAMSW_8 | 1601 | GRAHAME_8 | 1596 | GRAHAMSW_8
24 | CTG_Single_LEONSW_8_FLATCRK_T8 | 1624 | LEONSW_8 | 1642 | FLATCRK_T8
25 | CTG_Single_LINGLVLL_P8_STPHNVIL_8 | 1640 | LINGLVLL_P8 | 1641 | STPHNVIL_8
26 | CTG_Single_FLATCRK_T8_LINGLVLL_P8 | 1642 | FLATCRK_T8 | 1640 | LINGLVLL_P8
27 | CTG_Single_PAIP4B_MURRY_P8 | 6169 | PAIP4B | 1371 | MURRY_P8
28 | CTG_Single_ABMULCW7_L_BITTCR5_1N | 6235 | ABMULCW7 | 71050 | L_BITTCR5_1N
29 | CTG_Single_ABMULCW7_OKLA7A | 6235 | ABMULCW7 | 6100 | OKLA7A
30 | CTG_Single_SARC7A_COMCHESS1_5 | 6444 | SARC7A | 1440 | COMCHESS1_5
31 | CTG_Single_BLF_CRK7A_ABMULCE7 | 60040 | BLF_CRK7A | 6230 | ABMULCE7
32 | CTG_Single_SWEETWTR_5_LONCREK2_5 | 1420 | SWEETWTR_5 | 1439 | LONCREK2_5
33 | CTG_Single_ABMULCE7_LONGCREK_5 | 6230 | ABMULCE7 | 1435 | LONGCREK_5
34 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_MRGNCRK_5_L_BITTCR5_1N | 1030 | MRGNCRK_5 | 1420 | SWEETWTR_5 | 1030 | MRGNCRK_5 | 71050 | L_BITTCR5_1N
35 | CTG_double_MRGNCRK_5_SWEETWTR_5_AND_ABMULCW7_L_BITTCR5_1N | 1030 | MRGNCRK_5 | 1420 | SWEETWTR_5 | 6235 | ABMULCW7 | 71050 | L_BITTCR5_1N
36 | CTG_double_MRGNCRK_5_L_BITTCR5_1N_AND_SWEETWTR_5_LONCREK2_5 | 1030 | MRGNCRK_5 | 71050 | L_BITTCR5_1N | 1420 | SWEETWTR_5 | 1439 | LONCREK2_5
37 | CTG_double_BOWMAN_5_FISHRDSS1_5_AND_FISHRDSS1_5_OKLA7A | 1422 | BOWMAN_5 | 1425 | FISHRDSS1_5 | 1425 | FISHRDSS1_5 | 6100 | OKLA7A
38 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_LONCREK2_5_COKFIELD_5 | 1435 | LONGCREK_5 | 1430 | GRHAMSES1_5 | 1439 | LONCREK2_5 | 1442 | COKFIELD_5
39 | CTG_double_LONGCREK_5_GRHAMSES1_5_AND_COKFIELD_5_GRHAMSES1_5 | 1435 | LONGCREK_5 | 1430 | GRHAMSES1_5 | 1442 | COKFIELD_5 | 1430 | GRHAMSES1_5
40 | CTG_double_PARKER_5_BENBRK_A_T5_AND_GRHAMSES1_5_BENBRK_5 | 1436 | PARKER_5 | 1869 | BENBRK_A_T5 | 1430 | GRHAMSES1_5 | 1873 | BENBRK_5
41 | CTG_double_GRHAMSES1_5_BENBRK_5_AND_GRHAMSES1_5_PARKER_5 | 1430 | GRHAMSES1_5 | 1873 | BENBRK_5 | 1430 | GRHAMSES1_5 | 1436 | PARKER_5
42 | CTG_double_ABMULCE7_LONGCREK_5_AND_SWEETWTR_5_LONCREK2_5 | 6230 | ABMULCE7 | 1435 | LONGCREK_5 | 1420 | SWEETWTR_5 | 1439 | LONCREK2_5
43 | CTG_double_SWEETWTR_5_LONCREK2_5_AND_ABMULCW7_L_BITTCR5_1N | 1420 | SWEETWTR_5 | 1439 | LONCREK2_5 | 6235 | ABMULCW7 | 71050 | L_BITTCR5_1N

## S-N & N-S Contingencies 1
Contingency # | Contingency Name | From Bus | Name | To Bus | Name | From Bus | Name | To Bus | Name
1 | CTG_Single_VENUS_S5_THOUSE__5 | 1906 | VENUS_S5 | 3405 | THOUSE__5
2 | CTG_Single_VENUS_N5_THOUSE__5 | 1907 | VENUS_N5 | 3405 | THOUSE__5
3 | CTG_Single_LAKE_CRK2_5_THOUSE__5 | 3402 | LAKE_CRK2_5 | 3405 | THOUSE__5
4 | CTG_Single_LAKE_CRK1_5_THOUSE__5 | 3409 | LAKE_CRK1_5 | 3405 | THOUSE__5
5 | CTG_Single_TEMPSSLT__5_SANDOW__5 | 3413 | TEMPSSLT__5 | 3429 | SANDOW__5
6 | CTG_Single_TEMP_SS__5_SANDOW__5 | 3414 | TEMP_SS__5 | 3429 | SANDOW__5
7 | CTG_Single_TEMP_SS__5_TEMP_PEC__5 | 3414 | TEMP_SS__5 | 3412 | TEMP_PEC__5
8 | CTG_Single_TEMP_SS__8_TEMP_PEC__8 | 3415 | TEMP_SS__8 | 3420 | TEMP_PEC__8
9 | CTG_Single_TEMP_PEC__8_LAKE_CRK1_8 | 3420 | TEMP_PEC__8 | 3410 | LAKE_CRK1_8
10 | CTG_Single_WACOWOOD1_8_COTTONB_T_8 | 3591 | WACOWOOD1_8 | 13591 | COTTONB_T_8
11 | CTG_Single_ROGERS1A_8_TEMP_SS__8 | 3675 | ROGERS1A_8 | 3415 | TEMP_SS__8
12 | CTG_Single_L_AUSTRO5_1Y_SANDOW__5 | 7040 | L_AUSTRO5_1Y | 3429 | SANDOW__5
13 | CTG_Single_L_AUSTRO5_1Y_L_ZORN__5_2Y | 7040 | L_AUSTRO5_1Y | 7045 | L_ZORN__5_2Y
14 | CTG_Single_L_AUSTRO5_1Y_SAND_TXU_5 | 7040 | L_AUSTRO5_1Y | 13429 | SAND_TXU_5
15 | CTG_Single_L_GARFIE5_1Y_L_AUSTRO5_1Y | 7048 | L_GARFIE5_1Y | 7040 | L_AUSTRO5_1Y
16 | CTG_Single_L_ADAMSV8_1Y_L_EVANT_8_1Y | 7066 | L_ADAMSV8_1Y | 7068 | L_EVANT_8_1Y
17 | CTG_Single_L_EVANT_8_1Y_L_GOLDTH8_1Y | 7068 | L_EVANT_8_1Y | 7070 | L_GOLDTH8_1Y
18 | CTG_Single_L_GOLDTH8_1Y_BRNWDSW_8 | 7070 | L_GOLDTH8_1Y | 1655 | BRNWDSW_8
19 | CTG_double_VENUS_S5_THOUSE__5_AND_VENUS_N5_THOUSE__5 | 1906 | VENUS_S5 | 3405 | THOUSE__5 | 1907 | VENUS_N5 | 3405 | THOUSE__5
20 | CTG_double_LAKE_CRK1_5_THOUSE__5_AND_TEMP_PEC__5_THOUSE__5 | 3409 | LAKE_CRK1_5 | 3405 | THOUSE__5 | 3412 | TEMP_PEC__5 | 3405 | THOUSE__5
21 | CTG_double_TEMP_SS__5_SANDOW__5_AND_TEMPSSLT__5_SANDOW__5 | 3414 | TEMP_SS__5 | 3429 | SANDOW__5 | 3413 | TEMPSSLT__5 | 3429 | SANDOW__5
22 | CTG_double_TEMP_SS__5_TEMP_PEC__5_AND_TEMP_SS__5_LAKE_CRK1_5 | 3414 | TEMP_SS__5 | 3412 | TEMP_PEC__5 | 3414 | TEMP_SS__5 | 3409 | LAKE_CRK1_5
23 | CTG_double_TEMP_SS__5_LAKE_CRK1_5_AND_TEMP_PEC__5_THOUSE__5 | 3414 | TEMP_SS__5 | 3409 | LAKE_CRK1_5 | 3412 | TEMP_PEC__5 | 3405 | THOUSE__5
24 | CTG_double_L_AUSTRO5_1Y_SANDOW__5_AND_L_AUSTRO5_1Y_SAND_TXU_5 | 7040 | L_AUSTRO5_1Y | 3429 | SANDOW__5 | 7040 | L_AUSTRO5_1Y | 13429 | SAND_TXU_5
25 | CTG_double_L_AUSTRO5_1Y_L_ZORN__5_2Y_AND_L_GARFIE5_1Y_L_AUSTRO5_1Y | 7040 | L_AUSTRO5_1Y | 7045 | L_ZORN__5_2Y | 7048 | L_GARFIE5_1Y | 7040 | L_AUSTRO5_1Y

## N-H Contingencies
Contingency # | Contingency Name | From Bus | Name | To Bus | Name | From Bus | Name | To Bus | Name
1 | CTG_Single_GIBN_CREK_5_OBRIEN__345A | 967 | GIBN_CREK_5 | 44500 | OBRIEN__345A
2 | CTG_Single_JEWETT_S5_T_H_W___345B | 3390 | JEWETT_S5 | 45500 | T_H_W___345B
3 | CTG_Single_JEWETT_N5_TOMBAL__345B | 3391 | JEWETT_N5 | 46500 | TOMBAL__345B
4 | CTG_Single_ROANS___345C_KUYDAL755010 | 40600 | ROANS___345C | 45972 | KUYDAL755010
5 | CTG_Single_KUYDAL745005_KING____345A | 45971 | KUYDAL745005 | 40900 | KING____345A
6 | CTG_Single_KUYDAL755010_KING____345A | 45972 | KUYDAL755010 | 40900 | KING____345A
7 | CTG_Single_TOMBAL__345B_KUYDAL745005 | 46500 | TOMBAL__345B | 45971 | KUYDAL745005
8 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_GIBN_CREK_5_ROANS___345C | 967 | GIBN_CREK_5 | 44500 | OBRIEN__345A | 967 | GIBN_CREK_5 | 40600 | ROANS___345C
9 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_OBRIEN__345A_T_H_W___345B | 967 | GIBN_CREK_5 | 44500 | OBRIEN__345A | 44500 | OBRIEN__345A | 45500 | T_H_W___345B
10 | CTG_double_JEWETT_S5_T_H_W___345B_AND_JEWETT_N5_TOMBAL__345B | 3390 | JEWETT_S5 | 45500 | T_H_W___345B | 3391 | JEWETT_N5 | 46500 | TOMBAL__345B
11 | CTG_double_JEWETT_S5_T_H_W___345B_AND_OBRIEN__345A_T_H_W___345B | 3390 | JEWETT_S5 | 45500 | T_H_W___345B | 44500 | OBRIEN__345A | 45500 | T_H_W___345B
12 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_ROANS___345C_KUYDAL755010 | 3391 | JEWETT_N5 | 46500 | TOMBAL__345B | 40600 | ROANS___345C | 45972 | KUYDAL755010
13 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_TOMBAL__345B_KUYDAL745005 | 3391 | JEWETT_N5 | 46500 | TOMBAL__345B | 46500 | TOMBAL__345B | 45971 | KUYDAL745005
14 | CTG_double_JEWETT_N5_TOMBAL__345B_AND_GIBN_CREK_5_ROANS___345C | 3391 | JEWETT_N5 | 46500 | TOMBAL__345B | 967 | GIBN_CREK_5 | 40600 | ROANS___345C
15 | CTG_double_KUYDAL745005_KING____345A_AND_KUYDAL755010_KING____345A | 45971 | KUYDAL745005 | 40900 | KING____345A | 45972 | KUYDAL755010 | 40900 | KING____345A
16 | CTG_double_GIBN_CREK_5_OBRIEN__345A_AND_JEWETT_S5_T_H_W___345B | 967 | GIBN_CREK_5 | 44500 | OBRIEN__345A | 3390 | JEWETT_S5 | 45500 | T_H_W___345B