| OGRR Number | 208 | OGRR Title | Voltage Ride-Through (VRT) Requirement |
| --- | --- | --- | --- |

| Date | September 30, 2008 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Kenneth A. Donohoo |
| E-mail Address | Kdonoho1@oncor.com |
| Company | Oncor Electric Delivery Company, LLC |
| Phone Number | 214-743-6823 |
| Cell Number | 214-437-5287 |
| Market Segment | IOU |

Comments

| Overall Market Benefit |  |
| --- | --- |
| Overall Market Impact |  |
| Consumer Impact |  |

Oncor supports the requirement for Voltage Ride Through (VRT) capability on Wind-powered Generation Resources (WGRs).  The need for VRT has been well established by FERC Order 661A issued December 12, 2005 with the concurrence of American Wind Energy Association (AWEA) and the North American Electric Reliability Corporation (NERC).

Oncor performed a brief stability study to illustrate the effect a fault can have on West Texas voltage.

The load flow case and dynamics file used in the simulation are the 2007 ROS Dynamics Working Group (DWG) wind flat start case and dynamics file.  This case and associated dynamics file include wind generation modeled in detail using the available wind dynamic models. The load model used is the normal ZIP model. Note that the load model used does not accurately account for motor dynamics, so the results shown in this report are likely optimistic; that is the voltage will likely drop lower and the recovery time will likely be longer than illustrated in this report.

The contingency consisted of a three phase to ground fault near Odessa on one circuit of the Odessa to Morgan Creek 345 kV line. The fault was normally cleared in 4 cycles by removing the faulted circuit.

The attached spreadsheet lists the low point voltage at 42 buses in west Texas.  As expected, the low point voltage is near zero at the fault location.  Perhaps more surprising is that at about 50 miles (geographic, not circuit miles) away the voltage drop can be greater than 60%.  At 100 miles from the fault location, the voltage drop can be greater than 35%. Even at about 230 miles from the fault point the Graham 345 kV bus saw a 15 % voltage drop.  It should be noted that a 400 MVA synchronous generator is connected to the 345 kV bus at Graham.

The attached graphs show bus voltage at monitored buses over a 4 second interval for this contingency.  As expected the graphs show the voltage recovers significantly after the fault is removed.  This initial recovery varies from around 60% of normal to about 90%.  Then in many cases the voltage begins to decline before rapidly recovering to a value within normal operating range.  If uncorrected the voltage decline suggests an impending voltage collapse.  The voltage recovery from this decline is primarily due to the action of dynamic reactive devices such as synchronous generators and the application of some very fast acting switched capacitors.  As can be seen, the voltage within some facilities is very low for several cycles after the fault is removed.  Also note that a relatively high recovery voltage occurred at some buses.

Finally, wind generation at five locations tripped as a result of the fault.

Oncor supports additional accurate and appropriate studies (including detailed modeling of wind farms) need to be performed.  We are also concerned that there may already be a reliability concern with wind generation tripping off during faults.

Proposed Guide Language Revision

None.