## Slide 1: ERCOT Proposed Ancillary Service Methodology
Operations Planning
October 2nd, 2008

## Slide 2: Proposed Changes
Regulation Reserve
  Accounts for the expected increase in installed Wind Generation for the upcoming month
  Provision to increase regulation requirements if the last 30 day average CPS1 score falls below 100
Non-Spin Reserve
  Moves away from a flat 1354 MW procurement around peak load hours
  Considers Load Forecast Risk and Wind Forecast Risk

## Slide 3: Regulation Proposal
Continue to calculate the 98.8 percentile for the up and down regulation service deployed in the previous month with an expectation of running out of Regulation 1.2% of the intervals.
Utilize the GE Report to determine the impact of additional wind capacity for the upcoming month. The tables in the GE report indicate an amount of regulation up and down to add for each additional 1000 MW of wind capacity added to the system.
Maintain a rolling 12 month CPS1 score of 100 or greater by monitoring the CPS1 score of the previous 30 days.

## Slide 4: Non-Spin Proposal
The proposal eliminates a flat 1354 MW purchase of Non-Spin Reserves around Peak Load hours.
The combination of wind forecast uncertainty and load forecast uncertainty creates net load uncertainty that must be mitigated through ancillary services for each hour of the day.
The GE Report indicated that wind generation could be treated as negative load and load minus wind generation equals net load.
The change in procurement would ensure that enough Non-Spin capacity is purchased such that the Non-Spin capacity plus Regulation Up capacity would cover 95% of the errors observed in the Net Load Forecast over the last 90 days.

## Slide 5: Why is Non-Spin needed in Off Peak Hours?
Risk is no longer limited to Load forecast uncertainty and forced outages of generation. It includes Wind forecast uncertainty.
The next two slides show an example of risk associated with low Load and high wind output.
This example uses the resource plans from April 16th
  Generation Forced outage rates of the same category of generation from GADS
  Load Forecast accuracy distribution calculated from the last 5 years of data
  GE wind forecast accuracy distribution used from the GE Report.

## Slide 6: Sample Study 04-16-2008 at 2AM: Wind Replacement
Total Online Capacity [MW] | Wind Capacity [MW] (Included in Total Capacity) | Risk (LOLP) (Considers 1150 MW Demand Response)
30821 | 4345 | 1 day every 8.16 months
27275 (Wind replaced by 20% Conv. Gen.) | 0 | 1 day every 10.8 months
27584 (Wind replaced by 25% Conv. Gen.) | 0 | 1 day every 1.41 years
30820 (Wind replaced by 100% Conv. Gen.) | 0 | 1 day every 907 years
Load: 23347 MW |  | 

## Slide 7: Sample Study 04-16-2008 at 2AM: Fast Start
Total Capacity [MW] | Fast Start [MW] (Included in Total Capacity) | Risk (LOLP) (Considers 1150 MW Demand Response)
30821 | 0 | 1 day every 8.16 months
31387 | 566 | 1 day every 1.65 years
31952 | 1131 | 1 day every 4.24 years
32528 | 1707 | 1 day every 12.1 years
33089 | 2268 | 1 day every 36.5 years
Load: 23347 MW Wind: 4345 MW |  | 

## Slide 8: What is the increase to the Non-Spin Procurement Cost?
For hours in which Non-Spin was purchased, use the MCPC for that hour times the new quantity of Non-Spin (quantity may be higher or lower)
For all off-peak hours during which Non-Spin was not purchased, assume a clearing price of $4 per MWh.
For all on-peak hours during which Non-Spin was not purchased, assume that the clearing price for that hour would be equal to clearing price at the hour during which Non-Spin was first purchased for the day.
Assume that self arranged Non-Spin has the same MCPC value

## Slide 9
Cost of Non-Spin with Assumptions
Month | Off-Peak (1-6,22,24) or On-Peak (7-22) | Cost Using Old Methodology | Cost Using New Methodology
June | Off-Peak | $0.00 | $572,155.63
 | On-Peak | $9,024,504.78 | $9,873,673.35
July | Off-Peak | $0.00 | $1,199,205.58
 | On-Peak | $5,172,604.96 | $5,824,400.00
August | Off-Peak | $0.00 | $1,523,258.05
 | On-Peak | $4,381,747.10 | $6,698,622.29
September | Off-Peak | $0.00 | $1,592,004.21
 | On-Peak | $2,058,513.28 | $3,304,884.44
Total | Off-Peak | $0.00 | $4,886,623.47
 | On-Peak | $20,637,370.12 | $25,701,580.08
Total Price Difference for 4 Months of Study: ~$9.95 Million

## Slide 10
Non-Spin for September
 |  |  |  |  |  | NSRS Procurement
Hour Ending | 95th Percentile of Net Load Error combining On- and Off- Peak | 95th Percentile of MTLF Error | 95th Percentile of WGRPP Error | Reg. Up Requirement for Upcoming Month | Average Reg. Up On- and Off- Peak | 95th Percentile of all On- and Off Peak Hour Separately
1 | 2390 | 1515 | 1548 | 840 | 731 | 1658
2 | 2390 | 1648 | 1322 | 875 | 731 | 1658
3 | 2390 | 1633 | 1584 | 600 | 731 | 1658
4 | 2390 | 1752 | 1460 | 600 | 731 | 1658
5 | 2390 | 1834 | 1244 | 605 | 731 | 1658
6 | 2390 | 1954 | 1335 | 625 | 731 | 1658
7 | 2069 | 2184 | 1414 | 1065 | 840 | 1229
8 | 2069 | 2154 | 1139 | 630 | 840 | 1229
9 | 2069 | 1924 | 732 | 950 | 840 | 1229
10 | 2069 | 1727 | 706 | 835 | 840 | 1229
11 | 2069 | 1758 | 772 | 935 | 840 | 1229
12 | 2069 | 2034 | 754 | 960 | 840 | 1229
13 | 2069 | 2287 | 569 | 810 | 840 | 1229
14 | 2069 | 2092 | 501 | 795 | 840 | 1229
15 | 2069 | 2113 | 656 | 880 | 840 | 1229
16 | 2069 | 2009 | 967 | 780 | 840 | 1229
17 | 2069 | 1624 | 789 | 765 | 840 | 1229
18 | 2069 | 1609 | 533 | 615 | 840 | 1229
19 | 2069 | 1264 | 699 | 885 | 840 | 1229
20 | 2069 | 1020 | 682 | 955 | 840 | 1229
21 | 2069 | 1433 | 809 | 1010 | 840 | 1229
22 | 2069 | 1484 | 1108 | 565 | 840 | 1229
23 | 2390 | 1514 | 1374 | 815 | 731 | 1658
24 | 2390 | 1768 | 1869 | 890 | 731 | 1658
Blue = Off-Peak, Green = On-Peak

## Slide 11: Non-Spin for September (cont.)

## Slide 12
Non-Spin for October
 |  |  |  |  |  | NSRS Procurement
Hour Ending | 95th Percentile of Net Load Error combining On- and Off- Peak | 95th Percentile of MTLF Error | 95th Percentile of WGRPP Error | Reg. Up Requirement for Upcoming Month | Average Reg. Up On- and Off- Peak | 95th Percentile of all On- and Off Peak Hour Separately
1 | 2216 | 1029 | 1736 | 840 | 756 | 1460
2 | 2216 | 1300 | 1810 | 845 | 756 | 1460
3 | 2216 | 1290 | 1697 | 635 | 756 | 1460
4 | 2216 | 1329 | 1561 | 455 | 756 | 1460
5 | 2216 | 1344 | 1394 | 575 | 756 | 1460
6 | 2216 | 1650 | 1434 | 1150 | 756 | 1460
7 | 1878 | 2055 | 1422 | 1305 | 881 | 998
8 | 1878 | 1988 | 1257 | 945 | 881 | 998
9 | 1878 | 1688 | 695 | 1140 | 881 | 998
10 | 1878 | 1686 | 753 | 1000 | 881 | 998
11 | 1878 | 1656 | 778 | 695 | 881 | 998
12 | 1878 | 1549 | 268 | 690 | 881 | 998
13 | 1878 | 1503 | 587 | 805 | 881 | 998
14 | 1878 | 1784 | 927 | 680 | 881 | 998
15 | 1878 | 1783 | 745 | 540 | 881 | 998
16 | 1878 | 1246 | 1170 | 750 | 881 | 998
17 | 1878 | 1007 | 897 | 735 | 881 | 998
18 | 1878 | 932 | 941 | 970 | 881 | 998
19 | 1878 | 849 | 949 | 880 | 881 | 998
20 | 1878 | 845 | 684 | 1215 | 881 | 998
21 | 1878 | 1104 | 997 | 1110 | 881 | 998
22 | 1878 | 1218 | 1401 | 630 | 881 | 998
23 | 2216 | 1306 | 1903 | 760 | 756 | 1460
24 | 2216 | 1272 | 2021 | 790 | 756 | 1460
Blue = Off-Peak, Green = On-Peak

## Slide 13
Regulation for October
Current Methodology
Proposed Methodology (Affected Values in Yellow)
IE | Up | Down
1 | 835 | 875
2 | 835 | 515
3 | 635 | 805
4 | 455 | 760
5 | 575 | 580
6 | 1145 | 745
7 | 1295 | 825
8 | 945 | 1180
9 | 1140 | 865
10 | 990 | 650
11 | 695 | 900
12 | 690 | 705
13 | 795 | 725
14 | 680 | 805
15 | 540 | 860
16 | 750 | 680
17 | 735 | 755
18 | 955 | 785
19 | 880 | 1005
20 | 1210 | 910
21 | 1110 | 870
22 | 630 | 935
23 | 760 | 930
24 | 785 | 840
IE | Up | Down
1 | 840 | 875
2 | 845 | 525
3 | 635 | 805
4 | 455 | 760
5 | 575 | 580
6 | 1150 | 745
7 | 1305 | 825
8 | 945 | 1180
9 | 1140 | 865
10 | 1000 | 650
11 | 695 | 905
12 | 690 | 710
13 | 805 | 725
14 | 680 | 805
15 | 540 | 860
16 | 750 | 685
17 | 735 | 755
18 | 970 | 805
19 | 880 | 1005
20 | 1215 | 925
21 | 1110 | 885
22 | 630 | 935
23 | 760 | 935
24 | 790 | 845