## Questionnaire
| ERCOT Station ID | WGR 5, 6 & 7 | WGR5 | WGR6 | WGR7 | WGR 8 & 9 | WGR8 | WGR9 | WGR1 | WGR2 | WGR3 | WGR4
1 | Name of farm
2 | Name of interconnection TSP (who is interconnection agreement with) | AEP | AEP | AEP | AEP | Oncor | Oncor | Oncor | Oncor | Oncor | Oncor | Oncor
3 | QSE
4 | Interconnection point (station)
5 | How many miles of transmission are on your side of the interconnection point? | 12 miles 138KV |  |  |  | 28 miles 138 kv |  |  | 6 miles 138 kv | 6.2 miles 138 kv | 10 miles 345 kv | 5 miles 345kv
| Turbine Manufacturer |  | VESTAS | GENERAL ELECTRIC | SIEMENS | Mitsubishi 1000A | Mitsubishi 1000A | Mitsubishi 1000A | SIEMENS | GAMESA | SIEMENS | MITSUBISHI
6 | How may wind turbines are installed on your farm and what is the total installed capacity of your wind farm in MW. |  | 67 turbines 1.8MW each 120.6MW total | 155 turbines 1.5MW each 232.5MW total | 74 turbines 2.3MW each 170.2MW total | 160 turbines 1MW each 160MW total | 99 turbines 1MW each 99MW total | 61 turbines 1MW each 61MW total | 54 turbines 2.3MW each 124.2MW total | 45 turbines 2MW each 90MW total | 55 turbines 2.3MW each 126.5MW total | 209 turbines 1MW each 209MW total
7 | Please describe how your facility responds to balancing energy instructions. (energy dispatch instructions) |  | Verbal instructions from QSE to control room | Verbal instructions from QSE to control room | Verbal instructions from QSE to control room | QSE calls operator. Operator stops units. 25 turbines at a time (one circuit at a time) |  |  | QSE calls and a follow up email | QSE calls | QSE calls | QSE calls
8 | What is the transmission injection voltage (345/138/69 kV)? | 138KV | 138KV | 138KV | 138KV | 138KV |  |  | 138kV | 138kV | 345kV | 345kV
9 | How many circuit miles of transmission line are on your side of the generator breaker? Also give the voltage (345/138/69 kV)? | 8miles 138KV | 8 miles 138KV |  |  | ? |  |  | N/A | N/A | 10 - miles 345kV | 5 - miles 345kV
10 | Is your control room “On-Site” or “Remote” from your wind farm? |  | Remote Palm Springs, CA | Remote Palm Springs, CA | Remote Palm Springs, CA | Onsite - Office hours Remote - Rest of the time Phone forwarded to XXX home |  |  | Remote- Plans to move to Austin in 2 months | Remote- Plans to move to Austin in 2 months | On Site-day Remote - night (Austin) | On Site-day Remote - night (Austin)
11 | Is your control room staffed 24 X 7? If not explain how off hour request are completed. List all 24 X 7 phone number(s) in order of preference. | Yes | Yes | Yes | Yes | Yes |  |  | Yes | Yes | Yes | Yes
12 | To request a change in your voltage set point, does the TSP contact you directly or are you requiring them to go through your QSE? |  | Contact directly | Contact directly | Contact directly | Contacts directly. No voltage control. Have to shut down turbines. Plant is set to unit pf to be sure pf remains above 0.95 |  |  | Contact directly Dedicated line in Oncor PBX trunk | Contact directly Dedicated line in Oncor PBX trunk | Contact directly Dedicated line in Oncor PBX trunk | Contact directly Dedicated line in Oncor PBX trunk
13 | How long does it take to make a voltage set point change when requested by the TSP or QSE? |  | Less than 30 Mins | Less than 30 Mins | Less than 30 Mins | we can shut off turbines thus raising the voltage right away |  |  | < 2kV 5 minutes Up to 1 1/2 hrs for changes on the GSU taps | < 2kV 5 minutes Up to 1 1/2 hrs for changes on the GSU taps | < 2kV 5 minutes Up to 1 for changes on the GSU taps | 1 hr for voltage changes Remote SCADA in 2 months
14 | At what locations does your staff monitor voltage. Low side of GSU, High Side of GSU, Point of interconnect, etc? |  | Low and Highside of GSU at the substations | Low and Highside of GSU at the substations | Low and Highside of GSU at the substations | Through SCADA, low side, high side and interconnection voltage
15 | Please explain how your Automatic Voltage Control works. (Control system with generator set point, capacitor /reactor switching, LTC tap change, etc.) Indicate if SCADA is used in any of the methods. |  | Utilizes a combination of LTC on the main GSU and switched shunt caps on the turbines and in the subs 34.5kv bus. This system normally operates on a pf schedule | Utilizes (+/-)0.95 dynamic pf control of GE turbines coordinated with automatic switching of 34.5kv shunt caps on low side of GSU. Noramlly operates on voltage regulation schedule | Utilizes (+/-)0.90 dynamic pf control of siemens turbines and is planned to operate on pf schedule | Replays and meters control cap switching based on voltage and var flows. LTC is automatic |  |  | AVR @ termial of the generator & Park Pilot system monitoring the 34.5kV (medium) bus for larger steps | AVR @ termial of the generator & Park Pilot system monitoring the 34.5kV (medium) bus for larger steps | AVR @ termial of the generator & Park Pilot system monitoring the 34.5kV (medium) bus for larger steps | Inductive motor 600V LTC set to 34.5kV
16 | On your AVR, Where is the input voltage for control measured. | Low side of XFMR | Low side of transformer - 34.5kv | Low side of transformer - 34.5kv | Low side of transformer - 34.5kv | High side bus. Vars measured on lowside |  |  | At the lowside of the GSU 34.5kV (medium) bus | At the lowside of the GSU 34.5kV (medium) bus | 345kV bus | 34.5kV (medium) bus
17 | With generator breaker closed and zero MW output (little or no wind) what are your MVAR capability (both in consuming and in injecting MVARs into the transmission system)? | Later | Later | Later | Later | No reactor banks. So 5-10 MVAr injection |  |  | 10 MVAR reactive | 2 MVAR reactive | 20 MVAR capacitive | 40 MVAR capacitive
18 | Do you understand your responsibility in meeting .95 PF requirements? Explain your understanding of this requirement. | Our understanding is that we are required to have the capability to meet the 0.95 requirement on a total project basis for the Farm 1, 2, & 3 projects combined since we have one interconnection point and one EPS meter for the combined projects. |  |  |  | Generation resources are required to control voltages within normal operating ranges between 0.95 leading and 0.95 lagging power factor range measured at the high side of the main transformer |  |  | < 4 MW generaotrs may not be able to maintain .95 PF | <2 MW generaotrs may not be able to maintain .95 PF | <4 MW generaotrs may not be able to maintain .95 PF | <4 MW generaotrs may not be able to maintain .95 PF
19 | What MW output is required before you start meeting the .95 PF requirements? |  | 1MW | 1MW | 1MW |  | 25% of rated cap Equals 24.75 MWs | 25% of rated cap Equals 15.25 MWs | <4 MW generaotrs may not be able to maintain .95 PF | <2 MW generaotrs may not be able to maintain .95 PF | <4 MW generaotrs may not be able to maintain .95 PF | <4 MW generaotrs may not be able to maintain .95 PF
20 | Does your facility include capacitor banks and or reactors? |  | Yes | Yes | No |  | Caps | Caps | No | Yes | Yes | Yes
21 | If your facility includes capacitor banks or reactors please explain how they are controlled. Are they automatic, SCADA controlled or manual. Are they available for voltage control when there are zero MWs? List size of each capacitor bank and reactor. |  | 6 X 10.8 = 64.8 MVAr Uses PLC Logic to control caps | 2 banks 6 X 7.2 86.4 MVAr total Integrated with GE supervisory system | None |  | 2 X 9 MVArs controlled by SEL 734 meter | 4 X 4.5 MVArs controlled by SEL 451 relay that measure VAR flow and voltages | N/A | 3 - 10 MVAR capacitors (30 MVAR) Automatic and/or Manual | 1 - 8 MVAR capacitors (8 MVAR) Automatic and/or Manual | 8 - 17.5 MVAR capacitors (140 MVAR) Automatic set to maintain 34.5kv or Manual
22 | When your facility was energized, did you have an agreement with the local TSP to provide a portion of your voltage support requirements? | No |  |  |  | No | bar: WGR1 to WGR4
23 | Do your individual turbines control voltage? If so how is this control implemented (voltage control, power factor control, etc) |  | No | Yes. pf control | Yes. Voltage control |  | Yes. Internal Caps on turbines switch in and oout to control voltage | Yes. Internal Caps on turbines switch in and oout to control voltage | Yes, At the lowside of the GSU 34.5kV (medium) bus | No, Induction Generator | Yes, At the lowside of the GSU 34.5kV (medium) bus | No, Induction Generator
24 | If individual turbines control voltage, what is the control point used to govern their reactive output. (voltage on gathering network, low side of transformer interconnection point, interconnection point) |  | N/A | Low side of substation bus | Low side of substation bus |  | N/A? | N/A? | N/A | N/A | N/A | N/A
25 | Is your farm involved in a Special Protection Scheme (SPS)? Explain its operation. |  | No | No | Yes. Refer to Q25 in attachement 'Farm Responses.doc' |  | No | No | Yes, Automatic Scheme reduces generation | Yes, Automatic Scheme reduces generation | No | No
26 | Are there any temperature restrictions or operational restrictions that ERCOT might need to be aware of to better model or study operations of your facility for either Real or Reactive power production? |  | Later | 60+ C in cell (140 F) | 60+ C in cell (140 F) |  | Ambinet temp of 113 F | Ambinet temp of 113 F | N/A | >104° turbine shuts down due to high temperaure | N/A | N/A
27 | What is you ability to ramp your wind generation into the system via staggering windmills on or controlling individual ramp rates via blade pitch, braking or some other method. |  | Later | Pitch angle | Blade pitch system |  | WGR8: Staggered command on the SCADA - 5MW / Min etc; WGR9: Staggered command on the SCADA - 5MW / Min etc
28 | Discussion by the wind generator of the turbine/generator protection systems such as “high speed trip” and any other protection systems that cause a trip of the turbine so that we understood this better. At what wind speed does the turbine trip. Do all your turbines trip at the same wind speed? etc. |  | Over/Under voltage and frequency (in the GARF) | Over/Under voltage and frequency (in the GARF) | Over/Under voltage and frequency (in the GARF) |  | WGR8: Over speed tripping / rotor over speed / high shaft speed - 2095 rpm 25 m/sec for 10 mins or 30 m/sec instantaneous Over voltage trip - 120% of primary or secondary; WGR9: Over speed tripping / rotor over speed / high shaft speed - 2095 rpm 25 m/sec for 10 mins or 30 m/sec instantaneous Over voltage trip - 120% of primary or secondary
| Miscellaneous | All 3 projects have separate 34.5 kV low side busses. All voltage power factor control is based on the 34.5 kV low side voltage. In coordination with AEP and the XXX projects also connected to the XYZ 138 kV bus we operate Farm 1 & Farm 3 in power factor mode and normally operate near unity power factor. The larger Farm 2 project operates in voltage control mode to regulate the system. Having all 3 projects in voltage mode would result in one project influencing an adjacent project and irregular voltages. The existing arrangement seems to be working pretty well.