## Slide 1
Texas Regional Entity Compliance Report
October 20, 2008
COMPLIANCE REPORT OCTOBER 2008
Notes: Texas RE Board Report
<number>

## Slide 2: Texas Regional Entity
Report Details
COMPLIANCE REPORT OCTOBER 2008

## Slide 3: ERCOT’s CPS1 Monthly Performance
COMPLIANCE REPORT OCTOBER 2008
Notes: Texas RE Board Report
<number>

## Slide 4: Analysis of CPS1 Monthly Performance
Purpose: To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time.
CPS1 is one reliability measure of how well ERCOT Region managed the BPS.
The measure is based on a rolling 12 month average.
ERCOT region’s frequency performance is monitored by NERC Control Performance Standard 1 (CPS1).
COMPLIANCE REPORT OCTOBER 2008

## Slide 5: Analysis of CPS1 Monthly Performance (continued)
Seasonal fluctuation is expected.
Scores for individual months can be adversely affected by events, such as hurricanes.
A detailed formula can be found in NERC Reliability Standard BAL-001-0a.
COMPLIANCE REPORT OCTOBER 2008

## Slide 6: September 2008 – SCPS2 Scores for Non-Wind Only QSE’s
COMPLIANCE REPORT OCTOBER 2008
Notes: Texas RE Board Report
<number>

## Slide 7: September 2008 – SCPS2 Scores for Wind Only QSE’s
COMPLIANCE REPORT OCTOBER 2008

## Slide 8: Analysis of September 2008 – SCPS2 Scores
This is a schedule focused metric.
Calculations are Portfolio Based by QSE.
Because of variations in the wind, it is more difficult for wind generators to match their scheduled generation to their actual output.
A detailed formula can be found in Protocol 6.10.5.3.
COMPLIANCE REPORT OCTOBER 2008

## Slide 9: Wind Only SCPS2 Recommendations
The wide variation in SCPS2 scores for wind only QSEs should be analyzed to determine what is driving the wide variation between QSEs’ performance
The metric should be revised to make it relevant to wind generation operation and reasonable performance requirements should be set and enforced
If the metric cannot be tailored for wind generation it is recommended that it be discontinued for wind
COMPLIANCE REPORT OCTOBER 2008

## Slide 10: August 2008 Resource Plan Performance Metrics
COMPLIANCE REPORT OCTOBER 2008
Resource Plan Performance Metric | ID |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | JG | DK | BT | DE | IP | AP | AO | HA | BY | BC | JA | AY | AM | AR | BR | HJ | DF | CI | AE | AD | BJ | BH | JM | JL | JD | CF | ET | DA | GR | GS | HS | BF
Resource Status | - | 100 | - | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 99 | 99 | 100 | 99 | - | 99 | 100 | - | 100 | 100 | - | - | - | 100 | 100 | 100 | 100 | - | - | - | -
LSL as % of HSL | - | 99 | - | 94 | 97 | 100 | 98 | 98 | 99 | 100 | 94 | 100 | 94 | 95 | 95 | - | 100 | 100 | - | 100 | 98 | - | - | - | 98 | 99 | 100 | 100 | - | - | - | -
DA Zonal Schedule | 100 | 99 | 100 | 100 | 100 | 98 | 100 | 100 | 100 | 100 | 100 | 93 | 100 | 100 | 98 | 98 | 100 | 100 | - | 100 | 100 | 100 | 100 | 89 | 100 | 99 | - | 99 | 100 | 100 | 100 | 100
AP Zonal Schedule | 98 | 99 | 96 | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 99 | 99 | 100 | 98 | 100 | 100 | 99 | - | 100 | 99 | 100 | 100 | 98 | 100 | 99 | - | 99 | 100 | 100 | 100 | 100
Down Bid & Obligation | 99 | 95 | 97 | 98 | 100 | 100 | 99 | 100 | 96 | 99 | 98 | 100 | 98 | 97 | 100 | 100 | 93 | 97 | - | 100 | 97 | 97 | 100 | 100 | 100 | 99 | - | 98 | 100 | 100 | 100 | 99
Total Up AS Scheduled | - | - | - | 100 | - | 100 | 99 | 97 | 92 | 98 | 100 | 98 | 97 | 100 | 96 | - | 100 | - | 91 | - | - | - | - | - | 100 | 100 | - | 92 | - | - | - | -
Resource Plan Performance Metric | ID |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | BE | DP | EU | FX | JH | JI | JN | JJ | JC | CY | BG | CX | FK | HW | CK | IN | IZ | JK | BX | CC | JE | CD | DI | FS | AC | IE | CQ | IV | CR | IO | HM | FY
Resource Status | - | 100 | 100 | - | - | - | - | - | - | - | 99 | 99 | 99 | 100 | - | 99 | 100 | - | 99 | 100 | - | 90 | - | 100 | 99 | - | 99 | - | - | 100 | - | -
LSL as % of HSL | - | 100 | 100 | - | - | - | - | - | - | - | 98 | 99 | 99 | 100 | - | 99 | 99 | - | 98 | 98 | - | 100 | - | 100 | - | - | 97 | - | - | 100 | - | -
DA Zonal Schedule | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 68 | 100 | 99 | 100 | 100 | 98 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | - | - | 99 | 100 | 100 | 94 | 100 | -
AP Zonal Schedule | 100 | 100 | 100 | 99 | 99 | 99 | 88 | 99 | 100 | - | 99 | 97 | 99 | 98 | - | 95 | 100 | 100 | 98 | 99 | 100 | 100 | - | 100 | 100 | - | 100 | 100 | - | 46 | - | -
Down Bid & Obligation | 100 | 77 | 92 | 100 | 100 | 100 | 62 | 100 | 100 | - | 100 | 94 | 100 | 93 | - | 94 | 100 | 100 | 99 | 99 | 100 | 95 | - | - | - | - | 92 | 100 | - | 91 | - | -
Total Up AS Scheduled | - | 98 | 100 | - | - | - | - | - | - | - | 99 | 97 | 99 | 90 | - | 93 | 100 | - | 99 | 100 | - | 100 | - | - | - | - | 98 | - | - | - | - | 92
 |  |  |  |  |  | 4 Consecutive Failing Scores |  |  |  |  |  |  |  | 3 Consecutive Failing Scores |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  |  |  | 2 Consecutive Failing Scores |  |  |  |  |  |  |  | 1 Failing Score |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  | Note: This report is done with one month lag to accommodate for adjustments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 

## Slide 11: Analysis of August 2008 Resource Plan Performance Metrics
JL – Edison Mission Marketing and Trading Inc. (QSE)
  First time with a failed score in Day Ahead Zonal Schedule. August was their first month in operation (Wind Power). Edison Mission Marketing and Trading Inc was informed by email about their score and did not provide a response contesting the failed score.
DP – Fulcrum Power Service LP (QSE).
  First time with a failed score in Down Bid. Fulcrum Power Service LP was informed by email about their score and did not provide a response contesting the failed score.
JN – Invevergy McAdoo (SQ4)
  First time failing scores in Down Bid and Adjustment Period Zonal. August was their first month in operations. Invevergy McADoo (SQ4) was informed by email about their score and did not provide a response contesting the failed score.
COMPLIANCE REPORT OCTOBER 2008

## Slide 12: Analysis of August 2008 Resource Plan Performance Metrics (continued)
JC – J Aron and Company
  Second consecutive month with a failing score in Day Ahead Zonal. J Aron was informed by email and responded with a statement that they have submitted PRR 777 for this metric and for the Adjustment Period metric. PRR 777 was written so that Wind Generated Resources could be exempt from these two metrics. They are not using the ERCOT supplied wind resource plan for their submitted plan and when contacted for a response they did not disagree with the discrepancies.
IO – Westar SQ1
  First time failing score in Adjustment Period Zonal. Westar SQ1 was informed by email about their score and did not provide a response contesting the failed score.
COMPLIANCE REPORT OCTOBER 2008

## Slide 13: New Work in September 2008
COMPLIANCE REPORT OCTOBER 2008
7 New Protocol and Operating Guides Violation Investigations.
3 New Preliminary NERC Standards Violation Investigations.
2 New Event Investigations.
Notes: Texas RE Board Report
<number>

## Slide 14: Update on Key Issues
Four (4) entities are in settlement discussions representing 15 violations.
Entity “D” has re-entered settlement and has submitted a mitigation plan.
Entity “A”’ mitigation plan has been approved by NERC.
COMPLIANCE REPORT OCTOBER 2008

## Slide 15: Major Compliance Accomplishments in September 2008
11/29/07 EECP 1 Event Analysis Completed
  Protocol Violations Issued
Critical Infrastructure Protection Workshop
  Held October 1, 2008
  Over 120 Market Participants Attended
All 2007 Event Analyses have been completed
2008 Self-Certifications were issued by Texas RE and most responses have been received
Larry and Victor represented Texas RE at the Gulf Coast Power Association Conference
COMPLIANCE REPORT OCTOBER 2008

## Slide 16: Major Compliance Initiatives for October 2008
Next Texas Regional Entity Standards and Compliance Workshop
  November 5, 2008
  Workshop reservations currently at 80%
Determine dates and select a venue for the 2009 Operations Training Seminar
  Looking into alternative locations to the Met Center
Represent Texas RE at the NRECA Conference in San Antonio
COMPLIANCE REPORT OCTOBER 2008

## Slide 17: Special Project Report- Protocol/Nodal Update
Texas RE and PUC are working together to identify areas that will require metrics for the Nodal Market
  Half day work sessions are planned
Jointly providing coverage of the key committees and working groups to track progress
Plan to work with Market Participants to introduce desired metrics in committee
COMPLIANCE REPORT OCTOBER 2008

## Slide 18: Special Project Report- OGRR208 Briefing
Immediate need for an ERCOT Protocol to ensure that better technology is installed in the ERCOT region.
Approval is recommended. Market participants can continue to refine the grandfathering issue due to long implementation period.
7 year implementation period may be too long, however, it can be adjusted once studies are complete.
COMPLIANCE REPORT OCTOBER 2008

## Slide 19: Key Organizational Challenges Moving Forward
Staffing continues to be problematic
  Qualified staff not readily available in the job market
  Retention continues to be a challenge
    Wage and benefit pressure persists
Potential for significant work load increases due to unknowns such as investigations, appeals, registrations, etc.
Increased level of participation in ERCOT committees/working groups, and in performance metrics identification
COMPLIANCE REPORT OCTOBER 2008

## Slide 20: Key Organizational Challenges Moving Forward
LSE Registration
  The LSE definition does not work well with ERCOT’s unbundled market design
  May double the number of registered entities in ERCOT with an associated work load increase for registration/JRO and audits
  Large number of appeals predicted
  Texas RE has issued comments to FERC
  Texas RE has not registered any LSEs in ERCOT Region and is awaiting decision by FERC
COMPLIANCE REPORT OCTOBER 2008