## CRE recommendations
Attachment C: 2009 CREs Considered by WMS & TAC
ERCOT Recommendation
To Bus | To Bus Name | From Bus | From Bus Name | 2008 Existing? | 2009 CRE Selection Reason | 3b | 3i | 3h | 3b PTDF | 3i PTDF | 3h PTDF
CSC_4 - North to Houston: Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit
3391 | JEWETT_N5 | 46500 | TOMBAL__345B | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | 17.2 | 17.07 | 17.08
40600 | ROANS___345C | 45972 | KUYDAL755010 | Existing | Improved Operational control. | X | X | X | 14.5 | 14.25 | 14.26
40900 | KING____345A | 45971 | KUYDAL745005 | Existing | Improved Operational control. | X | X | X | -10.8 | -10.8 | -10.8
40900 | KING____345A | 45972 | KUYDAL755010 | Existing | Improved Operational control. | X | X | X | -14.5 | -14.25 | -14.26
45971 | KUYDAL745005 | 46500 | TOMBAL__345B | Existing | Improved Operational control. | X | X | X | -10.8 | -10.8 | -10.8
967 | GIBN_CREK_5 | 44500 | OBRIEN__345A | 2008 CSC | Passed Protocols Section 7.2.3 criteria. | X | X | X | 15.5 | 15.23 | 15.24
3390 | JEWETT_S5 | 45500 | T_H_W___345B | 2008 CSC | Passed Protocols Section 7.2.3 criteria. | X | X | X | 16.8 | 16.67 | 16.71
CSC_2 - South to North & North to South: Lake Creek-Temple/ Tradinghouse-Temple Pecan Creek 345-kV double circuit
3405 | THOUSE__5 | 3409 | LAKE_CRK1_5 | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | -7.5 | -8.1 | -8.11
3410 | LAKE_CRK1_8 | 3420 | TEMP_PEC__8 | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | -2.9 | -2.64 | -2.64
3412 | TEMP_PEC__5 | 3414 | TEMP_SS__5 | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | -17.3 | -16.91 | -16.92
3415 | TEMP_SS__8 | 3675 | ROGERS1A_8 | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | -2.4 | -2.33 | -2.33
3420 | TEMP_PEC__8 | 3415 | TEMP_SS__8 | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | 2.8 | 2.58 | 2.58
7040 | L_AUSTRO5_1Y | 3429 | SANDOW__5 | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | -17.9 | -17.45 | -17.47
7040 | L_AUSTRO5_1Y | 13429 | SAND_TXU_5 | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | 17.8 | 17.35 | 17.36
1655 | BRNWDSW_8 | 7070 | L_GOLDTH8_1Y | New for this CSC. | Passed Protocols Section 7.2.3 criteria. | X | X | X | -3.3 | -3.81 | -3.79
7068 | L_EVANT_8_1Y | 7066 | L_ADAMSV8_1Y | New for this CSC. | Passed Protocols Section 7.2.3 criteria. | X | X | X | 2.9 | 3.3 | 3.29
7070 | L_GOLDTH8_1Y | 7068 | L_EVANT_8_1Y | New for this CSC. | Passed Protocols Section 7.2.3 criteria. | X | X | X | 2.9 | 3.3 | 3.29
3402 | LAKE_CRK2_5 | 3405 | THOUSE__5 | No | Passed Protocols Section 7.2.3 criteria. | X | X | X | 8.7 | 9.52 | 9.52
3413 | TEMPSSLT__5 | 3429 | SANDOW__5 | No | Passed Protocols Section 7.2.3 criteria. | X | X | X | -18 | -17.56 | -17.57
3414 | TEMP_SS__5 | 3429 | SANDOW__5 | No | Passed Protocols Section 7.2.3 criteria. | X | X | X | -18.1 | -17.66 | -17.67
3591 | WACOWOOD1_8 | 13591 | COTTONB_T_8 | No | Passed Protocols Section 7.2.3 criteria. | X | X | X | -2.1 | -1.9 | -1.9
CSC_1 - West to North & North to West
| Stability Limit |  |  | Existing | Passed Protocols Section 7.2.3 criteria. (3b & 3i) | X | X | X | -- | -- | --
1422 | BOWMAN_5 | 1425 | FISHRDSS1_5 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X | X | X | -7.6 | -- | -5.89
1425 | FISHRDSS1_5 | 6100 | OKLA7A | Existing | Passed Protocols Section 7.2.3 criteria. (3h & 3b) | X | X | X | 9.5 | -- | -7.35
1435 | LONGCREK_5 | 1430 | GRAHAMSES1_5 | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | 18.9 | -9.61 | -7.46
1440 | COMCHESS1_5 | 6444 | SARC7A | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | -16.6 | -13.32 | -12.51
1442 | Cook Field | 1430 | Graham | Existing | Passed Protocols Section 7.2.3 criteria. | X | X | X | -19.5 | -7.77 | -5.62
1440 | COMCHESS1_5 | 1900 | COMCHPKW_5 | Existing | Passed Protocols Section 7.2.3 criteria. (3b & 3i) | X | X | X | 14.4 | 12.14 | 11.33
1439 | LONGCREK_5 | 1442 | Cook Field | Existing | Passed Protocols Section 7.2.3 criteria. (3h & 3i) | X | X | X | 17.3 | 15.2 | 13.37
6340 | Ballinger | 6360 | Coleman Ivey | No | Passed Protocols Section 7.2.3 criteria. | X | X | X
1048 | TONKAWAWI_5 | 1430 | GRAHAMSES1_5 | Existing | Passed Protocols Section 7.2.3 criteria. (3h & 3i) |  | X | X | 14.9 | 15.64 | 14.71
1371 | MURRY_P8 | 1431 | GRAHAMSES1_8 | Existing | Passed Protocols Section 7.2.3 criteria. (3i) |  | X | X | 3.3 | 3.87 | 3.38
6235 | ABMULCW7 | 6100 | OKLA7A | No | Passed Protocols Section 7.2.3 criteria. (3h) |  | X | X | -8 | 0.54 | -5.72
6169 | PAIP4B | 1371 | MURRY_P8 | New | Passed Protocols Section 7.2.3 criteria. (3i) |  | X |  | -3.3 | -3.87 | -3.38
1429 | JACKSBRO_5 | 988 | W_DENT_5 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | -11.6 | -5.25 | -5.63
1430 | GRAHAMSES1_5 | 1429 | JACKSBRO_5 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | -16.6 | -8.67 | -7.3
1468 | LKAROWHD_8 | 1470 | NEWPRT_P8 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | 3.8 | 1.57 | 1.83
1596 | GRAHAMSW_8 | 1599 | BARTON_8 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | 3.1 | 5.11 | 5.12
1599 | BARTON_8 | 1571 | ORAN1_8 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | -4.6 | 0.52 | 0.51
1624 | LEONSW_8 | 1642 | FLATCRK_T8 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | 5.5 | 3.14 | 3.07
1640 | LINGLVLL_P8 | 1641 | STPHNVIL_8 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | 0.1 | 0.33 | 0.26
1642 | FLATCRK_T8 | 1640 | LINGLVLL_P8 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | -0.1 | -0.33 | -0.26
1421 | WILLOWCK_5 | 1429 | JACKSBRO_5 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | -13 | -5.33 | -6.03
1421 | WILLOWCK_5 | 1436 | PARKER_5 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | 13 | 5.33 | 6.03
1422 | BOWMAN_5 | 1429 | JACKSBRO_5 | Existing | Passed Protocols Section 7.2.3 criteria. (3b) | X |  |  | 8 | 1.91 | 4.36
|  | CSC | Scenario 3b | Scenario 3h | Scenario 3i (2)
|  | N_H (1) | Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit | Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit | Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit
|  | N_S & S_N | Lake Creek-Temple/ Tradinghouse-Temple Pecan Creek 345-kV double circuit | Lake Creek-Temple/ Tradinghouse-Temple Pecan Creek 345-kV double circuit | Lake Creek-Temple/ Tradinghouse-Temple Pecan Creek 345-kV double circuit
|  | W_N & N_W | Graham-Benbrook/ Graham-Parker 345-kV double circuit | Sweetwater-Long Creek/ Abilene Mulberry Creek-Long Creek 345-kV double circuit | Sweetwater-Long Creek/ Abilene Mulberry Creek-Long Creek 345-kV double circuit
Notes:
(1) For N_H, Singleton is not scheduled to be in-service until May 2009.
(2) Post-contingency (Oklaunion-Fisher Road/Fisher Road-Bowman 345-kV) shift factors were used for the clustering analysis.

## all data
2008 vs. 2009 Closely Related Elements
[7 empty] | Oklaunion-Bowman Closed (3h) |  |  |  | Oklaunion-Bowman Open (3i) |  |  |  | No change to W-N & N-W CSC
To Bus | To Bus Name | From Bus | From Bus Namd | CRE Id | 2008 Existing / New CRE? | 2008 CRE Selection Reason | 3h Generation Moving Zones | 3h Pass? T or F | PTDF | Rec? | 3i Generation Moving Zones | 3i Pass? T or F | PTDF | Rec? | 3b Generation Moving Zones | 3b Pass? T or F | PTDF | Rec? | Pass all?
CSC_1: West to North & North to West
| Stability Limit | [5 empty] | 1527.67 | 0 | -- |  | 878 | 1 | -- |  | 752 | 1 | --
1048 | TONKAWAWI_5 | 1430 | GRAHAMSES1_5 | CSC_1 | New | Improved Operational control. | 165.5 | 1 | 14.71 |  | 0 | 1 | 15.64 |  | 2445.17 | 0 | 14.9
1371 | MURRY_P8 | 1431 | GRAHAMSES1_8 | CSC_1 | New | Passed Protocols Section 7.2.3 criteria. | 23588.97 | 0 | 3.38 |  | 636 | 1 | 3.87 |  | 24455.3 | 0 | 3.3
1420 | SWEETWTR_5 | 1430 | GRAHAMSES1_5 | CSC_1 | Existing | Improved Operational control. |  | n/a | -- |  |  | n/a | -- |  |  | n/a | --
1420 | SWEETWTR_5 | 1439 | LONGCREK_5 | CSC_1 | New, added 8/29/2008 | Long Creek cut-in between existing CRE. |  | n/a | -- |  |  | n/a | -- |  | 4056.87 | 0 | 11.5
1439 | LONGCREK_5 | 1430 | Graham | CSC_1 | New, added 8/29/2009 | Long Creek cut-in between existing CRE. |  | n/a | -- |  |  | n/a | -- |  |  | n/a | --
1421 | WILLOWCK_5 | 1429 | JACKSBRO_5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2279.67 | 0 | -6.03 |  | 1630 | 0 | -5.33 |  | 0 | 1 | -13
1421 | WILLOWCK_5 | 1436 | PARKER_5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2929.67 | 0 | 6.03 |  | 2280 | 0 | 5.33 |  | 650 | 1 | 13
1422 | BOWMAN_5 | 1425 | FISHRDSS1_5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 1551.67 | 0 | -5.89 |  |  | n/a | -- |  | 728 | 1 | -7.6
1422 | BOWMAN_5 | 1429 | JACKSBRO_5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 3034.17 | 0 | 4.36 |  | 2458.5 | 0 | 1.91 |  | 754.5 | 1 | 8
1425 | FISHRDSS1_5 | 6100 | OKLA7A | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 1450.67 | 1 | -7.35 |  |  | n/a | -- |  | 829 | 1 | 9.5
1429 | JACKSBRO_5 | 988 | W_DENT_5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2989.67 | 0 | -5.63 |  | 2340 | 0 | -5.25 |  | 710 | 1 | -11.6
1430 | GRAHAMSES1_5 | 1429 | JACKSBRO_5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2178.67 | 0 | -7.3 |  | 1529 | 0 | -8.67 |  | 101 | 1 | -16.6
1431 | GRAHAMSES1_8 | 1601 | GRAHAME_8 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 26638.47 | 0 | 4.82 |  | 25385.8001 | 0 | 4.87 |  | 23899.8001 | 0 | 3
1435 | LONGCREK_5 | 1430 | GRAHAMSES1_5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 1450.67 | 1 | -7.46 |  | 801 | 1 | -9.61 |  | 1478.67 | 1 | 18.9 |  | TRUE
1439 | LONGCREK_5 | 1442 | Cook Field | CSC_1 | New, added 8/29/2008 | Cook Field cut-in between existing CRE. | 636 | 1 | 13.37 |  | 636 | 1 | 15.2 |  | 1643.67 | 0 | 17.3
1442 | Cook Field | 1430 | Graham | CSC_1 | New, added 8/29/2009 | Cook Field cut-in between existing CRE. | 801 | 1 | -5.62 |  | 801 | 1 | -7.77 |  | 1478.67 | 1 | -19.5 |  | TRUE
1435 | LONGCREK_5 | 6230 | ABMULCE7 | CSC_1 | New | Passed Protocols Section 7.2.3 criteria. |  | n/a | -- |  |  | n/a | -- |  | 1861 | 0 | -16.3
1436 | PARKER_5 | 1869 | BENBRK_A_T5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 3825.17 | 0 | 3.66 |  | 3175.5 | 0 | 3.36 |  | 2135.5 | 0 | 8.2
1440 | COMCHESS1_5 | 1900 | COMCHPKW_5 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 1510.67 | 0 | 11.33 |  | 861 | 1 | 12.14 |  | 889 | 1 | 14.4
1440 | COMCHESS1_5 | 6444 | SARC7A | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 1450.67 | 1 | -12.51 |  | 801 | 1 | -13.32 |  | 829 | 1 | -16.6 |  | TRUE
1468 | LKAROWHD_8 | 1470 | NEWPRT_P8 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2785.67 | 0 | 1.83 |  | 2196 | 0 | 1.57 |  | 794 | 1 | 3.8
1596 | GRAHAMSW_8 | 1599 | BARTON_8 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2195.67 | 0 | 5.12 |  | 2196 | 0 | 5.11 |  | 204 | 1 | 3.1
1596 | GRAHAMSW_8 | 1601 | GRAHAME_8 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 26035.47 | 0 | -4.82 |  | 1486 | 1 | -4.84 |  | 23899.8001 | 0 | -3
1599 | BARTON_8 | 1571 | ORAN1_8 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2315.67 | 0 | 0.51 |  | 2316 | 0 | 0.52 |  | 84 | 1 | -4.6
1624 | LEONSW_8 | 1642 | FLATCRK_T8 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2339.67 | 0 | 3.07 |  | 1690 | 0 | 3.14 |  | 60 | 1 | 5.5
1640 | LINGLVLL_P8 | 1641 | STPHNVIL_8 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2339.67 | 0 | 0.26 |  | 1690 | 0 | 0.33 |  | 60 | 1 | 0.1
1642 | FLATCRK_T8 | 1640 | LINGLVLL_P8 | CSC_1 | Existing | Passed Protocols Section 7.2.3 criteria. | 2339.67 | 0 | -0.26 |  | 1690 | 0 | -0.33 |  | 60 | 1 | -0.1
6169 | PAIP4B | 1371 | MURRY_P8 | CSC_1 | New | Passed Protocols Section 7.2.3 criteria. | 24110.97 | 0 | -3.38 |  | 636 | 1 | -3.87 |  | 24017.3 | 0 | -3.3
6230 | ABMULCE7 | 60040 | BLF_CRK7A | CSC_1 | New | Improved Operational control. | 9271.85 | 0 | -16.16 |  | 33700.3501 | 0 | -15.26 |  | 11387.52 | 0 | -9.4
1430 | GRHAMSES1_5 | 1873 | BENBRK_5 | CSC_1 | 2008 CSC |  | 2929.67 | 0 | 7.22 |  | 2280 | 0 | 7.24 |  |  | n/a | --
1430 | GRHAMSES1_5 | 1436 | PARKER_5 | CSC_1 | 2008 CSC |  | 2279.67 | 0 | 8.19 |  | 1630 | 0 | 8.32 |  |  | n/a | --
6235 | ABMULCW7 | 71050 | L_BITTCR5_1N | CSC_1 | No |  | 2028.2 | 0 | -18.84 |  | 2827.87 | 0 | -17.78 |  | 4307.87 | 0 | -14.2
6235 | ABMULCW7 | 6100 | OKLA7A | CSC_1 | No |  | 1176.5 | 1 | -5.72 |  | 10864.55 | 0 | 0.54 |  | 1854.17 | 0 | -8
1030 | MRGNCRK_5 | 1420 | SWEETWTR_5 | CSC_1 | No |  | 2008.2 | 0 | -18.2 |  | 2657.87 | 0 | 18.44 |  | 4287.87 | 0 | 11.5
1030 | MRGNCRK_5 | 71050 | L_BITTCR5_1N | CSC_1 | No |  | 2532.2 | 0 | 11.99 |  | 3331.87 | 0 | 10.93 |  | 4961.87 | 0 | 8.3
1422 | BOWMAN_5 | 1430 | GRHAMSES1_5 | CSC_1 | No |  | 11966.72 | 0 | -0.02 |  | 23935.8 | 0 | -3.54 |  | 12793.0501 | 0 | -2
1318 | CHINAGRV_8 | 1398 | RADIUMMT_8 | CSC_1 | No |  | 24628 | 0 | 1.99 |  | 25781.67 | 0 | 1.91 |  | 27411.67 | 0 | 1.9
CSC_2: South to North & North to South
1655 | BRNWDSW_8 | 7070 | L_GOLDTH8_1Y | CSC_2 | New for this CSC. | Passed Protocols Section 7.2.3 criteria. | 0 | 1 | -3.79 |  | 0 | 1 | -3.81 |  | 0 | 1 | -3.3 |  | TRUE
3405 | THOUSE__5 | 3409 | LAKE_CRK1_5 | CSC_2 | Existing | Passed Protocols Section 7.2.3 criteria. | 946.67 | 1 | -8.11 |  | 297 | 1 | -8.1 |  | 297 | 1 | -7.5 |  | TRUE
3409 | LAKE_CRK1_5 | 3414 | TEMP_SS__5 | CSC_2 | Existing | Passed Protocols Section 7.2.3 criteria. |  | n/a | -- |  |  | n/a | -- |  |  | n/a | --
3410 | LAKE_CRK1_8 | 3420 | TEMP_PEC__8 | CSC_2 | Existing | Passed Protocols Section 7.2.3 criteria. | 649.67 | 1 | -2.64 |  | 0 | 1 | -2.64 |  | 0 | 1 | -2.9 |  | TRUE
3412 | TEMP_PEC__5 | 3405 | THOUSE__5 | CSC_2 | Existing | Passed Protocols Section 7.2.3 criteria. |  | n/a | -- |  |  | n/a | -- |  |  | n/a | --
3412 | TEMP_PEC__5 | 3414 | TEMP_SS__5 | CSC_2 | Existing | Passed Protocols Section 7.2.3 criteria. | 649.67 | 1 | -16.92 |  | 0 | 1 | -16.91 |  | 0 | 1 | -17.3 |  | TRUE
3415 | TEMP_SS__8 | 3675 | ROGERS1A_8 | CSC_2 | Existing | Passed Protocols Section 7.2.3 criteria. | 0 | 1 | -2.33 |  | 0 | 1 | -2.33 |  | 0 | 1 | -2.4 |  | TRUE
3420 | TEMP_PEC__8 | 3415 | TEMP_SS__8 | CSC_2 | Existing | Passed Protocols Section 7.2.3 criteria. | 0 | 1 | 2.58 |  | 0 | 1 | 2.58 |  | 0 | 1 | 2.8 |  | TRUE
7040 | L_AUSTRO5_1Y | 3429 | SANDOW__5 | CSC_2 | Existing | Passed Protocols Section 7.2.3 criteria. | 1161 | 1 | -17.47 |  | 1161 | 1 | -17.45 |  | 1161 | 1 | -17.9 |  | TRUE
7040 | L_AUSTRO5_1Y | 7045 | L_ZORN__5_2Y | CSC_2 | New | Improved Operational control. | 7413.15 | 0 | -12.51 |  | 6763.48 | 0 | -12.51 |  | 6763.48 | 0 | -12.8
7040 | L_AUSTRO5_1Y | 7048 | L_GARFIE5_1Y | CSC_2 | New | Improved Operational control. | 4108 | 0 | -12.67 |  | 4108 | 0 | -12.66 |  | 4108 | 0 | -13
7040 | L_AUSTRO5_1Y | 13429 | SAND_TXU_5 | CSC_2 | New | Passed Protocols Section 7.2.3 criteria. | 1161 | 1 | 17.36 |  | 1161 | 1 | 17.35 |  | 1161 | 1 | 17.8 |  | TRUE
7068 | L_EVANT_8_1Y | 7066 | L_ADAMSV8_1Y | CSC_2 | New for this CSC. | Passed Protocols Section 7.2.3 criteria. | 649.67 | 1 | 3.29 |  | 0 | 1 | 3.3 |  | 0 | 1 | 2.9 |  | TRUE
7070 | L_GOLDTH8_1Y | 7068 | L_EVANT_8_1Y | CSC_2 | New for this CSC. | Passed Protocols Section 7.2.3 criteria. | 0 | 1 | 3.29 |  | 0 | 1 | 3.3 |  | 0 | 1 | 2.9 |  | TRUE
3591 | WACOWOOD1_8 | 13591 | COTTONB_T_8 | CSC_2 | No |  | 0 | 1 | -1.9 |  | 0 | 1 | -1.9 |  | 0 | 1 | -2.1 |  | TRUE
1906 | VENUS_S5 | 3405 | THOUSE__5 | CSC_2 | No |  | 3136.67 | 0 | -13.85 |  | 2487 | 0 | -13.83 |  | 2487 | 0 | -12.4
1907 | VENUS_N5 | 3405 | THOUSE__5 | CSC_2 | No |  | 3136.67 | 0 | -14.96 |  | 2487 | 0 | -14.94 |  | 2487 | 0 | -13.1
3402 | LAKE_CRK2_5 | 3405 | THOUSE__5 | CSC_2 | No |  | 946.67 | 1 | 9.52 |  | 297 | 1 | 9.52 |  | 297 | 1 | 8.7 |  | TRUE
3413 | TEMPSSLT__5 | 3429 | SANDOW__5 | CSC_2 | No |  | 0 | 1 | -17.57 |  | 0 | 1 | -17.56 |  | 0 | 1 | -18 |  | TRUE
3414 | TEMP_SS__5 | 3429 | SANDOW__5 | CSC_2 | No |  | 0 | 1 | -17.67 |  | 0 | 1 | -17.66 |  | 0 | 1 | -18.1 |  | TRUE
CSC_4: North to Houston
3391 | JEWETT_N5 | 46500 | TOMBAL__345B | CSC_4 | Existing | Passed Protocols Section 7.2.3 criteria. | 851.2 | 1 | 17.08 |  | 851.2 | 1 | 17.07 |  | 851.2 | 1 | 17.2 |  | TRUE
40600 | ROANS___345C | 45972 | KUYDAL755010 | CSC_4 | Existing | Improved Operational control. | 2665 | 0 | 14.26 |  | 3178.9999 | 0 | 14.25 |  | 3248.1999 | 0 | 14.5
40900 | KING____345A | 45971 | KUYDAL745005 | CSC_4 | Existing | Improved Operational control. | 4920.3999 | 0 | -10.8 |  | 4920.3999 | 0 | -10.8 |  | 4920.3999 | 0 | -10.8
40900 | KING____345A | 45972 | KUYDAL755010 | CSC_4 | Existing | Improved Operational control. | 3248.1999 | 0 | -14.26 |  | 3178.9999 | 0 | -14.25 |  | 3248.1999 | 0 | -14.5
45971 | KUYDAL745005 | 46500 | TOMBAL__345B | CSC_4 | Existing | Improved Operational control. | 4721.3999 | 0 | -10.8 |  | 4721.3999 | 0 | -10.8 |  | 4920.3999 | 0 | -10.8
967 | GIBN_CREK_5 | 44500 | OBRIEN__345A | CSC_4 | 2008 CSC |  | 649.67 | 1 | 15.24 |  | 0 | 1 | 15.23 |  | 0 | 1 | 15.5 |  | TRUE
3390 | JEWETT_S5 | 45500 | T_H_W___345B | CSC_4 | 2008 CSC |  | 851.2 | 1 | 16.71 |  | 851.2 | 1 | 16.67 |  | 851.2 | 1 | 16.8 |  | TRUE
the sum of flows for these four lines
Jewett to TH Wharton
Jewett to Tomball
Gibbons Creek to O’Brien
Roans Prairie to Kuykendahl