## TPITFutureNoCost08012008
AUGUST BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) FUTURE PROJECTS As Of 08/01/2008
Projects (New/Old) | Service Date Changes | ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) | Associated Projects (project number) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (TSP Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Transformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | Location County (Start If Line) | End Location If Line County | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers ( CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Requested Additional Information | Other
Old Project | No Change | 08TPIT0123 | Long Creek Switching Station circuit breakers | Install 345 kV circuit breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R620B-WAC | 2008-08-01 |  | 345 | 0 | 0 | 0 | 0 | SHACKELFORD |  |  |  |  | 6230, 1435, 1437, 1430 | Y
Old Project | Change in Service Date. Change from 5/1/2008 8/1/2008 | 08TPIT0177 | Keller Wall Price 138 kV Capacitors | Install 138 kV capacitors | Construction delays |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5126-WA | 2008-08-01 |  | 138 | 0 | 0 | 0 | 110.4 | TARRANT | [5 empty] | Y
Old Project | Change in Service Date. Change from 5/1/2008 8/2/2008 | 08TPIT0089 | Mill Creek - Gay Hill | Increase the line-to-ground clearance on the Mill Creek (7565) - Gay Hill (7572) 138 kV transmission line as necessary to increase the capacity of this circuit to its full conductor rating of 128 MVA. |  |  | BBEC | Eric Kocian (979) 542-4150 eric.kocian@bluebonnetelectric.coop |  | 2008-08-02 |  | 138 | 0 | 9.1 | 0 | 0 | WASHINGTON |  |  |  |  | SEE PROJECT DESCRIPTION | Y | SEE PROJECT DESCRIPTION
Old Project | No Change | 08TPIT0207 | TXDOT Hwy 511 | Relocate 138kV line from Central Ave to East Rio Hondo Substation |  | 08TPIT0208 | MVEC | Loretta C. Gallaga (956) 514-1289 lgallaga@stec.org | 975628 | 2008-08-08 |  | 138 | 0.75 | 0.19 | 0 | 0 | Cameron | Cameron | [6 empty] | TXDOT Project to relocate line due to road widening
Old Project | Change in Service Date. Change from 5/1/2008 8/8/2008 | 07TPIT0090 | Greenville: Construct new Shelby sub with 138-69 auto and re-route Royse line into new sub | Construct a new substation with a 138-69 kV autotransformer and route Royse line into sub | Construction Delays |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05012 | 2008-08-08 |  | 138 | 4 | 0 | 150 | 0 | HUNT | HUNT |  |  |  | 960, 961 | Y
Old Project | Change in Service Date. Change from 5/1/2008 8/15/2008 | 06TPIT0018 | Maypearl 69 kV capacitor | Install 69 kV capacitors | Construction delays |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R423-WA | 2008-08-15 |  | 69 | 0 | 0 | 0 | 27.6 | ELLIS |  |  |  |  | 3536 | Y
Old Project | No Change | 08TPIT0168 | Crane, Add 2nd 138 kV 57.6 Mvar Shunt Capacitor | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto, and add Transfer Trip to Barrilla to Ft. Stockton |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2273 | 2008-08-31 |  | 138 | 0 | 0 | 0 | 57.6 | PRESIDIO
Old Project | Change in Service Date. Change from 5/1/2008 9/1/2008 | 08TPIT0147 | Ajo to IPP, build 345 kV line | Build 345 kV switching station in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's | Schedule Update | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2223 | 2008-09-01 |  | 345 | 21.6 | 0 | 0 | 0 | KENEDY | KENEDY
Old Project | No Change | 09TPIT0036 | Castroville - New 138kV Substation | Loop new 138kV substation into the existing 138kV TX Research to Lytle line | Design/Build contract has been awarded | T-0072 | CPS | PM: Ulrich Skerhut | S-0185 | 2008-09-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5083 | Y |  | There are no transformers associated with this project
Old Project | No Change | 08TPIT0163 | West Denton - Denton Steam: 138 KV Line Upgrade | Rebuild and upgrade capacity of West Denton to Denton Steam 138 kV Line | Delayed due to original requirements have changed per Chuck Sears - Denton |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T08001 | 2008-09-01 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  |  | 986, 982
Old Project | Change in Service Date. Change from 5/8/2008 9/1/2008 | 08TPIT0209 | Victoria: Upgrade Sub, Relay, SCADA, Metering | Interconnect new generation at the Victoria substation, install a phase shifting transformer at Thomaston substation, and rebuild Magruder to North Victoria 69 kV Line | Schedule Update | AEP GROUP 402 | AEP/TCC | Dave Goetz 918-599-2653 | 3111 | 2008-09-01 |  | 138 | 0 | 0 | 0 | 0 | VICTORIA
Old Project | Change in Service Date. Change from 5/8/2008 9/1/2008 | 08TPIT0137 | North Padre: Add 1-14.4 MVAR Cap Bank | North Padre: Add 1-14.4 MVAR 69KV Cap Bank and Termination Upgrades | Schedule Update | AEP GROUP 029 | AEP/TCC | Michael Glueck 918-599-2653 | 205 | 2008-09-01 |  | 69 | 0 | 0 | 0 | 14.4 | ARANSAS
Old Project | No Change | 08TPIT0204 | White Baker Substation - Sherbino | Build new 138kV station at White Baker. The station will have 138kV ringbus section to serve Orion (BP) Sherbino Mesa Project and 69kV section to serve Northern Natural to White Baker. |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com | NTE 07207 | 2008-09-08 |  | 138 | 0 | 0 | 70 | 0 | PECOS | PECOS |  |  |  | 38430, 38420 | Y
Old Project | No Change | 08TPIT0203 | Uprate White Baker to Rio Pecos | Rebuild existing 69kV line from White Baker to Rio Pecos to accommodate 300MW generation for 138kV interconnection at White Baker substation. Work will include changing out poles for clearance, and reconductoring from White Baker to Rio Pecos with 795 ACSS conductor. Building a new entrance to AEP Rio Pecos Plant to the 138kV bay. |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com | NTE 07207 | 2008-09-08 |  | 69 | 0 | 14 | 0 | 0 | PECOS | CROCKETT |  |  |  | 38430, 6601 | Y
Old Project | No Change | 08TPIT0134 | Ajo, Build 345 KV SS | Build 345 kV switching station with shunt reactors in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's |  | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2052 | 2008-09-30 |  | 345 | 0 | 0 | 0 | -200 | KENEDY
Old Project | No Change | 08TPIT0200 | Interconnection between TNMP and BP Alternative Energy North America Inc | BP's one 244 MW steam turbine generating unit will be interconnected with TNMP's 138kV system at Greenbelt Switching Station in Texas City, TX |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2008-09-30 |  | 138 | 0 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | N
Old Project | No Change | 08TPIT0167 | Friend Ranch, Add 2nd 138 kV 28.8 Mvar Shunt Capacitor | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2264 | 2008-09-30 |  | 138 | 0 | 0 | 0 | 28.8 | CROCKETT
Old Project | Change in Service Date. Change from 5/15/2008 9/30/2008 | 08TPIT0083 | Clyde to Putnam, Rebuild 69 kV line | Rebuild the Clyde to Putnam 69 kV line | Schedule & Cost Update | AEP GROUP 354 | AEP/TNC | John Pulay 918-599-2653 | 2143 | 2008-09-30 |  | 69 | 0 | 19.08 | 0 | 0 | CALLAHAN | CALLAHAN
Old Project | No Change | 08TPIT0149 | Willow Valley 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R813-WAC | 2008-10-01 |  | 138 | 0 | 0.23 | 0 | 0 | SCURRY |  |  |  |  | 1048 | Y
Old Project | No Change | 08TPIT0184 | Lamesa Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R691-WA - R694-WA, R696-WA & R697-WA | 2008-10-01 |  | 138 | 0 | 0 | 0 | 0 | DAWSON | [5 empty] | Y
Old Project | No Change | 07TPIT0261 | County Rd 101 | Build 1.23 miles of 138 kV for retail service | Customer will be ready to take power on Oct-08 |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com |  | 2008-10-01 |  | 138 | 1.23 | 0 | 0 | 0 | REEVES | REEVES |  |  |  | 6657, 38375 | Y
Old Project | Change in Service Date. Change from 5/31/2008 10/1/2008 | 08TPIT0062 | Bell County to Schwertner Rebuild | Rebuild Bell County to Schwertner 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-10-01 |  | 69 | 0 | 13.7 | 0 | 0 | BELL | BELL |  |  |  | 133114122 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | Change in Service Date. Change from 5/31/2008 10/2/2008 | 06TPIT0081 | Airline to Laguna, rebuild 69 kV line | Rebuild Airline to Laguna 69 kV transmission line from 477 ACSR to 795 ACSR |  | AEP GROUP 029 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 4, LCRA#1003908 | 2008-10-02 |  | 69 | 0 | 6.4 | 0 | 0 | NUECES | NUECES
Old Project | No Change | 08TPIT0099 | Sandow Switch circuit breaker installation | Install 138 kV circuit breakers and terminate existing 138 kV lines |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R701-WA | 2008-10-15 |  | 138 | 0 | 0 | 0 | 0 | MILAM |  |  |  |  | 13431, 13432, 13430, 13429 | Y |  | Remaining work has been rescheduled to after summer.
Old Project | No Change | 07TPIT0130 | Buda-Centex-Lehigh-Kyle-Canyon | Upgrade the 3.5-mile Lehigh-Buda(7498) 4/0-ACSR 69-kV transmission line to a 69/138 kV double circuit transmission line. One circuit will be 795 ACSR 69 KV and the other circuit will be bundled 795 ACSR 138 kV. The 69 kV circuit will terminate at Buda(7 |  | 06TPIT0224 | PEC | Darrel Mitchell (830) 868-7155 Darrel.Mitchell@PECI.com |  | 2008-10-29 |  | 138 | 3.5 | 12.2 | 0 | 0 | HAYS |  |  |  |  | SEE PROJECT DESCRIPTION | Y | The name of Kohler's Crossing Substaion has been changed to Lehigh Substation
Old Project | Change in Service Date. Change from 5/31/2008 10/31/2008 | 08TPIT0154 | Cook Field Road 345 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R817-WAC | 2008-10-31 |  | 345 | 0 | 0 | 0 | 0 | SHACKELFORD | [5 empty] | Y
Old Project | Change in Service Date. Change from 6/1/2008 10/31/2008 | 08TPIT0142 | Elm Grove 138 kV new substation and load serving, and its 138 kV connections to Olinger and to Ben Davis | Elm Grove 138 kV new substation and load serving | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2008-10-31 |  | 138 | 0 | 20.1 | 0 | 0 | DALLAS |  |  |  |  | 818, 2705, 968 | Y |  | This project adds a new 138kV Elm Grove substation, its new load serving, and its 2 rebuilt lines to Olinger and to Ben Davis
Old Project | Change in Service Date. Change from 6/1/2008 10/31/2008 | 06TPIT0098 | Newman 138 kV new switching substation and installing a 138 kV/69 kV autotransformer (140MVA) | Install a 138 kV/69 kV autotransformer (140MVA) at Newman substation | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2008-10-31 |  | 138 | 0 | 0 | 140 | 0 | DALLAS |  |  |  |  | 849, 814 | Y |  | This project is related to 06TPIT0100 and 07TPIT0046 projects, and the 138/69kV-140MVA auto transfomer is moved from Wynn Joyce substation and then installed at Newman substation
Old Project | No Change | 08TPIT0174 | Tonkawa 345 kV Switching Station | Install 345 kV breakers to connect new wind farms |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R821-WA | 2008-11-01 |  | 345 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | Y
Old Project | No Change | 11TPIT0007 | Cibolo Creek - New 138kV Substation | Loop new 138kV substation into the existing 138kV Stonegate to Green Mountain line | Design/Build contract has been awarded | T-0110 | CPS | S: Bill Wards | S-0271 | 2008-11-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5093 | Y |  | There are no transformers associated with this project
Old Project | Change in Service Date. Change from 6/1/2008 11/7/2008 | 06TPIT0100 | Newman-Walnut line 69 kV to 138 kV voltage conversion | Converts voltage for the line | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2008-11-07 |  | 138 | 0 | 0.55 | 0 | 0 | DALLAS |  |  |  |  | 814, 823 | Y |  | This project is a line voltage conversion and reconductor for solving overload
Old Project | No Change | 06TPIT0179 | West Denton Sub: Expand 138 bus, add terminal for DME's line to R.G. Wells Sub | Expand 138 kV breaker and a half substation for new line to Denton's RD Wells Interchange and Substation | Delayed due to problems with site acquisition |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05006 | 2008-11-08 |  | 138 | 0 | 0 | 0 | 0 | DENTON |  |  |  |  | 986 | Y
Old Project | Change in Service Date. Change from 6/8/2008 11/8/2008 | 08TPIT0202 | Arco Tank Farm 69FF Relocation | Relocate 7 spans of line 69-FF inside the Texas City Terminal Railroad Yard to facilitate new construction by the railroad | Transmission Material lead time has delayed the project |  | TNMP | Mike Grider, 409-948-8451, mike.grider@tnmp.com |  | 2008-11-08 |  | 69 | 0.5 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  | 39400, 39410 | N
Old Project | No Change | 08TPIT0088 | TCC - New 138kV Substation | Install new 138kV substation and connect to AMD |  | T-0106 | CPS | PM: Janna Junkin | S-0269 | 2008-11-15 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5423 | Y |  | Underground transmission being installed at customer cost.
Old Project | No Change | 08TPIT0205 | Longshore 345 kV Switching Station | Expand 345 kV switching station to connect additional wind farms |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R682B-E | 2008-11-21 |  | 345 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | Y
Old Project | No Change | 08TPIT0084 | Ballinger, Add distribution transformer and cap | Ballinger, Add 138/13.02 kV transformer, 14.4 Mvar 69 kV cap |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2149 | 2008-11-30 |  | 138 | 0 | 0 | 0 | 14.4 | RUNNELS
Old Project | No Change | 09TPIT0126 | Sonora 69 kV: SPS | Open the Friend Ranch to Sonora 69 kV line when the Friend Ranch to Sonora 138 kV line trips to keep the 69 kV line from overloading |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2265 | 2008-11-30 |  | 138 | 0 | 0 | 0 | 0 | SUTTON
Old Project | Change in Service Date. Change from 6/30/2008 11/30/2008 | 09TPIT0142 | Spur: Add 138 kV Terminal, upgrade relaying | Interconnect McAdoo Wind Farm at Spur substation, add 138 kV terminal, upgrade relaying, at Aspermont and Spur. | Schedule Update | AEP GROUP 395 | AEP/TNC | Dave Goetz 918-599-2653 | 3086 | 2008-11-30 |  | 138 | 0 | 0 | 0 | 0 | DICKENS
Old Project | Change in Service Date. Change from 6/30/2008 11/30/2008 | 07TPIT0137 | Abilene Plant to Clyde, Rebuild 69/138 kV Dbld Crkt Capable | Re-build 13 miles Abilene Plant to Clyde Dbl Crkt 69/138 KV line @ 795 ACSR - Energize @ 69 kV | Schedule & Cost Update | AEP GROUP 341 | AEP/TNC | John Pulay 918-599-2653 | 1697 | 2008-11-30 |  | 69 | 0 | 13 | 0 | 0 | TAYLOR | CALLAHAN
Old Project | No Change | 07TPIT0124 | Seagoville Switch 345/138 kV autotransformer | Replace the existing 345/138 kV autotransformer |  | M4042 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4038-WA | 2008-12-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | 2006-09-27 | 2006-10-19 | N/A | 2433, 2434 | Y
Old Project | No Change | 07TPIT0233 | Anna Switch - Collin Switch 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3060-WAC | 2008-12-01 |  | 345 | 0 | 13.2 | 0 | 0 | COLLIN | COLLIN | 2006-10-10 | 2007-02-01 | 2007-04-01 | 2373, 2372 | Y
Old Project | No Change | 08TPIT0112 | Tonkawa 345 kV Switching Station shunt reactor | Install 345 kV shunt reactor |  | R677 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R673B-WA | 2008-12-01 |  | 345 | 0 | 0 | 0 | -100 | SCURRY |  |  |  |  | 1048 | Y
Old Project | No Change | 06TPIT0046 | Tyler NE - Tyler East 138 kV line | Upgrade existing 138 kV line |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R337B-E | 2008-12-01 |  | 138 | 0 | 3.74 | 0 | 0 | SMITH | SMITH | 2007-09-11 | 2008-01-01 | 2008-03-01 | 3210, 3211 | Y
Old Project | No Change | 07TPIT0123 | Seagoville Switch - Lawson Rd. 138 kV line | Upgrade existing 138 kV line |  | M4038 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4042-E | 2008-12-01 |  | 138 | 0 | 2.5 | 0 | 0 | DALLAS | DALLAS |  |  |  | 2434, 2779 | Y
Old Project | No Change | 07TPIT0230 | Tyler GE - Tyler Omen Road 138 kV line | Rebuild existing 138 kV line |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R386-E | 2008-12-01 |  | 138 | 0 | 2.4 | 0 | 0 | SMITH | SMITH | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3213, 3212 | Y
Old Project | No Change | 08TPIT0102 | Crandall 138 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3045-WA | 2008-12-01 |  | 138 | 0 | 0 | 0 | 55.2 | KAUFMAN |  |  |  |  | 2727 | Y
Old Project | No Change | 08TPIT0108 | Lufkin E. - Lufkin S. 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R388-E | 2008-12-01 |  | 138 | 0 | 6.3 | 0 | 0 | ANGELINA | ANGELINA |  |  |  | 3326 | Y
Old Project | No Change | 08TPIT0140 | Brownwood Switch - Goldthwaite 138 kV line | Reconductor existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R540-WAC | 2008-12-01 |  | 138 | 0 | 29.54 | 0 | 0 | BROWN | MILLS |  |  |  | 1655, 7070 | Y
Old Project | No Change | 08TPIT0171 | Notrees 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R822-E | 2008-12-01 |  | 138 | 0 | 0 | 0 | 0 | WINKLER | [5 empty] | Y
Old Project | No Change | 08TPIT0173 | Lavon Switch second 138 kV capacitor installation | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3069-WA | 2008-12-01 |  | 138 | 0 | 0 | 0 | 36.8 | COLLIN | [5 empty] | Y
Old Project | No Change | 08TPIT0175 | Comanche Peak capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R547-WA | 2008-12-01 |  | 138 | 0 | 0 | 0 | 18.4 | SOMERVELL | [5 empty] | Y
Old Project | No Change | 08TPIT0176 | Custer (BEC) 138 kV loop line reconfigure | Convert 138 kV loop line into two radial lines |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3029-WA | 2008-12-01 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | [5 empty] | Y
Old Project | No Change | 08TPIT0206 | Leon Switch #5 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R553-E | 2008-12-01 |  | 138 | 0 | 0 | 116 | 0 | EASTLAND | [5 empty] | Y
Old Project | No Change | 08TPIT0196 | Construct Bender 138kV Substation | Serve substation by looping into ckt.86 Barhill to Crosby |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-01 |  | 138 | 0.2 | 0 | 0 | 0 | CHAMBERS | HARRIS |  |  |  | 40155 | Y |  | No transformer capacity added.
Old Project | No Change | 08TPIT0190 | New Berlin(7612)-Olmos(7613) (Wilson Tap) | Rebuild New Berlin(7612)-Olmos (Wilson Tap)(7613) 4/0 ACSR 69-kV transmission line to 795 ACSR and convert to 138-kV. Construct Olmos 69/138 kV switching station. Relocate the New Berlin Autotransformer to Olmos switching station. |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2008-12-01 |  | 138 | 0 | 6.1 | 0 | 0 | WILSON |  |  |  |  | See Project Title | Y
Old Project | No Change | 06TPIT0235 | Rice 69 kV capacitor | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3025-WA | 2008-12-01 |  | 69 | 0 | 0 | 0 | 18.4 | NAVARRO |  |  |  |  | 2347 | Y
Old Project | No Change | 08TPIT0103 | Eastland 69 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R512-WA | 2008-12-01 |  | 69 | 0 | 0 | 0 | 9.2 | EASTLAND |  |  |  |  | 1622 | Y
Old Project | No Change | 08TPIT0106 | Gorman 69 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R514-WA | 2008-12-01 |  | 69 | 0 | 0 | 0 | 9.2 | EASTLAND |  |  |  |  | 1630 | Y
Old Project | Change in Service Date. Change from 8/29/2008 12/1/2008 | 07TPIT0026 | Booneville to Hearne Southwest Rebuild | Rebuild existing Booneville - Hearne Southwest with 795 | Estimate adjusted to reflect recent bids |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-12-01 |  | 69 | 0 | 22.2 | 0 | 0 | ROBERTSON | BRAZOS |  |  |  | 31,29,38 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | No Change | 09TPIT0065 | Spruce 2 - Power Plant Loop | Install 345kV connection between the Spruce 2 GSU and the existing Spruce 345kV switchyard |  | S-0138 | CPS | T: LeeRoy Perez S: Darrell Clifton | T-0075 | 2008-12-15 |  | 345 | 0.07 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5130 5370 | Y |  | There are no transformers associated with this project
Old Project | No Change | 06TPIT0232 | Forney - Lake Hubbard 138 kV line | Upgrade existing 138 kV line to operate at an elevated conductor temperature |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4040-WA | 2008-12-15 |  | 138 | 0 | 7.58 | 0 | 0 | KAUFMAN | DALLAS | 2008-06-02 | 2008-06-25 | N/A | 2438, 2934, 2402 | Y |  | Temporary upgrade completed in 2007 will be made permanent in 2008.
Old Project | No Change | 08TPIT0179 | DeCordova terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5142-WA | 2008-12-15 |  | 138 | 0 | 0 | 0 | 0 | HOOD | [5 empty] | Y
Old Project | No Change | 08TPIT0155 | Jefferson - College Tap ckt.06 | Reconductor 138kV ckt.06 Jefferson to College Tap to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-30 |  | 138 | 0 | 4.73 | 0 | 0 | HARRIS | HARRIS |  |  |  | 41240, 42312 | Y |  | No transformer capacity added.
Old Project | No Change | 08TPIT0157 | Blodgett - Garrott ckt.37 | Raise conductors to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-12-30 |  | 138 | 0 | 1.64 | 0 | 0 | HARRIS | HARRIS |  |  |  | 47521, 47660 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | Change in Service Date. Change from 9/1/2008 12/31/2008 | 08TPIT0117 | New Gulf tap - Pledger tap - West Columbia ckt.04 | Raise conductors, partially rebuild ckt.04 and upgrade limiting equipment at West Columbia to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-31 |  | 138 | 0 | 27.47 | 0 | 0 | WHARTON | BRAZORIA |  |  |  | 43340, 43011, 43120, 43380 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added. 3) IDEV reflects change in project in-service date.
Old Project | Change in Service Date. Change from 9/8/2008 12/31/2008 | 08TPIT0156 | H.O. Clarke - Brays ckt.09 | Raise conductors and upgrade limiting equipment at H.O. Clarke and Brays to increase thermal ratings. |  | 07TPIT0263 | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-31 |  | 138 | 0 | 2.62 | 0 | 0 | HARRIS | HARRIS |  |  |  | 47150, 47050 | Y |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2) IDEV reflects change in project in-service date.
Old Project | No Change | 08TPIT0162 | Convert Alta Loma 69/138kV dual voltage substation to a 138kV substation. | Convert Alta Loma 69/138kV dual voltage double tap configuration substation to a 138kVsectionalizing substation looped into ckt.93 PH Robinson to Hitchcock. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-12-31 |  | 138 | 0 | 0.1 | 0 | 0 | GALVESTON | GALVESTON |  |  |  | 42061, 42062. | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | No Change | 07TPIT0132 | West Denton Re-route 138 KV Line Exits | Relocate 138 lines and add new line to R.D. Wells Interchange and Substation | On Schedule | 06TPIT0179 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T06014 | 2008-12-31 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  |  | 988 | Y
Old Project | Change in Service Date. Change from 9/30/2008 12/31/2008 | 07TPIT0262 | Abilene South to Putnam, ugrades to improve ratings | Abilene South to Putnam 138 kV line, upgrades to improve rating | Schedule Update | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2171 | 2008-12-31 |  | 138 | 0 | 35.3 | 0 | 0 | TAYLOR | CALLAHAN
Old Project | No Change | 08TPIT0193 | Sonora to Hamilton 138 kV Line: Create a Dynamic Rating | Install line tension monitors to increase the normal and emergency ratings on Sonora to Hamilton 138 kV line | Cost Update | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2231 | 2008-12-31 |  | 138 | 0 | 0 | 0 | 0 | SUTTON | VAL VERDE
Old Project | Change in Service Date. Change from 9/30/2008 12/31/2008 | 07TPIT0172 | Freer 69 kV, add 1-7.2 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | Schedule | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2035 | 2008-12-31 |  | 69 | 0 | 0 | 0 | 7.2 | Val VERDE | Val VERDE
Old Project | Change in Service Date. Change from 9/30/2008 1/1/2009 | 08TPIT0073 | Convert Cardinal Lane substation and Zilker Demolition | Rebuild Cardinal Lane substation as a 138kV substation and decommission Zilker substation and relocate the Seaholm cap bank to Cardinal Lane substation. | Comments-The substation has been converted to 138kV and three 30MVA units are activated in June 2008. The 4th unit will be activated by January 2009. |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | 3230_117_2884 3240_117_4884 3240_117_2859 3240_117_4859 PLAN_117_P133 PLAN_117_P139 | 2009-01-01 |  | 138 | 0 | 0 | 90 | 0 | TRAVIS | TRAVIS |  |  |  | 9120,9179,9299, 9132 | Y
Old Project | Change in Service Date. Change from 9/30/2008 1/31/2009 | 09TPIT0111 | Bluff Creek to Oak Creek, Rebuild line | Rebuild the Bluff Creek to Oak Creek with 2X795 ACSS | Schedule Update | AEP GROUP 391 | AEP/TNC | Ashley Beasley 918-599-2653 | 2259 | 2009-01-31 |  | 138 | 0 | 20.8 | 0 | 0 | TAYLOR | COKE
Old Project | No Change | 06TPIT9999 | Doedyns-Gandy 138kV Line | Build New 138kV Line from Doedyns-Gandy Substations |  | 06TPIT0166 | MVEC | Loretta C. Gallaga (956) 514-1289 lgallaga@stec.org | 789640 | 2009-02-01 |  | 138 | 10.67 | 0 | 0 | 0 | HIDALGO | HIDALGO | 2005-02-01 | 2005-04-20
Old Project | Change in Service Date. Change from 10/1/2008 2/1/2009 | 08TPIT0098 | Gabriel to Schwertner Rebuild | Rebuild existing Gabriel to Schwertner |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-02-01 |  | 69 | 0 | 9.4 | 0 | 0 | WILLIAMSON | WILLIAMSON |  |  |  | 1221237345 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | No Change | 07TPIT0152 | Abilene South, 2nd 69/138 kV Auto | Abilene South, add 2nd 69/138 kV 90 MVA Autotransformer |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2134 | 2009-02-28 |  | 138 | 0 | 0 | 90 | 0 | TAYLOR
Old Project | No Change | 09TPIT0141 | Abilene South, Replace 138/69 kV Auto | Abilene South, add 2nd 69/138 kV 90 MVA Autotransformer |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2134 | 2009-02-28 |  | 138 | 0 | 0 | 90 | 0 | TAYLOR
Old Project | Change in Service Date. Change from 10/1/2008 3/1/2009 | 09TPIT0055 | Skyline to Dresden - 138kV Line Upgrade | Upgrade small section from 556 to 2-1272 to match rest of line |  |  | CPS | T: Adam Marin | T-0128 | 2009-03-01 |  | 138 | 0 | 1 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5025 5417 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
Old Project | No Change | 08TPIT0024 | Wilson(7615)-CPS Sutherland Springs(5418) | Construct a new 795 ACSR (220-MVA) 138-kV transmission line between the Wilson(7615) and Floresville Sutherland Springs(5418) substations. |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2009-03-01 |  | 138 | 9.2 | 0 | 0 | 0 | WILSON |  |  |  |  | See Project Title | Y
Old Project | Change in Service Date. Change from 10/15/2008 3/1/2009 | 06TPIT0113 | McNeil autotransformer replacement | With the completion of 138kV conversion of circuit 822 and 824, the Seaholm auto will replace the autotransformer at the McNeil substation. |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P049 | 2009-03-01 |  | 138 | 0 | 0 | 200 | 0 | TRAVIS | TRAVIS |  |  |  | 9079, 9080 | Y
Old Project | No Change | 09TPIT0052 | Justin Lane 138/69 kV substation | Establish a new substation at Justin Lane site and install (2) 30MVA transformers. The substation will cut into the existing Ckt 811 (McNeil to Koenig Lane). |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | 3240_117_4855 PLAN_117_P042 PLAN_117_P135 | 2009-03-01 |  | 138 | 0.5 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  | 9225 | Y
Old Project | No Change | 08TPIT0097 | Rhome to Roanoke Rebuild | Rebuild existing Rhome to Roanoke |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-03-01 |  | 138 | 0 | 16.6 | 0 | 0 | WISE | TARRANT |  |  |  | 5765856401852 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | Change in Service Date. Change from 10/30/2008 3/1/2009 | 09TPIT0029 | Hilltop Lakes Sw. to Hearne Rebuild | Rebuild existing Hilltop Lakes to Hearne |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-03-01 |  | 69 | 0 | 14.5 | 0 | 0 | ROBERTSON | ROBERTSON |  |  |  | 36,53,57,43 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | Change in Service Date. Change from 10/30/2008 3/16/2009 | 07TPIT0076 | Friendship-Escarpment-Manchaca | Construct a new 795 ACSR 138-kV transmission line (approximately eight miles) between the Friendship(7507) and Manchaca(7504) substations. Construct a new 138-26.18-kV 22.4-MVA distribution substation to serve the load requirements in the area south of Austin. The new Escarpment(7672) substation will be cut midway into the new 138-kV Friendship-Manchaca transmission line. |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 1006535 | 2009-03-16 |  | 138 | 8 | 0 | 0 | 0 | TRAVIS | HAYS |  |  |  | SEE PROJECT DESCRIPTION | Y |  | The name of the new substation was changed from HWY 45 to Escarpment.
Old Project | No Change | 08TPIT0082 | Live Oak, Add 69/138 kV Auto | Add second Auto 138/69 (LTC) at Live Oak 50 MVA - Expand to a four position ring bus |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2130 | 2009-03-31 |  | 138 | 0 | 0 | 50 | 0 | SCHLEICHER
Old Project | Change in Service Date. Change from 10/30/2008 3/31/2009 | 07TPIT0098 | Replace five poles, Hickory - Locust 69kV Transmission Line | Replace five poles in an existing 69kV transmission line | On Schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600774 | 2009-03-31 |  | 69 | 0 | 0.25 | 0 | 0 | DENTON | DENTON |  |  | NA | 910, 914 | Y
Old Project | No Change | 09TPIT0092 | VH Braunig to Streich to OW Sommers - 138kV Transmission Line Reroute | The VH Braunig tie breakers will be opened in order to reduce fault current creating an East and West bus. The following reroutes will occur: Braunig E - Streich becomes Braunig W - Streich Sommers - Streich becomes Deely - Streich |  | S-0369 | CPS | T: Adam Marin S: Keith Calle | T-0122 | 2009-04-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5395 5417 | Y |  | There are no transformers associated with this project
Old Project | No Change | 09TPIT0006 | Lobo, build 138/69 kV substation | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV |  | AEP GROUP 216 | AEP/TCC | Bill Eakin 918-599-2653 | 1306 | 2009-04-01 |  | 138 | 0 | 0 | 93 | 0 | WEBB
Old Project | No Change | 07TPIT0092 | Denton West to RD Wells 138kV Transmission Line | Construct 4.6 miles of new 138kV transmission line | On schedule | 07TPIT0091, 0094, 0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600129 | 2009-04-01 |  | 138 | 4.6 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 986, 930 | Y
Old Project | Change in Service Date. Change from 11/1/2008 4/1/2009 | 09TPIT0063 | Whitney to Bosque Reconductor | Reconductor existing Whitney to Bosque 138kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-04-01 |  | 138 | 0 | 13.4 | 0 | 0 | BOSQUE | MCLENNAN |  |  |  | 241181177 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | No Change | 08TPIT0138 | Aransas Pass: Add 1-28.8 MVAR Cap Bank | Aransas Pass: Add 3-69 KV Breakers, Add 1-28.8 MVAR 69 KV Cap Bank |  | AEP GROUP 029 | AEP/TCC | Michael Glueck 918-599-2653 | 1192 | 2009-04-01 |  | 69 | 0 | 0 | 0 | 28.8 | ARANSAS
Old Project | Change in Service Date. Change from 11/3/2008 4/1/2009 | 06TPIT0198 | Hickory Substation 69kV Bay Addition | Construct new 69kV bays to allow tie in of the new Iron Horse to Hickory transmission line | On Schedule | 07TPIT0095 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600128 | 2009-04-01 |  | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 910 | Y
Old Project | No Change | 07TPIT0095 | RD Wells to Hickory 69kV Transmission Line | Construct 1.6 miles of new 138kV transmission line to be operated at 69kV | On schedule | 07TPIT0091, 0092, 0094, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600130 | 2009-04-01 |  | 69 | 1.6 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 932, 910 | Y
Old Project | No Change | 09TPIT0136 | Northern Natural 2 Mvar Capacitor bank | Install 2 Mvar 69 kV Cap Bank at Northern Natural |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com |  | 2009-04-09 |  | 69 | 0 | 0 | 0 | 0 | PECOS | PECOS |  |  |  | 38440 | Y
Old Project | Change in Service Date. Change from 11/21/2008 4/30/2009 | 09TPIT0087 | Singleton Switching Station | Build a new 345 kV Singleton substation. Loop ckt.1 Jewett - T.H. Wharton, ckt.1 Jewett - Tomball, ckt.75 Gibbons Creek - Roans Prairie and ckt.99 Gibbons creek - Obrien into the new substation. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-04-30 |  | 345 | 0 | 0.5 | 0 | 0 | GRIMES | GRIMES | 2007-01-08 | 2007-07-16 | 2007-08-21 | 44645 | Y |  | 1)_Part of Houston Area Constraint Mitigation Project, Phase II. 2)_No transformer capacity to be added. 3) IDEV reflects change in project in-service date.
New Project | New Project | 09TPIT0175 | Reconfigure ckt.03 Lynch - Cedar Bayou. | Reconfigure ckt.03 Lynch - Cedar Bayou substation to create two new circuits ckt.03 Lynch - EXXON and ckt.03 Baytown - Cedar Bayou substation per customers request. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-04-30 |  | 138 | 0.7 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 41010, 40011, 40015, 40170, 40570 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | Change in Service Date. Change from 11/30/2008 4/30/2009 | 07TPIT0043 | Wynn Joyce-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2009-04-30 |  | 138 | 0 | 2.81 | 0 | 0 | DALLAS |  |  |  |  | 811, 824 | Y |  | This project is a line voltage conversion and reconductor for solving overload
Old Project | Change in Service Date. Change from 11/30/2008 4/30/2009 | 07TPIT0044 | Miller 69 kV to 138 kV voltage conversion | Converts voltage for the substation | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2009-04-30 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 824 | Y |  | This project is related to 06TPIT0098, 07TPIT0048, 07TPIT0043, and 05TPIT0026 projects
Old Project | Change in Service Date. Change from 11/30/2008 4/30/2009 | 07TPIT0046 | Newman-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2009-04-30 |  | 138 | 0 | 2.27 | 0 | 0 | DALLAS |  |  |  |  | 814, 824 | Y |  | This project is a line voltage conversion and reconductor for solving overload
Old Project | Change in Service Date. Change from 12/1/2008 5/1/2009 | 09TPIT0082 | Jewett - Big Brown 345 kV circuit #1 | Upgrade circuit breaker and associated equipment at Big Brown to increase emergency rating of line. | Construction schedule change |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R707-E | 2009-05-01 |  | 345 | 0 | 0 | 0 | 0 | FREESTONE |  |  |  |  | 3390, 3380 | Y |  | 1)_Part of Houston Area Constraint Mitigation Project, Phase II. 2)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | No Change | 09TPIT0139 | Johnson Switch | Add 345 kV circuit breakers |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3070-E | 2009-05-01 |  | 345 | 0 | 0 | 0 | 0 | JOHNSON | [5 empty] | Y
Old Project | No Change | 10TPIT0035 | Roanoke Switching Station #1 345/138 kV autotransformer replacement | Replace existing 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5122-E | 2009-05-01 |  | 345 | 0 | 0 | 600 | 0 | DENTON |  | 2007-12-31 | 2008-02-26 | N/A | 1850, 1851 | Y
New Project | New Project | 09TPIT0148 | Falcon Seaboard terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R837-E | 2009-05-01 |  | 345 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | Y
New Project | New Project | 09TPIT0152 | Graham terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R575-E | 2009-05-01 |  | 345 | 0 | 0 | 0 | 0 | YOUNG | [5 empty] | Y
New Project | New Project | 09TPIT0155 | Lake Creek terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R715-E | 2009-05-01 |  | 345 | 0 | 0 | 0 | 0 | MCLENNAN | [5 empty] | Y
New Project | New Project | 09TPIT0158 | Midland East terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R838-E | 2009-05-01 |  | 345 | 0 | 0 | 0 | 0 | MIDLAND | [5 empty] | Y
New Project | New Project | 09TPIT0160 | Morgan Creek terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R833-E, R841-E & R842-E | 2009-05-01 |  | 345 | 0 | 0 | 0 | 0 | MITCHELL | [5 empty] | Y
New Project | New Project | 09TPIT0169 | Tradinghouse terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R716-E | 2009-05-01 |  | 345 | 0 | 0 | 0 | 0 | MCLENNAN | [5 empty] | Y
Old Project | No Change | 09TPIT0094 | Westover Hills - New 138kV Substation | Install new 138kV substation and connect to VLSI |  | T-0121 | CPS | T: LeeRoy Perez S: Darrell Clifton | S-0328 | 2009-05-01 |  | 138 | 1.36 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5488 | Y |  | There are no transformers associated with this project
Old Project | Change in Service Date. Change from 12/1/2008 5/1/2009 | 10TPIT0046 | Austin to Tuttle - 138kV Transmission Line Rebuild | Reconductor existing 138 kV line |  | S-0396 | CPS | T: Kevin Phillips | T-0127 | 2009-05-01 |  | 138 | 0 | 2 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5005 5435 | Y |  | There are no transformers associated with this project
Old Project | No Change | 06TPIT0037 | Carrollton East - Renner 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M448-WA | 2009-05-01 |  | 138 | 0 | 6.9 | 0 | 0 | DALLAS | DALLAS |  |  |  | 2356, 2611, 2578, 2582 | Y |  | Carrollton East - Farmers Branch Gillis Rd section will be completed in 12/2008.
Old Project | No Change | 07TPIT0016 | Saginaw - Euless/Roanoke Switch 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M507-E | 2009-05-01 |  | 138 | 0 | 17.4 | 0 | 0 | TARRANT | TARRANT |  |  |  | 1957, 2039, 2040, 2041, 2042, 2043, 2044, 2047 | Y |  | Saginaw - Watagua section will be completed in 12/2008.
Old Project | No Change | 07TPIT0158 | Sandow Switch - Salty - Thorndale North - Taylor 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R485-E | 2009-05-01 |  | 138 | 0 | 20.9 | 0 | 0 | MILAM | WILLIAMSON | 2007-04-23 | 2007-08-01 | N/A | 3430, 3661, 3659, 3658 | Y |  | Sandow Switch - Thorndale N section will be completed in 12/2008.
Old Project | No Change | 07TPIT0224 | Decatur - Bennett Rd - Wise County 138 kV line | Rebuild existing 138 kV line |  | R510A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R511-E | 2009-05-01 |  | 138 | 0 | 12.6 | 0 | 0 | WISE | WISE |  |  |  | 1582, 1566 | Y |  | Wise County - Bennett Rd section will be completed in 12/2008.
Old Project | No Change | 07TPIT0225 | Bennett Road Switching Station | Construct 138 kV switching station |  | R510A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510B-WA | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | WISE |  |  |  |  | 1582, 1565, 1566, 1568 | Y
Old Project | No Change | 08TPIT0152 | Big Spring - Chalk - McDonald 69 kV line | Rebuild existing 69 kV line for double-circuit operation with one 138 kV circuit and one 69 kV circuit |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R645-E | 2009-05-01 |  | 138 | 18 | 18 | 0 | 0 | HOWARD | HOWARD | 2007-09-01 | 2008-01-18 | N/A |  | Y |  | Big Spring - Signal Mountain section wll be completed by 12/2008.
Old Project | No Change | 09TPIT0022 | Killeen Switch - S. Harker Heights 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R410-E | 2009-05-01 |  | 138 | 0 | 5.3 | 0 | 0 | BELL | BELL |  |  |  | 3423, 3633 | Y
Old Project | No Change | 09TPIT0119 | Whitesboro SE 138 kV tap line | Construct 138 kV line and convert existing 69 kV line and substations to 138 kV operation. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R546-E | 2009-05-01 |  | 138 | 0.9 | 7.9 | 0 | 0 | GRAYSON | GRAYSON |  |  |  |  | Y
Old Project | No Change | 09TPIT0140 | Muleshoe Road Switch | Add 138 kV switching station to connect a new wind farm. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R832-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | BORDEN | [5 empty] | Y
Old Project | No Change | 10TPIT0036 | Temple Elm Creek Switching Station - Temple N. 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R491-E | 2009-05-01 |  | 138 | 0 | 0.6 | 0 | 0 | BELL | BELL |  |  |  | 13662, 3608 | Y
Old Project | Change in Service Date. Change from 12/1/2008 5/1/2009 | 08TPIT0107 | Leon - Flat Creek 138 kV line | Rebuild existing 138 kV line | Construction schedule change |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R520A-E | 2009-05-01 |  | 138 | 0 | 19.5 | 0 | 0 | EASTLAND | ERATH |  |  |  | 1624, 1640 | Y
Old Project | Change in Service Date. Change from 12/1/2008 5/1/2009 | 10TPIT0057 | Benbrook series reactors | Install a 2-ohm 138 kV series reactor on autotransformer A and B. | Construction schedule change |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5068-E & M5139-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | TARRANT | [5 empty] | N
New Project | New Project | 09TPIT0143 | Anna Switch 138 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3080-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 110.4 | COLLIN | [5 empty] | Y
New Project | New Project | 09TPIT0144 | Collin Switch 138 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3081-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 110.4 | COLLIN | [5 empty] | Y
New Project | New Project | 09TPIT0145 | Shamburger Switch 138 kV capacitors | Install capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R860-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 110.4 | SMITH | [5 empty] | Y
New Project | New Project | 09TPIT0147 | China Grove terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R684-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | MITCHELL | [5 empty] | Y
New Project | New Project | 09TPIT0150 | Graham terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R848-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | YOUNG | [5 empty] | Y
New Project | New Project | 09TPIT0154 | Lake Creek terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R725-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | MCLENNAN | [5 empty] | Y
New Project | New Project | 09TPIT0156 | Leon Switch terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R577-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | EASTLAND | [5 empty] | Y
New Project | New Project | 09TPIT0157 | Liquid Air terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R869-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR | [5 empty] | Y
New Project | New Project | 09TPIT0159 | Midland West terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R843-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | MIDLAND | [5 empty] | Y
New Project | New Project | 09TPIT0161 | Moss Switch terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R846-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR | [5 empty] | Y
New Project | New Project | 09TPIT0162 | Odessa terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R871-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR | [5 empty] | Y
New Project | New Project | 09TPIT0163 | Odessa EHV terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R870-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | ECTOR | [5 empty] | Y
New Project | New Project | 09TPIT0164 | Scurry Chevron terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R844-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | Y
New Project | New Project | 09TPIT0165 | Shamburger Switch terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R686-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | SMITH | [5 empty] | Y
New Project | New Project | 09TPIT0168 | Temple Switch terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R723-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | BELL | [5 empty] | Y
New Project | New Project | 09TPIT0170 | Tyler Bullard Road terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R836-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | SMITH | [5 empty] | Y
New Project | New Project | 09TPIT0171 | Tyler South terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R835-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | SMITH | [5 empty] | Y
New Project | New Project | 09TPIT0172 | Wichita Falls Switch terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R576-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | WICHITA | [5 empty] | Y
New Project | New Project | 09TPIT0173 | Waco West - Waco Woodway 138 kV line | Rebuild existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R409-E | 2009-05-01 |  | 138 | 0 | 3.25 | 0 | 0 | MCLENNAN | MCLENNAN | 2008-07-07 |  |  |  | Y |  | Project submitted to RPG by Luminant.
Old Project | Change in Service Date. Change from 1/31/2009 5/1/2009 | 06TPIT0030 | West Waco - Lorena - Eddy 69 kV line | Upgrade existing 69 kV line | Construction delays |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R093-WA | 2009-05-01 |  | 69 | 0 | 16.3 | 0 | 0 | MCLENNAN | MCLENNAN |  |  |  | 3437, 3577, 3580 | Y |  | The Waco West to Lorena section will be reconstructed by 12/31/2008.
Old Project | No Change | 09TPIT0048 | Poage - Temple Taylors Valley - Bell County 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R472-E | 2009-05-01 |  | 69 | 0 | 3.4 | 0 | 0 | BELL | BELL |  |  |  | 3635, 3636 | Y
New Project | New Project | 09TPIT0149 | Garden City terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R840-E | 2009-05-01 |  | 69 | 0 | 0 | 0 | 0 | GLASSCOCK | [5 empty] | Y
New Project | New Project | 09TPIT0151 | Graham terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R554-E | 2009-05-01 |  | 69 | 0 | 0 | 0 | 0 | YOUNG | [5 empty] | Y
New Project | New Project | 09TPIT0166 | Snyder terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R685-E | 2009-05-01 |  | 69 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | Y
New Project | New Project | 09TPIT0167 | Spraberry terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R872-E | 2009-05-01 |  | 69 | 0 | 0 | 0 | 0 | MIDLAND | [5 empty] | Y
Old Project | Change in Service Date. Change from 3/1/2009 5/1/2009 | 08TPIT0050 | Gustine to Hamilton Rebuild | Rebuild Hamilton to Gustine 69kv line with 795 and 138kv construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-05-01 |  | 69 | 0 | 17.1 | 0 | 0 | COMANCHE | HAMILTON |  |  |  | 258279 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | No Change | 07TPIT0231 | Tyler Grande 345/138 kV Switching Station | Construct switching station and install a 345/138 kV autotransformer, 138 kV capacitor and 138 kV series reactor |  | R387, R337B & R386 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R384-E | 2009-05-15 |  | 345 | 0 | 0 | 493 | 0 | SMITH |  | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3102, 3196 | Y
Old Project | No Change | 07TPIT0232 | Tyler Grande - Tyler S. 138 kV line | Rebuild existing 138 kV line for double-circuit operation |  | R384 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R387-E | 2009-05-15 |  | 138 | 2.32 | 2.32 | 0 | 0 | SMITH | SMITH | 2007-09-01 | 2008-01-01 | 2008-03-01 | 3196, 3218 | Y
New Project | New Project | 09TPIT0146 | Chalk terminal equipment | Replace terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R839-E | 2009-05-23 |  | 69 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | Y
Old Project | No Change | 08TPIT0169 | Cut Bluff Creek to Oak Creek into Nicole | Provide inteconnection at new Nicole substation and rebuild the Red Creek to Nicole 138kV line with 2X795 ACSS |  | AEP GROUP 390 | AEP/TNC | Ashley Beasley 918-599-2653 | 3116 | 2009-05-29 |  | 138 | 0 | 2 | 0 | 0 | COKE | COKE
Old Project | No Change | 09TPIT0083 | P.H. Robinson - Oasis ckt.99 | Raise conductors and upgrade in-series equipment at P.H. Robinson to increase thermal rating. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-05-31 |  | 345 | 0 | 20.45 | 0 | 0 | GALVESTON | BRAZORIA | 2007-01-08 |  |  | 42000, 43035 | N | 1) Stakeholder question: I'm trying to determine what the upgraded thermal capacity will be on the 345-kV Oasis (to Alvin) to PH Robinson line (or Oasis to P.H. Robinson) will be after the P.H. Robinson to Oasis upgrades are complete. The 2012 Summer Peak load flow case that I am using reports 957 Normal and 1,173 Emergency but it's not clear if that is the expected final thermal capacity after the upgrades. It appears that the upgrade is TPIT Project Number 09TPIT0083 but my question is not necessarily limited to that project but seeks information on the final forward-looking thermal limit on the P.H. Robinson to Oasis connection regardless of which TPIT projects are or are not involved. 2) CNP response May 27, 2008: While the final actual ratings can be affected by unanticipated circumstances, the expected rating after the upgrade is 1173 MVA for the continuous rating and 1450 MVA for the emergency rating. Please note that a final determination concerning whether to proceed with this project has not yet been made. The project status and scheduled completion date are subject to change pending such determination. | 1) Project is still under review. 2) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | No Change | 08TPIT0158 | Baytown - Haney ckt.66 | Raise conductors and upgrade limiting equipment at Baytown to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2009-05-31 |  | 138 | 0 | 7.1 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40170, 40172, 40790 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | No Change | 09TPIT0088 | East Bernard - Wallis - Sealy - Peters ckt.65 | Raise conductors and partially rebuild ckt.65 to increase thermal ratings. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-05-31 |  | 138 | 0 | 25.28 | 0 | 0 | WHARTON | AUSTIN |  |  |  | 44190, 44740, 44640, 46220 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added. 3) IDEV reflects change in project scope.
Old Project | Change in Service Date. Change from 4/1/2009 5/31/2009 | 08TPIT0145 | Putnam, reconnect the Phase Shifting Transformer | Putnam, reconnect the Phase Shifting Transformer from the Abilene South to Putnam line to Leon to Putnam line | Schedule Update | AEP GROUP 390 | AEP/TNC | Dave Goetz 918-599-2653 | 2271 | 2009-05-31 |  | 138 | 0 | 0 | 150 | 0 | CALLAHAN
Old Project | No Change | 09TPIT0109 | Nicole, Four Position Ring | Provide inteconnection at new Nicole substation and rebuild the Red Creek to Nicole 138kV line with 2X795 ACSS |  | AEP GROUP 390 | AEP/TNC | Ashley Beasley 918-599-2653 | 3115 | 2009-05-31 |  | 138 | 0 | 0 | 0 | 0 | COKE
Old Project | Change in Service Date. Change from 4/1/2009 5/31/2009 | 07TPIT0047 | Centerville-Miller line 69 kV to 138 kV voltage conversion | Converts voltage for the line | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2009-05-31 |  | 138 | 0 | 2.68 | 0 | 0 | DALLAS |  |  |  |  | 810, 824 | Y |  | This project is a line voltage conversion and reconductor for solving overload
Old Project | No Change | 09TPIT0077 | McCree-Shiloh 138 kV line | Line reconductor | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2009-05-31 |  | 138 | 0 | 2.2 | 0 | 0 | DALLAS |  |  |  |  | 830, 834 | Y |  | This project is a line reconductor for solving overload
Old Project | No Change | 09TPIT0130 | Newman 138 kV, install 24.0 MVAR Cap Bank | Install 24 MVAR capacitor bank to support local low voltage problems | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2009-05-31 |  | 138 | 0 | 0 | 0 | 24 | DALLAS |  |  |  |  | 849 | Y |  | This project is a capacitor bank installing for supporting local load voltage problems
Old Project | Change in Service Date. Change from 4/30/2009 5/31/2009 | 09TPIT0104 | Presidio, add NaS Battery | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a Nas Battery at Presidio | Schedule Update | AEP GROUP 358 | AEP/TNC | Brett Madison 918-599-2653 | 2281 | 2009-05-31 |  | 69 | 0 | 0 | 0 | 0 | PRESIDIO |  | 2008-03-21 | 2008-06-10 | 2008-07-15
Old Project | No Change | 09TPIT0007 | Spruce to Skyline - 345kV 2nd Circuit | Build second 345kV line from Spruce to Skyline. The second circuit will be installed on existing transmission structures |  | S-0127 | CPS | T: LeeRoy Perez S: Darrell Clifton | T-0050 | 2009-06-01 |  | 345 | 20.77 | 0 | 0 | 0 | BEXAR | BEXAR | 2007-05-08 | 2007-05-31 | N/A | 5371 5400 | Y |  | There are no transformers associated with this project
Old Project | No Change | 09TPIT0131 | Interconnect a new combined cycle plant at Cedar Bayou. | Add a new combined cycle plant at the NRG Cedar Bayou site connected to the Cedar Bayou substation. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-06-01 |  | 345 | 0 | 0 | 0 | 0 | CHAMBERS | CHAMBERS |  |  |  | 40000, 48583, 48584, 48585 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | Change in Service Date. Change from 5/1/2009 6/1/2009 | 06TPIT0166 | MVEC Palmhurst-MVEC Merett | Rebuild 138kV line from Palmhurst to Merett Substations |  | 06TPIT0165 | MVEC | Loretta C. Gallaga (956) 514-1289 lgallaga@stec.org | 984501 | 2009-06-01 |  | 138 | 0 | 4.2 | 0 | 0 | HIDALGO | HIDALGO
Old Project | No Change | 09TPIT0095 | Cagnon - 138kV Capacitor Bank Addition | 80 MVAR Capacitor Addition at Cagnon |  |  | CPS | S: Darrell Clifton | S-0362 | 2009-06-01 |  | 138 | 0 | 0 | 0 | 80 | BEXAR | BEXAR |  |  |  | 5055 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
Old Project | No Change | 09TPIT0096 | Floresville - 138kV Capacitor Bank Addition | Install a new circuit breaker and 10MVAR capacitor bank at the Floresville substation |  |  | CPS | S: Darrell Clifton | S-0364 | 2009-06-01 |  | 138 | 0 | 0 | 0 | 10 | BEXAR | BEXAR |  |  |  | 5155 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
Old Project | No Change | 09TPIT0134 | Galle - New Substation | Construct a new 138-kV 22.4 MVA substation on the LCRA Zorn-Luling 138-kV transmission line. |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2009-06-01 |  | 138 | 0 | 0 | 22.4 | 0 | GUADALUPE |  |  |  |  | See Project Title | N
Old Project | No Change | 05TPIT0118 | Hidden Valley 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Hidden Valley substation. | Comments: Delayed to June 2009 due to scheduling conflicts. |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | 3230_117_1442 | 2009-06-01 |  | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS |  |  |  | 9207 | Y
Old Project | No Change | 07TPIT0087 | Lakeshore 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Lakeshore substation. | Comments: Delayed to June 2009 due to scheduling conflicts. |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P205 | 2009-06-01 |  | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS |  |  |  | 9128 | Y |  | The capacitor is relocated to Lakeshore sub due to the long permitting process required at Northland.
New Project | New Project | 09TPIT0177 | AMD to Pedernales Upgrade | Combine circuit 1014 (Pedernales to Burleson) and circuit 1017 (AMD to Burleson) to one single circuit bypassing Burleson substation. |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P285 | 2009-06-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 911891209151 | Y
Old Project | Change in Service Date. Change from 5/1/2009 6/1/2009 | 07TPIT0091 | RD Wells 138kV to 69kV Interchange | Construct a new 138kV to 69 kV 150MVA interchange | On schedule | 07TPIT0092, 0094,0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600005 | 2009-06-01 |  | 138 | 0 | 0 | 168 | 0 | DENTON | DENTON |  |  | NA | 930, 932 | Y
Old Project | No Change | 09TPIT0027 | Fox to Hilltop 138KV Conversion | Convert existing Fox to North Texas 69KV line to 138KV operation. Rebuild Fox to Brock line with double circuit construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 |  | 138 | 0 | 3.7 | 0 | 0 | PARKER | PARKER |  |  |  | 501, 495, 498, 487, 478 | Y |  | There is no reactive or transformer capability associated with this project
New Project | New Project | 09TPIT0178 | Fox to Granbury 138KV Conversion | Convert exisitng Fox to Granbury 69KV line to 138KV operation |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 |  | 138 | 3 | 0 | 0 | 0 | Parker | Hood |  |  |  | 306487478 | N
Old Project | Change in Service Date. Change from 5/1/2009 6/1/2009 | 07TPIT0250 | Foster Field: Install 2-7.2 MVAR 69 kV Cap Banks | Reconductor Victoria to Magruder, reconductor 69 kV line to 795 ACCC and Install 138/69 kV 187 MVA autotransformer at Magruder on the Victoria to Thomaston 138kV line | Cost and Schedule Update | AEP GROUP 389 | AEP/TCC | Dave Goetz 918-599-2653 | 2047 | 2009-06-01 |  | 69 | 0 | 0 | 0 | 14.4 | VICTORIA
Old Project | No Change | 08TPIT0133 | Rocksprings Station: Install 69 KV Ring Bus | Rocksprings : Install 5-69 KV Breaker Ring Bus and 3.6 MVAR Cap Bank |  | AEP GROUP 377 | AEP/TCC | Brian Johnson 918-599-2653 | 3019 | 2009-06-01 |  | 69 | 0 | 0 | 0 | 3.6 | EDWARDS
Old Project | Change in Service Date. Change from 5/1/2009 6/2/2009 | 07TPIT0094 | RD Wells Substation | Install three 25MVA, 138kV to 13.2kV substation transformers served from the RD Wells 138kV bus | On schedule | 07TPIT0091, 0092, 0095, 0179 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600126 | 2009-06-02 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 932 | Y
Old Project | No Change | 09TPIT0123 | Parkdale SVC installation | Install two +300 Mvar/-265 Mvar SVCs |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4056-WA | 2009-06-15 |  | 138 | 0 | 0 | 0 | 600 | DALLAS |  | 2007-02-01 |  | 2007-08-01 |  | Y
Old Project | No Change | 09TPIT0056 | McNeil-Gilleland | Replace under-rated limiting line terminal equipment to increase McNeil (7334)-Gilleland (7336) to the conductor's rating. |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2009-06-30 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | No Change | 09TPIT0059 | Lago Vista-Nameless | Replace under-rated limiting line terminal equipment at Lago Vista to increase Lago Vista (7352)-Nameless (7526) to the conductor's rating. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2009-06-30 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | SEE PROJECT DESCRIPTION | Y | This project is included with the Buda-Turnersville project.
Old Project | No Change | 09TPIT0060 | Buda-Turnersville | Replace under-rated limiting line terminal equipment at Buda to increase Buda (7498)-Turnersville (7500) to the conductor's rating. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2009-06-30 |  | 138 | 0 | 0 | 0 | 0 | HAYS | HAYS |  |  |  | SEE PROJECT DESCRIPTION | Y | This project is included with the Lago Vista-Nameless project.
Old Project | No Change | 09TPIT0070 | Fayetteville-Willow Springs | Replace under-rated limiting line terminal equipment to increase Fayetteville (7286)-Willow Springs (7273) to the conductor's rating. | Columns left blank are explained in (AG) |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2009-06-30 |  | 138 | 0 | 0 | 0 | 0 | FAYETTE |  |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | No Change | 09TPIT0071 | Avery Ranch-Jollyville | Replace under-rated limiting line terminal equipment to increase Avery Ranch (7534)-Jollyville (9223) to the conductor's rating. | Columns left blank are explained in (AG) |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2009-06-30 |  | 138 | 0 | 0 | 0 | 0 | WILLIAMSON |  |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | No Change | 09TPIT0090 | Williamson County Capacitor Bank Additions | Add one 138 kV 31.2 MVAR capacitor bank at Avery Ranch(7534) and add one 138 kV 31.2 MVAR capacitor bank at Buttercup (7531). |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2009-06-30 |  | 138 | 0 | 0 | 0 | 62.4 | WILLIAMSON |  |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | No Change | 09TPIT0091 | Giddings Capacitor Bank Addition | Add a 138 kV 31.2 MVAR capacitor bank at the Giddings (7302). |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2009-06-30 |  | 138 | 0 | 0 | 0 | 31.2 | LEE |  |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | Change in Service Date. Change from 5/31/2009 6/30/2009 | 06TPIT0133 | Los Fresnos, Convert 69 kV distribution substation to 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 1708 | 2009-06-30 |  | 138 | 0 | 0 | 0 | 0 | CAMERON
Old Project | No Change | 06TPIT0014 | LaPalma to Loma Alta, cut-in Los Fresnos at 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 645 | 2009-06-30 |  | 138 | 0.1 | 0 | 0 | 0 | CAMERON | CAMERON
Old Project | No Change | 07TPIT0252 | Greta: Install 1-7.2 MVAR 69 kV Cap Bank | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV 50 MVA auto and build new 69 kV line from Melon Creek to Tatton |  | AEP GROUP 100 | AEP/TCC | Paul Hassink 918-599-2653 | 2045 | 2009-06-30 |  | 69 | 0 | 0 | 0 | 7.2 | REFUGIO
Old Project | No Change | 09TPIT0125 | Cisco: Auto-Sectionalizing Scheme | Add auto sectionalizing scheme at Cisco to allow the 69 kV line to operate normally open |  | AEP GROUP 450 | AEP/TNC | Dave Goetz 918-599-2653 | 2272 | 2009-06-30 |  | 69 | 0 | 0 | 0 | 0 | EASTLAND
Old Project | Change in Service Date. Change from 5/31/2009 7/1/2009 | 09TPIT0005 | Laredo Plant to Lobo, upgrade 69 kV to 138 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | Cost Update | AEP GROUP 216 | AEP/TCC | Bill Eakin 918-599-2653 | 1303 | 2009-07-01 |  | 138 | 0 | 16.5 | 0 | 0 | WEBB | WEBB
Old Project | Change in Service Date. Change from 5/31/2009 7/1/2009 | 09TPIT0138 | Hillsboro - Alvarado 69 kV line | Rebuild existing 69 kV line | Construction schedule change |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R489-E | 2009-07-01 |  | 69 | 0 | 27.2 | 0 | 0 | HILL | JOHNSON | 2008-05-01 | 2008-06-10 | N/A |  | Y
Old Project | Change in Service Date. Change from 5/31/2009 7/1/2009 | 09TPIT0062 | West Weatherford to Shady Grove Rebuild | Rebuild existing West Weatherford to Shady Grove 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-07-01 |  | 69 | 0 | 2.35 | 0 | 0 | PARKER | PARKER |  |  |  | 5151585 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | No Change | 05TPIT0092 | Port O'Connor 69 kV line | Construct new 25 mile 336 MCM ACSR 69 kV line between the AEP Union Carbide station and STEC's Port O'Connor substation. | Acquiring Right-Of-Way Easements |  | STEC | Dung Nguyen, 361-485-6142, dnguyen@stec.org |  | 2009-07-06 |  | 69 | 25 | 0 | 0 | 0 | CALHOUN | CALHOUN |  | 2001-06-22 | 2001-07-09 | 5596-8149 | Y
Old Project | No Change | 09TPIT0128 | Zorillo: Build 345kV Station | Build 345 kV switching station in the Nelson Sharpe to Rio Hondo 345 kV line and 345kV line from Ajo to IPP's |  | AEP GROUP 343 | AEP/TCC | John Pulay 918-599-2653 | 2222 | 2009-08-01 |  | 345 | 0 | 0 | 0 | 0 | KENEDY
New Project | New Project | 09TPIT0174 | Lufkin Switch - Aspen Power 138 kV line | Construct second 138 kV circuit on an existing line to connect a new power plant. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R850-E | 2009-08-01 |  | 138 | 1.9 | 0 | 0 | 0 | ANGELINA | ANGELINA |  |  |  |  | Y
Old Project | No Change | 06TPIT0247 | Salt Dome / AEP Clemville 69 kV tie | Construct a new United Brine substation in the 3.0 mile, 1/0 ACSR, 69 kV AEP transmission line from AEP Clemville Tap to AEP Clemville Substation. Construct a 4/0 ACSR 69 kV line from the new Texas Brine substation to the existing STEC South Clemville substation | Tie is delayed to verify load. Load customer delays and changing load configuration. Project scope may be reduced before actual construction. Name Changed from "United Brine" to "Salt Dome" |  | STEC | Dung Nguyen, 361-485-6142, dnguyen@stec.org |  | 2009-08-09 |  | 69 | 3 | 0 | 20 | 0 | JACKSON | JACKSON | 2006-03-23 | 2006-04-17 | N/A | 5551 | Y
Old Project | No Change | 09TPIT0038 | Ben Davis Sub: Replace 138 kV Breakers due to interrupting rating | Replace existing circuit breakers due to interrupting rating | On Schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T07005 | 2009-08-12 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 968
Old Project | Change in Service Date. Change from 6/1/2009 8/31/2009 | 09TPIT0107 | Rio Pecos, Add 2nd 138/69 kV Auto & reconfig 69 kV bus | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto | Schedule Update | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2232 | 2009-08-31 |  | 138 | 0 | 0 | 68 | 0 | PECOS
Old Project | No Change | 09TPIT0108 | Rio Pecos, Add SVC at Rio Pecos | Reconfigure Rio Pecos to add SVC and 2nd 138/69 kV auto |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2227 | 2009-08-31 |  | 69 | 0 | 0 | 0 | 90 | PECOS
Old Project | No Change | 09TPIT0069 | Rattlesnake Road 345 kV Switching Station | Construct 345 kV switching station to connect a new power plant. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R499-E | 2009-09-01 |  | 345 | 0 | 0 | 0 | 0 | MCLENNAN |  |  |  |  | 3397, 3398, 3399 | Y
Old Project | Change in Service Date. Change from 6/1/2009 9/1/2009 | 08TPIT0049 | Second Whitney 345/138 Autotransformer | Install second 450MVA 345/138KV auto at Whitney |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-09-01 |  | 345 | 0 | 0 | 450 | 0 | BOSQUE |  |  |  |  | 240, 241 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
Old Project | Change in Service Date. Change from 6/1/2009 9/1/2009 | 09TPIT0025 | Second Concord 345/138 Autotransformer | Install second 300MVA 345/138KV auto at Concord |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-09-01 |  | 345 | 0 | 0 | 300 | 0 | JOHNSON |  |  |  |  | 393, 394 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
Old Project | No Change | 05TPIT0069 | Waller-Prairie View-Seaway-Macedonia | Upgrade the 22.0-mile Waller(7272)-Macedonia(7671) 138-kV transmission line from 477 ACSR (159-MVA) to 959 ACSS (392-MVA). |  |  | SBEC | Billy Marricle (979) 865-3171 bmarricle@sbec.org | 1004653 | 2009-09-01 |  | 138 | 0 | 22 | 0 | 0 | WALLER | WALLER |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | Change in Service Date. Change from 6/1/2009 9/1/2009 | 07TPIT0251 | Victoria Power Plant: Install 1-28.8 MVAR 69 kV Cap Bank | Reconductor Victoria to Magruder, reconductor 69 kV line to 795 ACCC and Install 138/69 kV 187 MVA autotransformer at Magruder on the Victoria to Thomaston 138kV line | Cost and Schedule Update | AEP GROUP 389 | AEP/TCC | Dave Goetz 918-599-2653 | 2243 | 2009-09-01 |  | 69 | 0 | 0 | 0 | 28.8 | VICTORIA
Old Project | No Change | 05TPIT0117 | HiCross to Slaughter Lane 138kV circuit | Establish a new 138kV circuit from HiCross to Slaughter Lane substation | The project will be delayed from June 2009 to September 09 due to scheduling conflicts. |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P225 PLAN_117_P251 | 2009-09-09 |  | 138 | 2.2 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9147,9292,9267, 9075 | Y
Old Project | No Change | 09TPIT0135 | CSU Dowling Road Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2009-09-11 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS | [5 empty] | N
Old Project | No Change | 09TPIT0099 | Villa Cavazos, Convert 69 kV distribution substation to 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 3065 | 2009-09-30 |  | 138 | 0 | 0 | 0 | 0 | CAMERON
Old Project | No Change | 09TPIT0100 | La Palma to Military Highway 138kV line, cut-in Villa Cavazos at 138 kV | Convert Los Fresnos to 138 kV connecting to the La Palma to Loma Alta 138 kV line and convert Cavazos to 138 kV connecting to the La Palma to Military Highway 138 kV line |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 3071 | 2009-09-30 |  | 138 | 0.1 | 0 | 0 | 0 | CAMERON | CAMERON
Old Project | Change in Service Date. Change from 6/1/2009 9/30/2009 | 09TPIT0103 | Alamito Creek, add 2nd 138/69 kV auto | Add 2nd 138/69 kV autotransformer at Alamito Creek, and install a NaS Battery at Presidio | Schedule Update | AEP GROUP 358 | AEP/TNC | Brett Madison 918-599-2653 | 1178 | 2009-09-30 |  | 138 | 0 | 0 | 50 | 0 | PRESIDIO
Old Project | Change in Service Date. Change from 6/1/2009 10/1/2009 | 08TPIT0116 | CenterPoint Energy/TNMP Alvin interconnection | Build a new 345 kV, 3 breaker ring bus South Alvin substation looped into ckt.99 P.H. Robinson - Oasis. Add 345/138 kV autotransformer at new South Alvin substation interconnect with TNMP 138 kV North Alvin bus. |  | 07TPIT0161 | CNP, TNMP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2009-10-01 |  | 345 | 0.1 | 0 | 500 | 0 | BRAZORIA | BRAZORIA | 2006-07-25 | 2006-11-06 | 2007-01-16 | 43030 | Y | 1) Stakeholder question: We see that in the SSWG data set B cases for 2009 and beyond, one of the four 345/138 xfmrs at P.H. Robinson (A3) disappears. There seems no mention of this in the TPIT file. Can you please comment on why this 345/138 xmfr (A3) is removed? 2) CNP response July 24, 2008: The auto from PHR is currently planned to be moved to the new South Alvin interconnection we will have with TNMP, see 07TPIT0161 and 08TPIT0116. We have included the project in future base cases although we have yet to finalize all of the agreements with TNMP. | 1)_TNMP and CenterPoint Energy jointly studied project. 2)_No transmission circuits to be built, rebuilt or reconductored. 3) See Project #07TPIT0161 for reason for delay. 4) IDEV reflects change in project in-service date.
Old Project | No Change | 09TPIT0097 | Hunt Lane - New 138kV substation | Build a new two-terminal 138kV substation to replace Marbach. |  | T-0126 | CPS | S: Darrell Clifton PM:Hector Torres | S-0398 | 2009-10-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5295 | Y |  | There are no transformers associated with this project
Old Project | Change in Service Date. Change from 6/1/2009 10/1/2009 | 10TPIT0013 | Apollo to East Richardson | Rebuild existing Apollo to East Richardson 138kv line | TXUED to rebuild their portion of the line |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-10-01 |  | 138 | 0 | 1.4 | 0 | 0 | DALLAS | DALLAS |  |  |  | 8022690 | Y |  | mileage shown is for Bepc portion of line
Old Project | No Change | 08TPIT0042 | Seaton to Barclay Rebuild | Rebuild existing Seaton to Barclay with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-10-01 |  | 69 | 0 | 10.2 | 0 | 0 | BELL | FALLS |  |  |  | 69131 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | Change in Service Date. Change from 6/1/2009 10/15/2009 | 07TPIT0161 | Centerpoint Energy/TNMP Alvin Interconnection Project | Install 138 kV switching station on Alvin-Hastings transmission line and interconnect with Centerpoint 345-138 kV auto-transformer near Alvin. | Difficulties in acquistion of land of switching station site has delayed the project. | 08TPIT0116 | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | GCEC 27517, 27519 | 2009-10-15 |  | 138 | 0 | 0 | 0 | 0 | BRAZORIA | BRAZORIA | 2006-07-06 | 2006-11-06 | 2007-01-07 | 39015 | Y | Autotransformer for this project is being relocated from PH Robinson.
Old Project | No Change | 09TPIT0013 | Skyline - Install a Third 345kV Autotransformer | Install one 600 MVA autotransformer. |  |  | CPS | S: Darrell Clifton | S-0182 | 2009-11-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR | 2007-03-29 | 2007-04-20 | N/A | 5369 5370 5371 | Y |  | There is no transmission line additions associated with this project
Old Project | Change in Service Date. Change from 6/30/2009 11/1/2009 | 06TPIT0167 | MVEC Merett-MVEC Pharr | Rebuild 138kV line from Merett to MVEC Pharr Substations |  | 06TPIT0166 | MVEC | Loretta C. Gallaga (956) 514-1289 lgallaga@stec.org | 984505 | 2009-11-01 |  | 138 | 0 | 1.8 | 0 | 0 | HIDALGO | HIDALGO
Old Project | No Change | 06TPIT0080 | Medina Lake-CPS (Part 1) | Construct a new 138-kV 795 ACSR transmission line (approximately 20 miles in length) from the BEC Medina Lake substation (7432) to the future CPS Energy Talley Road substation (5422), then continuing on to the CPS Energy Texas Research Park substation (5430). |  | 07TPIT0034 CPS S-0275 | CPS / LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org PM:Hector Torres (210) 353-2404 HVTorres@cpsenergy.com | CPS T-0049 | 2009-11-01 |  | 138 | 20.7 | 0 | 0 | 0 | BANDERA | BEXAR | 2007-10-03 | 2007-11-03 |  | 5430 7432 | Y |  | CPS and LCRA have filed update letter with ERCOT. BEC is proposing a new load serving substation between Medina Lake and CPS.
Old Project | No Change | 05TPIT0072 | Mountain Top-Blanco-Devil's Hill | Close the 69-kV switch (SW 458) at the Blanco substation(7482) to loop the load located at the Blanco substation. Upgrade the capacity of the 138-69-kV auto-transformer (T2) at the Devil’s Hill substation(7493) from 20-MVA to 45-MVA. | Customer Coordination |  | PEC | Darrel Mitchell (830) 868-7155 Darrel.Mitchell@PECI.com | 1005443 | 2009-11-30 |  | 138 | 0 | 0 | 45 | 0 | BLANCO | COMAL |  |  |  | SEE PROJECT DESCRIPTION | Y
New Project | New Project | 09TPIT0176 | Bertram-Andice | Close the normally open Bertram (7520)-Andice(7521) 69 kV transmission line. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2009-11-30 |  | 69 | 0 | 0 | 0 | 0 | BURNET | WILLIAMSON |  |  |  | SEE PROJECT DESCRIPTION | Y | This project is included with the Lago Vista-Nameless project.
Old Project | No Change | 07TPIT0253 | West Childress to Childress 20th St: Rebuild Dbl Ckt 138/69 kV Line | Rebuild Dbl Crkt 138/69 Line and purch R/W from West Chilldress to Childress 20th Street to Connect BEC's Henry Substation | Cost Update | AEP GROUP 403 | AEP/BEC | John Pulay 918-599-2653 | 2279 | 2009-11-30 |  | 69 | 1 | 0 | 0 | 0 | CHILDRESS | CHILDRESS
Old Project | No Change | 06TPIT0010 | W. Levee - Norwood 345 kV line | Construct W. Levee - Norwood 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M477-WAC | 2009-12-01 |  | 345 | 6.5 | 0 | 0 | 0 | DALLAS | DALLAS | 2003-10-01 | 2004-02-01 | 2004-04-01 | 2398, 2406 | Y
Old Project | No Change | 08TPIT0086 | Exeter - New 138kV Substation | Construct new 138kV substation to replace Terrell Hills substation | Location has been defined. Project to be awarded to Design Build Contractor end of July 08. | T-0088 | CPS | PM: Ulrich Skerhut | S-0230 | 2009-12-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5143 | Y |  | There are no transformers associated with this project
Old Project | No Change | 09TPIT0137 | Hill Country - 138kV Capacitor Bank Addition | Remove one existing back-to-back 50.4MVAR capacitor bank at Harmony Hills and relocate to the 138kV Hill Country bus |  |  | CPS | Blake Williams |  | 2009-12-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5209 | Y |  | There are no transmission line additions associated with this project There are no transformers associated with this project
Old Project | Change in Service Date. Change from 6/30/2009 12/1/2009 | 08TPIT0172 | Gunsight 138 kV Switching Station | Construct new switching station to connect a new wind farm | Wind farm changed schedule. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R829-E | 2009-12-01 |  | 138 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | Y
Old Project | Change in Service Date. Change from 6/30/2009 12/1/2009 | 06TPIT0043 | Sherry - Liggett 138 kV line & Liggett - International Airport 138 kV line | Upgrade 138 kV line | Construction schedule change |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5042-E | 2009-12-01 |  | 138 | 0 | 13 | 0 | 0 | TARRANT | DALLAS |  |  |  | 1920, 2140, 1922, 2124, 2128, 2133, 2137 | Y
Old Project | No Change | 07TPIT0070 | Taylor - Taylor West - Hutto Switch 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R457-E | 2009-12-01 |  | 138 | 0 | 10.07 | 0 | 0 | WILLIAMSON | WILLIAMSON |  | 2007-08-01 | N/A | 3666, 3673, 3658 | Y
Old Project | No Change | 07TPIT0115 | Elgin Switch - Taylor 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R026-E | 2009-12-01 |  | 138 | 0 | 11.4 | 0 | 0 | BASTROP | BASTROP |  |  |  | 3650, 3658 | Y
Old Project | No Change | 07TPIT0238 | Krum Tap 138 kV Switching Station and Krum Tap - Krum - Allison - Decatur 138 kV line | Construct 138 kV switching station and convert 69 kV line to 138 kV operation |  | R510B & R511 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R510A-E | 2009-12-01 |  | 138 | 0 | 19 | 0 | 0 | DENTON | WISE | 2008-01-14 | 2008-05-19 | N/A | 1582, 1568, 1987, 1990, 1986 | Y |  | Krum - Allison section will be completed in 12/2008.
Old Project | No Change | 09TPIT0049 | Roanoke Switch - Roanoke West - Southlake 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5118-E | 2009-12-01 |  | 138 | 0 | 7.1 | 0 | 0 | DENTON | DENTON |  |  |  | 1852, 2018, 2020 | Y
Old Project | Change in Service Date. Change from 7/10/2009 12/1/2009 | 08TPIT0085 | Palo Duro Switching Station | Construct a new Palo Duro substation in the MEC 138 kV transmission line, from Pearsall to Batesville, at the point where the line changes from a north/south direction to an east/west direction, to tie-in new 138 kV transmission line to AEP Dilley. | Negotiation of site is in progress. |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2009-12-01 |  | 138 | 0 | 0 | 0 | 0 | FRIO | FRIO | 2006-02-01 | 2006-06-29 |  | 5866 | Y
Old Project | Change in Service Date. Change from 7/31/2009 12/1/2009 | 08TPIT0094 | Palo Duro to Dilley SS 138 kV Line | Construct 9 miles 795 ACSR 138 kV line from Palo Duro to Dilley | Changed responsibility to STEC |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2009-12-01 |  | 138 | 9 | 0 | 0 | 0 | FRIO | FRIO |  |  |  | 5866 | Y
Old Project | No Change | 09TPIT0106 | Perry Auto | Increase 138/69 autotransformer capacity at Perry |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-12-01 |  | 138 | 0 | 0 | 100 | 0 | FALLS |  |  |  |  | 91,92 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
Old Project | No Change | 05TPIT0187 | Verdi 69 kV Substation | Construct a 12 mile radial 69 kV tap-line from the STEC Pleasanton 69 kV substation to the new substation at Verdi. | Delay for SAWS |  | STEC | Dung Nguyen, 361-485-6142, dnguyen@stec.org |  | 2009-12-01 |  | 69 | 12 | 0 | 10 | 0 | ATASCOSA | WILSON | 2004-08-01 | 2004-09-01 |  | 5723 | N
Old Project | Change in Service Date. Change from 8/9/2009 12/30/2009 | 09TPIT0098 | Dilley, add 138 kV terminal | Construct 9 miles 795 ACSR 138 kV line from Palo Duro to Dilley | Changed In-Service Date | AEP GROUP 382 | AEP/TCC | Paul Hassink 918-599-2653 | 3098 | 2009-12-30 |  | 138 | 0 | 0 | 0 | 0 | FRIO | FRIO
Old Project | Change in Service Date. Change from 8/12/2009 12/31/2009 | 10TPIT0002 | Lobo, build 345 kV for 675MVA autotransformer | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | Cost and Schedule Update | AEP GROUP 216 | AEP/TCC | Bill Eakin 918-599-2653 | 1720 | 2009-12-31 |  | 345 | 0 | 0 | 675 | 0 | WEBB
Old Project | No Change | 07TPIT0151 | Yellowjacket, New 138/69 Station | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2138 | 2009-12-31 |  | 138 | 0 | 0 | 90 | 28.8 | MENARD
Old Project | No Change | 07TPIT0153 | Yellowjacket, Add 2nd 69/138 kV Auto | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank, |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2123 | 2009-12-31 |  | 138 | 0 | 0 | 90 | 0 | MENARD
Old Project | No Change | 08TPIT0135 | Yellowjacket, Install 150 MVA Phase Shifting Transformer | Yellowjacket, Install 150 MVA 138 kV Phase Shifting Transformer on the SAPS 138 kV line |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2219 | 2009-12-31 |  | 138 | 0 | 0 | 150 | 0 | MENARD
Old Project | No Change | 08TPIT0146 | Santa Anna, Add Phase Shifting Transformer | Add 138 kV Phase Shifting Transformer on the Santa Anna to Brownwood 138 kV line at Santa Anna |  | AEP GROUP 391 | AEP/TNC | Ashley Beasley 918-599-2653 | 2269 | 2009-12-31 |  | 138 | 0 | 0 | 150 | 0 | COLEMAN
Old Project | No Change | 09TPIT0110 | Nicole to Red Creek, Build 138 kV line | Provide inteconnection at new Nicole substation and rebuild the Red Creek to Nicole 138kV line with 2X795 ACSS |  | AEP GROUP 390 | AEP/TNC | Ashley Beasley 918-599-2653 | 3114 | 2009-12-31 |  | 138 | 0 | 38 | 0 | 0 | COKE | TOM GREEN
Old Project | No Change | 09TPIT0114 | San Angelo Power Station, Reconfigure Station | San Angleo Power Station, Reconfigure Station to separate wind from load circuits |  | AEP GROUP 429 | AEP/TNC | Paul Hassink 918-599-2653 |  | 2009-12-31 |  | 138 | 0 | 0 | 0 | 0 | TOM GREEN
Old Project | No Change | 09TPIT0127 | Menard to San Angelo Power Station 138 kV Hairpin into Yellowjacket | Yellowjacket, Build new 138 kV Switch Station Station: Five postion ring with 2-90 MVA Auto 138/69 (LTC), 138 KV 28.8 MVAR Capacitor and 1- 10 MVA distribution bank |  | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2154 | 2009-12-31 |  | 138 | 2 | 0 | 0 | 0 | MENARD | TOM GREEN
Old Project | No Change | 09TPIT0129 | Paducah 69/138 kV Station, Replace the existing 69/138 kV auto | Replace 69/138 kV auto at Paducah with an 90 MVA 69/138 kV with LTC and add 20 MVAR 138 kV shunt reactor |  | AEP GROUP 289 | AEP/TNC | Brett Madison 918-599-2653 | 1436 | 2009-12-31 |  | 138 | 0 | 0 | 90 | 0 | COTTLE
Old Project | No Change | 08TPIT0067 | Fort Worth Substation | Construct new 25MVA, 138kV to 13.2kV substation adjacent to TMPA's 138kV transmission line where it intersects US377 | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600821 | 2009-12-31 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 919 | Y
Old Project | Change in Service Date. Change from 10/1/2009 12/31/2009 | 05TPIT0026 | Wynn Joyce-Miller 69 kV line | Line upgrade | FUNDED |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2009-12-31 |  | 69 | 0 | 3 | 0 | 0 | DALLAS |  |  |  |  | 811, 824 | Y |  | This project is a line rebuild to relieve overload and serve loads at Wynn Joyce and Miller
Old Project | No Change | 10TPIT0042 | Ables Springs 138 kV line and point of interconnection (Oncor Electric Delivery portion only) | Construct 138 kV line and point of interconnection |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3055-E | 2010-01-01 |  | 138 | 15.67 | 4.97 | 0 | 0 | KAUFMAN | HUNT | 2007-01-05 | 2007-05-01 | N/A |  | N
Old Project | Change in Service Date. Change from 11/1/2009 1/1/2010 | 06TPIT0112 | Lakeway second circuit from LCRA tap to the substation. | Construct a mile long 138kV circuit from the Lakeway substation to the LCRA tap between Marshall Ford and LCRA's Bee Creek substation. |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | 3230_117_4255 | 2010-01-01 |  | 138 | 1 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 7349, 9235 | Y
Old Project | No Change | 09TPIT0018 | Reagor Springs to India Rebuild/Upgrade | Upgrade/rebuild existing Reagor Springs. to India line | SCOPE UPDATED |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-02-01 |  | 69 | 0 | 11.5 | 0 | 0 | ELLIS | ELLIS |  |  |  |  | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | Change in Service Date. Change from 11/30/2009 3/1/2010 | 07TPIT0097 | Reconstruct 1.2 miles - Hickory to North Lakes 69kV Transmission Line | Reconstruct 1.2 miles of existing 69V transmission line | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600775 | 2010-03-01 |  | 69 | 0 | 1.2 | 0 | 0 | DENTON | DENTON |  |  | NA | 910, 915 | Y
Old Project | Change in Service Date. Change from 11/30/2009 4/1/2010 | 07TPIT0248 | San Miguel 345 kV line terminal for San Miguel to Rio Lobo 345 kV line | Breakers, bus, relaying for San Miguel to Lobo 345 kV line termination | Previous 2007 date entry was a typo. Work is planned for 2009. Changed responsibility to STEC and AEP |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2010-04-01 |  | 345 | 0 | 0 | 0 | 0 | ATASCOSA |  |  |  |  | 5901 | Y
New Project | New Project | 10TPIT0075 | San Miguel 345 kV line | Construct a 110 mile 345kV line from San Miguel to Rio Lobo. Joint project with AEP. STEC portion 44 miles | Previous 2007 date entry was a typo. Work is planned for 2009. Changed responsibility to STEC and AEP |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2010-04-01 |  | 345 | 44 | 0 | 0 | 0 | ATASCOSA | WEBB |  |  |  | 5901 | Y
Old Project | Change in Service Date. Change from 12/1/2009 4/1/2010 | 09TPIT0003 | Lobo to San Miguel, build 345 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and con |  | AEP GROUP 216 | AEP/STEC | Bill Eakin 918-599-2653 | 633 | 2010-04-01 |  | 345 | 110 | 0 | 0 | 0 | WEBB | ATASCOSA
Old Project | No Change | 11TPIT0025 | Anderson to Westover Hills - New 138kV Transmission Line | Build new 138kV line to Westover Hills |  | S-0328 | CPS | T: LeeRoy Perez S: Darrell Clifton | T-0200 | 2010-04-01 |  | 138 | 2 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5003 5488 | Y |  | There are no transformers associated with this project
Old Project | Change in Service Date. Change from 12/1/2009 4/1/2010 | 06TPIT0057 | Magruder: Add 138/69 kV Auto, 1-14.4 MVAR 69 kV Cap Bank | Reconductor Victoria to Magruder, reconductor 69 kV line to 795 ACCC and Install 138/69 kV 187 MVA autotransformer at Magruder on the Victoria to Thomaston 138kV line | Cost and Schedule Update | AEP GROUP 389 | AEP/TCC | Dave Goetz 918-599-2653 | 209 | 2010-04-01 |  | 138 | 0 | 0 | 187 | 14.4 | VICTORIA
Old Project | Change in Service Date. Change from 12/1/2009 4/1/2010 | 10TPIT0069 | Thomaston: Install 138 kV PST | Interconnect new generation at the Victoria substation, install a phase shifting transformer at Thomaston substation, and rebuild Magruder to North Victoria 69 kV Line | Schedule Update | AEP GROUP 402 | AEP/TCC | Dave Goetz 918-599-2653 | 2294 | 2010-04-01 |  | 138 | 0 | 0 | 180 | 0 | DEWITT
Old Project | No Change | 10TPIT0055 | Eagle Mountain 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5141-E | 2010-05-01 |  | 345 | 0 | 0 | 517 | 0 | TARRANT |  | 2007-12-31 | 2008-02-26 | N/A |  | Y
Old Project | Change in Service Date. Change from 12/1/2009 5/1/2010 | 07TPIT7777 | MVEC Pharr-Alberta Switch | Rebuild 138kV line from Pharr to Alberta Switch Substations |  | 06TPIT0166 | MVEC | Loretta C. Gallaga (956) 514-1289 lgallaga@stec.org |  | 2010-05-01 |  | 138 | 0 | 1.9 | 0 | 0 | HIDALGO | HIDALGO
Old Project | Change in Service Date. Change from 12/1/2009 5/1/2010 | 09TPIT0120 | Sun Switch - Golden - Sacroc 138 kV line | Rebuild 138 kV line | Change in relative priority and/or resource limitations |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R807-E | 2010-05-01 |  | 138 | 0 | 12.8 | 0 | 0 | SCURRY | SCURRY |  |  |  |  | Y
Old Project | No Change | 06TPIT0087 | Coppell Tap - McKamy Tap 138 kV line | Upgrade existing138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5001-E | 2010-05-01 |  | 138 | 0 | 1.35 | 0 | 0 | TARRANT | TARRANT |  |  |  | 2014, 2025 | Y
Old Project | No Change | 07TPIT0017 | Handley - Hurst 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M572-E | 2010-05-01 |  | 138 | 0 | 18.7 | 0 | 0 | TARRANT | TARRANT |  |  |  | 1950, 2110, 2109, 1951 | Y
Old Project | No Change | 08TPIT0104 | Elgin Switching Station - Elgin 69 kV line conversion to 138 kV | Rebuild existing 69 kV line and convert to 138 kV operation |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R471-E | 2010-05-01 |  | 138 | 0 | 5.9 | 0 | 0 | WILLIAMSON | BASTROP |  |  |  | 3655, 3650 | Y
Old Project | No Change | 08TPIT0105 | Forest Grove - Eustace 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R390-E | 2010-05-01 |  | 138 | 0 | 0.74 | 0 | 0 | HENDERSON | HENDERSON |  |  |  | 3177, 3178, 3172, 3131 | Y
Old Project | No Change | 09TPIT0045 | Lake Creek - Robinson 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R476-E | 2010-05-01 |  | 138 | 0 | 8.3 | 0 | 0 | MCLENNAN | MCLENNAN |  |  |  | 3410, 3597 | Y
Old Project | No Change | 10TPIT0033 | Eustace - Mabank 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R391-E | 2010-05-01 |  | 138 | 0 | 7.1 | 0 | 0 | HENDERSON | HENDERSON |  |  |  | 3176, 3177 | Y
Old Project | No Change | 10TPIT0040 | Temple Switch - Bell County 138 kV line | Upgrade existing 138 kV line |  | R494 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R704A-E | 2010-05-01 |  | 138 | 0 | 8.2 | 0 | 0 | WILLIAMSON | WILLIAMSON | 2006-11-01 |  | 2007-07-01 | 3666, 3673, 3658 | Y
Old Project | No Change | 10TPIT0053 | Kaufman South 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3064-E | 2010-05-01 |  | 138 | 0 | 0 | 0 | 55.2 | KAUFMAN | [5 empty] | Y
Old Project | No Change | 10TPIT0054 | Royse 138/69 kV autotransformer | Install larger autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3065-E | 2010-05-01 |  | 138 | 0 | 0 | 120 | 0 | ROCKWALL | [5 empty] | Y
Old Project | No Change | 10TPIT0056 | Renner SVC | Install dynamic reactive device (+300 Mvar/-265 Mvar) |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4058-E | 2010-05-01 |  | 138 | 0 | 0 | 0 | 300 | DALLAS |  | 2008-05-01 |  |  |  | N
Old Project | No Change | 07TPIT0034 | Medina Lake-Pipe Creek Rebuild (formally (Medina Lake-CPS Cagnon (Part 2)) | Rebuild and upgrade the 7.8 mile Pipe Creek (7437) - Medina Lake (7432) 1/0 ACSR 69kV transmission line to 795 ACSR 138kV. |  | 06TPIT0080 | Bandera Electric | Brian D. Bartos (830) 796-6074 b.bartos@banderaelectric.com | 57596 | 2010-05-01 |  | 138 | 0 | 7.8 | 0 | 0 | BANDERA | BANDERA | 2003-10-01 | 2003-11-01 |  | See Project Description | Y |  | This project was formally known as Medina Lake - CPS Cagnon (Part 2). Submissions to ERCOT RPG for review where concurrent with Medina Lake - CPS Cagnon (Part 1)
Old Project | No Change | 10TPIT0026 | Mueller 138kV substation | Establish a new 138kV Mueller substation with (2) 30MVA transformers. The substation will cut into existing Ckt 938 (Kingsbery to Wheless Lane). |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | 3230_117_2793 3240_117_4793 3230_117_4229 | 2010-05-01 |  | 138 | 1 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  | 9342 | Y
Old Project | Change in Service Date. Change from 12/31/2009 5/1/2010 | 09TPIT0133 | Jim Christal Substation 138kV Reconstruction | Reconstruct 138kV section of the station installing five 138kV circuit breakers to break the Denton West to Denton North transmission line into two sections | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602153 | 2010-05-01 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 919 | Y
Old Project | No Change | 05TPIT0040 | Fairview to Aledo | Construct 138kv 795 line from Fairview to Aledo, rebuild Waples to Fairview radial |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-05-01 |  | 138 | 32 | 5.8 | 0 | 0 | HOOD | PARKER |  | 2002-09-01 | 2003-01-01 | 467470527 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | Change in Service Date. Change from 12/31/2009 5/1/2010 | 09TPIT0116 | Gatesville Tap - Gatesville TDC 69 kV line | Upgrade existing 69 kV line | Change in relative priority and/or resource limitations |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R497-E | 2010-05-01 |  | 69 | 0 | 4.4 | 0 | 0 | MCLENNAN | CORYELL |  |  |  |  | Y
Old Project | No Change | 07TPIT0116 | Handley - Duval 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5116-E | 2010-05-01 |  | 69 | 0 | 5.4 | 0 | 0 | TARRANT | TARRANT |  |  |  | 1952, 2158 | Y
Old Project | No Change | 09TPIT0115 | Laguna Vista 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R544-E | 2010-05-01 |  | 69 | 0 | 0 | 0 | 9.2 | PARKER | [5 empty] | Y
Old Project | Change in Service Date. Change from 12/31/2009 5/1/2010 | 07TPIT0157 | West Pleasanton Substation | Hairpin a 69/12.5 kV substation into the Pleasanton to Poteet 69 kV line. Construct 2.5 miles of double circuit 69 kV transmission line. | Project delayed by property acquisition. |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2010-05-01 |  | 69 | 2.5 | 0 | 10 | 0 | ATASCOSA | ATASCOSA |  |  |  | 5715 | Y
Old Project | No Change | 10TPIT0015 | West Denton- NW Carrollton New 345 line (W.D. to Tap) | Additional 345 KV circuit from West Denton to N.W Carrollton | Delayed due to original requirements have changed per Chuck Sears - Denton |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org |  | 2010-05-07 |  | 345 | 0 | 9 | 0 | 0 | DENTON | DENTON |  |  |  | 986 | Y
Old Project | No Change | 10TPIT0016 | West Denton Sub: 345 Terminal for W. Krum line | Provide terminal for 345 line from West Krum | Delayed due to original requirements have changed |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org |  | 2010-05-07 |  | 345 | 0 | 0 | 0 | 0 | DENTON |  |  |  |  | 986 | Y
Old Project | No Change | 09TPIT0086 | Rothwood 345/138 kV substation | Build a new 345/138 kV Rothwood substation. Loop ckt.74 Kuykendahl to King and 138 kV ckt.66 Rayford tap section into the new substation. Add one 800 MVA 345/138 kV autotransformer at Rothwood substation. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2010-05-31 |  | 345 | 0.4 | 0 | 800 | 0 | HARRIS | HARRIS | 2008-03-27 | N/A | 2008-05-20 | 46290, 46295 | Y |  | Added as part of 2007 ERCOT 5 year plan projects.
Old Project | No Change | 09TPIT0084 | Tomball - Rothwood - Rayford ckt.66 | Upgrade 138 kV ckt.66 Tomball - Rothwood to increase thermal ratings |  | 09TPIT0086 | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2010-05-31 |  | 138 | 0 | 13 | 0 | 0 | HARRIS | MONTGOMERY | 2008-03-26 | 2008-04-14 | 2008-05-20 | 46510, 46295, 46261 | Y |  | Added as part of 2007 ERCOT 5 year plan projects.
Old Project | No Change | 09TPIT0085 | Convert Rayford 138 kV substation. | Convert Rayford from a double tap substation to a loop tap configuration substation. |  | 09TPIT0086 | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2010-05-31 |  | 138 | 0 | 0 | 0 | 0 | MONTGOMERY | MONTGOMERY | 2008-03-26 | 2008-04-14 | 2008-05-20 | 46261, 46262 | Y |  | Added as part of 2007 ERCOT 5 year plan projects.
New Project | New Project | 10TPIT0071 | Rayford - Louetta ckt.66 | Upgrade 138 kV ckt.66 Rayford - Louetta to increase thermal ratings |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2010-05-31 |  | 138 | 0 | 9.14 | 0 | 0 | MONTGOMERY | HARRIS |  |  |  | 46261, 46051 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
Old Project | No Change | 11TPIT0016 | Plastipak-Shiloh 138 kV line and Shiloh 138kV substation rebuild | Line upgrade and substation rebuild | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2010-05-31 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  |  |  |  | 808, 830 | Y |  | This project is a line upgrade and substation rebuild for serving new load at Plastipak
Old Project | No Change | 09TPIT0132 | Bonnie Brae Substation | Construct new 50MVA, 69kV to 13.2kV substation adjacent to DME's 69kV Hickory to North Lakes transmission line 1/4 mile south of US 380 | On schedule | 07TPIT0097 | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 602099 | 2010-05-31 |  | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 905 | Y
Old Project | Change in Service Date. Change from 3/31/2010 6/1/2010 | 10TPIT0041 | Temple Switch - Salado Switch 345 kV line | Upgrade existing 345 kV line |  | R494 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R705-E | 2010-06-01 |  | 345 | 0 | 15.2 | 0 | 0 | BELL | BELL | 2006-11-01 |  | 2007-07-01 | 3414, 3699 | N
Old Project | No Change | 08TPIT0003 | Hutto Switch - Salado Switch 345 kV line | Construct Hutto Switch - Salado Switch 345 kV line and Salado 345 kV Switching Station |  | R456 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R445-E | 2010-06-01 |  | 345 | 63 | 0 | 0 | 0 | WILLIAMSON | BELL |  |  | 2004-12-18 | 3699, 3696 | Y
Old Project | No Change | 10TPIT0008 | Hutto Switch and 345/138 kV autotransformer | Create 345 kV switching station and install a 345/138 kV autotransformer |  | R445 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R456-E | 2010-06-01 |  | 345 | 0 | 0 | 600 | 0 | WILLIAMSON |  |  |  | 2004-12-18 | 3696, 3666 | Y
New Project | New Project | 10TPIT0081 | Hasse Auto | Increase Hasse Auto to 100MVA |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 138 | 0 | 0 | 100 | 0 | COMANCHE |  |  |  |  | 1649277 | N
Old Project | No Change | 10TPIT0044 | Marbach substation removal - Reconfigure 138kV lines at Marbach and Cagnon | Reroute the 138kV lines at Marbach and Cagnon. Due to removal of the Marbach substation. |  | S-0401 | CPS | T: Aaron Finley PM:Hector Torres | T-0129 | 2010-06-01 |  | 138 | 0.3 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5295 | Y |  | There are no transformers associated with this project
Old Project | No Change | 10TPIT0045 | Mauermann Rd - New 138kV Substation | Loop new 138kV substation into the existing existing VH Braunig to Toyota line |  | T-0087 | CPS | S: Darrell Clifton PM:Hector Torres | S-0399 | 2010-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5421 | Y |  | There are no transformers associated with this project
Old Project | No Change | 10TPIT0066 | Rackspace - New 138kV Substation | Loop new 138kV substation into the existing 138kV Fratt to Kirby line |  |  | CPS | Blake Williams |  | 2010-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5357 | Y |  | There are no transformers associated with this project
Old Project | No Change | 10TPIT0067 | Holbrook - New 138kV Substation | Loop new 138kV substation into the existing 138kV Fort Sam to Kirby line |  |  | CPS | Blake Williams |  | 2010-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5218 | Y |  | There are no transformers associated with this project
Old Project | No Change | 10TPIT0068 | Broadview to Fredericksburg Rd - 138kV line upgrade | Upgrade the existing Broadview to Fredericksburg Rd 138kV transmission line |  |  | CPS | Blake Williams |  | 2010-06-01 |  | 138 | 0 | 2.3 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5040 5170 | Y |  | There are no transformers associated with this project
Old Project | No Change | 08TPIT0009 | Hutto Switch - Round Rock NE/Round Rock 138 kV line | Upgrade existing138 kV line and add a second circuit to existing structures |  | R456 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R406-E | 2010-06-01 |  | 138 | 8.6 | 5.5 | 0 | 0 | WILLIAMSON | WILLIAMSON |  |  |  | 3666, 3670 | Y
Old Project | No Change | 10TPIT0062 | Weil Road - New Subsation | Build a 138-26.18 kV 22.4 MVA substation on the GVEC Marion(7178)-Cibolo(7608) 138 kV transmission line near the Marion Interchange |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2010-06-01 |  | 138 | 0 | 0 | 22.4 | 0 | GUADALUPE |  |  |  |  | See Project Title | N
Old Project | No Change | 10TPIT0063 | McQueeney(7605)-Geronimo(7604) 138 kV Line rebuild | Rebuild the existing 69-kV 4/0 transmission line to 138-kV 795 MCM between Geronimo and McQueeney substations on existing right-of-way |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2010-06-01 |  | 138 | 0 | 5.5 | 0 | 0 | GUADALUPE | GUADALUPE |  |  |  | See Project Title | Y
Old Project | No Change | 10TPIT0064 | Parkway(7611) - Shertz(7610) Transmission Line | Build a new 138-kV 795 MCM transmission line on common structures with the existing Parkway-Schertz 138-kV line |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2010-06-01 |  | 138 | 2.8 | 0 | 0 | 0 | GUADALUPE | GUADALUPE |  |  |  | See Project Title | Y
Old Project | No Change | 10TPIT0024 | Stoney Ridge 138kV substation (original title is Linda Vista substation) | Establish new 138kV Stoney Ridge substation and install (2) 30MVA transformers. The substation will cut into Ckt 962 (Garfield to Onion Creek). |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P224 PLAN_117_P230 | 2010-06-01 |  | 138 | 0.1 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  | 9236 | Y
Old Project | No Change | 09TPIT0102 | El Campo: Add 138 kV Terminal | Addition 138/69 kV substation at Sierra Verde and conversion El Campo to Sierra Verde 69 kV line to 138 kV with 795 ACSR conductor |  | AEP GROUP 063 | AEP/TCC | Paul Hassink 918-599-2653 | 3117 | 2010-06-01 |  | 138 | 0 | 0 | 0 | 0 | WHARTON
Old Project | Change in Service Date. Change from 5/1/2010 6/1/2010 | 08TPIT0131 | Melon Creek: Install 138/69 KV Auto | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV 50 MVA auto and build new 69 kV line from Melon Creek to Tatton | Cost Update | AEP GROUP 100 | AEP/TCC | Paul Hassink 918-599-2653 | 2021 | 2010-06-01 |  | 138 | 0 | 0 | 50 | 0 | REFUGIO
Old Project | No Change | 10TPIT0029 | Robertson to Watson Chapel Rebuild | Rebuild existing Robertson to Watson Chapel 138kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 138 | 0 | 21.6 | 0 | 0 | ROBERTSON | LEON |  |  |  | 32,33 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
New Project | New Project | 10TPIT0076 | Stephenville to Granbury 138KV Conversion | Convert exisitng Stephenville to Granbury 69KV line to 138KV operation |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 138 | 0 | 0 | 0 | 0 | Hood | Erath |  |  |  | 306295 | N
Old Project | No Change | 10TPIT0070 | Magruder to North Victoria: Rebuild 69 kV Line | Interconnect new generation at the Victoria substation, install a phase shifting transformer at Thomaston substation, and rebuild Magruder to North Victoria 69 kV Line |  | AEP GROUP 402 | AEP/TCC | Dave Goetz 918-599-2653 | 3261 | 2010-06-01 |  | 69 | 0 | 3.7 | 0 | 0 | VICTORIA | VICTORIA
Old Project | No Change | 09TPIT0030 | Acton to Nassau Bay Switch Rerate/Rebuild | Rerate/Rebuild existing Acton to Nassau Bay Switch 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 69 | 0 | 3 | 0 | 0 | HOOD | HOOD |  |  |  | 373451 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | No Change | 10TPIT0011 | Olney to Lake Kemp Switch Rebuild | Rebuild exisitng Olney to Lake Kemp Switch 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 69 | 0 | 29 | 0 | 0 | YOUNG | BAYLOR |  |  |  | 788781784782 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
New Project | New Project | 10TPIT0077 | Hamilton to Pancake Rebuild | Rebuild Hamilton to Pancake with 795ACSR, 138KV |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 69 | 0 | 21.9 | 0 | 0 | Hamilton | Coryell |  |  |  | 158258 | N
New Project | New Project | 10TPIT0078 | Granbury to Glen Rose Rebuild | Rebuild Granbury to Geln Rose with 959ACSS |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 69 | 0 | 14.2 | 0 | 0 | Hood | Somervell |  |  |  | 315307 | N
New Project | New Project | 10TPIT0079 | Morris Sheppard to Oran Rebuild | Rebuild Morris Sheppard to Oran with 959ACSS |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 69 | 0 | 18.4 | 0 | 0 | Palo Pinto | Palo Pinto |  |  |  | 343785 | N
New Project | New Project | 10TPIT0080 | Olney to South Bend Switch Rebuild | Rebuild Olney to South Bend Switch with 959ACSS |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 69 | 0 | 24 | 0 | 0 | Young | Young |  |  |  | 788795 | N
New Project | New Project | 10TPIT0082 | Carlton Switch to Mountary Rebuild | Rebuild Carlton Switch to Mountary with 959ACSS |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 |  | 69 | 0 | 9.6 | 0 | 0 | Erath | Comanche |  |  |  | 297294 | N
Old Project | No Change | 05TPIT0172 | Jones to Dansby 138, New line construction | Build a 795 ACSR 138 kV line | Increased load in the area | 07TPIT0030 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 802 | 2010-06-11 |  | 138 | 9 | 0 | 0 | 0 | BRAZOS | BRAZOS |  |  |  | 32897, 32863 | N |  | There were no new transformers added with this project.
Old Project | No Change | 10TPIT0065 | Dansby Substation | Install (1) Breaker in existing ring bus for a 138 lines from Jones Rd Substation |  | 11TIPIT0030 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2010-06-11 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS |  |  |  |  | 32897 | N
Old Project | No Change | 11TPIT0030 | Jones Road Substation | Install (3) Breaker ring to include (2) 138 lines and (1) 138/12.5 transformer |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2010-06-11 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS | [5 empty] | N
Old Project | No Change | 10TPIT0058 | Lytton Springs Autotransformer Addition | Add a new 345-138 kV 478 MVA autotransformer at the Lytton Springs substation (9074). Terminate the Mendoza (7325) - Turnersville (7500) 138 kV transmission line (T-382) into the Lytton Springs substation 138 kV bus (9075), creating the new Turnersville (7500) - Lytton Springs (9075) and Mendoza (7325) - Lytton Springs (9075) 138 kV transmission lines. Upgrade the new Turnersville (7500) - Lytton Springs (9075) 138 kV transmission line from 795 ACSR (220MVA) to 1433 ACSS/TW (507 MVA). Upgrade the new Mendoza (7325) - Lytton Springs (9075) 138 kV transmission line from 795 ACSR (220 MVA) to bundled 795 ACSR (440 MVA). |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2010-06-30 |  | 345 | 0 | 7 | 478 | 0 | CALDWELL |  |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | No Change | 05TPIT0065 | Highway 32-Wimberley | Construct a new 795 ACSR (220-MVA) 138-kV double circuit transmission line (approximately four miles) between the Highway 32(7546) and Wimberley(7496) substations. |  |  | PEC | Darrel Mitchell (830) 868-7155 Darrel.Mitchell@PECI.com |  | 2010-06-30 |  | 138 | 4 | 0 | 0 | 0 | HAYS |  |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | Change in Service Date. Change from 6/1/2010 6/30/2010 | 05TPIT0068 | Marshall Ford-Buttercup | Upgrade the 9.8-mile Marshall Ford(7356)-Buttercup(7531) 795 ACSR (220-MVA) 138-kV transmission line to bundled 795 ACSR (440MVA). |  |  | PEC | Darrel Mitchell (830) 868-7155 Darrel.Mitchell@PECI.com |  | 2010-06-30 |  | 138 | 0 | 9.8 | 0 | 0 | TRAVIS | WILLIAMSON |  |  |  | SEE PROJECT DESCRIPTION | Y
Old Project | No Change | 06TPIT0077 | Rim Rock-Goat Creek | Construct a new 336 ACSR 138 kV transmission line (approximately 7.5 miles) between the existing Rim Rock substation (7143) and a new 138 kV switching substation (Goat Creek)(7141). |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 1002912 | 2010-06-30 |  | 138 | 7.5 | 0 | 0 | 0 | KERR |  | 2005-09-01 | 2205-09-01 |  | SEE PROJECT DESCRIPTION | Y
Old Project | No Change | 07TPIT0039 | El Campo to Sierra Verde, upgrade 69 kV line | Addition 138/69 kV substation at Sierra Verde and conversion El Campo to Sierra Verde 69 kV line to 138 kV with 795 ACSR conductor | Changed responsibility to LCRA | AEP GROUP 063 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 67 | 2010-06-30 |  | 138 | 0 | 18 | 0 | 0 | WHARTON | COLORADO
Old Project | No Change | 07TPIT0040 | Sierra Verde, add 138/69 kV autotransformer | Addition 138/69 kV substation at Sierra Verde and conversion El Campo to Sierra Verde 69 kV line to 138 kV with 795 ACSR conductor | Changed responsibility to LCRA | AEP GROUP 063 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 18 | 2010-06-30 |  | 138 | 0 | 0 | 93 | 0 | COLORADO
New Project | New Project | 10TPIT0072 | Fayetteville-Willow Springs-New Bremen-Bellville South | Rebuild the 28-mile Fayetteville (7286)-Willow Springs (7273)-New Bremen (7271)-Bellville South (7270) 138 kV transmission line (T-216). Upgrade the conductor along the entire line to 1433 ACSS (450 MVA). |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2010-06-30 |  | 138 | 0 | 28.2 | 0 | 0 | FAYETTE | AUSTIN |  |  |  | SEE PROJECT DESCRIPTION | Y
New Project | New Project | 10TPIT0073 | Buda-Rutherford | Replace under-rated limiting line terminal equipment at Buda to increase Buda (7498)-Rutherford (7509) to the conductor's rating. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2010-06-30 |  | 138 | 0 | 0 | 0 | 0 | HAYS |  |  |  |  | SEE PROJECT DESCRIPTION | Y | This project is included with the Lago Vista-Nameless project.
Old Project | No Change | 09TPIT0101 | Oleander, Construct 138/69 kV Substation | Construct a new 138/69 kV Switching Station near East Harrison substation and reconductor the 69 kV line from La Palma to San Benito |  | AEP GROUP 362 | AEP/TCC | Rich Haley 918-599-2653 | 3101 | 2010-06-30 |  | 138 | 0 | 0 | 93 | 0 | CAMERON | CAMERON
Old Project | No Change | 08TPIT0092 | North Victoria to Victoria: Reconductor 69 kV Line | Reconductor Victoria to Magruder, reconductor 69 kV line to 795 ACCC and Install 138/69 kV 187 MVA autotransformer at Magruder on the Victoria to Thomaston 138kV line | Cost Update | AEP GROUP 389 | AEP/TCC | Dave Goetz 918-599-2653 | 15 | 2010-06-30 |  | 69 | 0 | 3.1 | 0 | 0 | VICTORIA | VICTORIA
New Project | New Project | 10TPIT0074 | Buttercup-Whitestone | Replace under-rated limiting line terminal equipment at Buttercup and Whitestone to increase Buttercup (7531)-Whitestone (7529) to the conductor's rating. |  |  | PEC | Randy Buchanan (830) 868-6058 |  | 2010-07-01 |  | 138 | 0 | 0 | 0 | 0 | WILLIAMSON | WILLIAMSON |  |  |  | SEE PROJECT DESCRIPTION | Y | This project is included with the Lago Vista-Nameless project.
Old Project | Change in Service Date. Change from 6/1/2010 7/1/2010 | 09TPIT0004 | Laredo Plant to Lobo, rebuild 138 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and convert Lobo to Laredo 69 kV line section to 138 kV | Cost and Schedule Update | AEP GROUP 216 | AEP/TCC | Bill Eakin 918-599-2653 | 1304 | 2010-07-01 |  | 138 | 0 | 15 | 0 | 0 | WEBB | WEBB
Old Project | No Change | 10TPIT0052 | Big Lake, Add 150 MVA Phase Shifting Transformer | Install a 138 kV Phase Shifting Transformer at Big Lake |  | AEP GROUP 386 | AEP/TNC | Brett Madison 918-599-2653 | 2228 | 2010-08-31 |  | 138 | 0 | 0 | 150 | 0 | REAGAN
Old Project | Change in Service Date. Change from 6/1/2010 9/1/2010 | 08TPIT0079 | Steamboat, new 69/138 kV station | Build Bluff Creek to Steamboat 138 kV line and add Steamboat substation with 69/138 kV autotransformer | Schedule Update | AEP GROUP 341 | AEP/TNC | Brett Madison 918-599-2653 | 2074 | 2010-09-01 |  | 138 | 0 | 0 | 130 | 0 | TAYLOR
Old Project | No Change | 10TPIT0050 | Rayburn Substation | Install (3) Breaker ring to include (2) 69 lines and (1) 69/12.5 transformer |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2010-09-10 |  | 69 | 0 | 0 | 0 | 0 | BRAZOS | [5 empty] | N
Old Project | Change in Service Date. Change from 6/1/2010 9/30/2010 | 08TPIT0136 | Clear Crossing, Build 345 kV switch station | Construct Clear Crossing 345 kV switch station where Oklaunion to Mulberry and Grahm to Morgan 345 kV lines cross | Schedule Update | AEP GROUP 376 | AEP/TNC | Paul Hassink 918-599-2653 | 2323 | 2010-09-30 |  | 345 | 0 | 0 | 0 | 0 | HASKELL | [6 empty] | ERCOT 5 year plan project
Old Project | Change in Service Date. Change from 6/1/2010 9/30/2010 | 08TPIT0080 | Steamboat to Abilene South, Rebuild Dbl Crkt 69/138 kV | Re-Build the Steamboat to Abilene South 69 kV line Dbl Crt 138/69 kV | Schedule Update | AEP GROUP 354 | AEP/TNC | Brett Madison 918-599-2653 | 2121 | 2010-09-30 |  | 138 | 0 | 21.02 | 0 | 0 | TAYLOR | TAYLOR
Old Project | No Change | 08TPIT0151 | Coahoma North 138 kV Switching Station | Construct new switching station to connect a new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R816-E | 2010-11-14 |  | 138 | 0 | 0 | 0 | 0 | HOWARD | [5 empty] | Y
Old Project | No Change | 10TPIT0039 | East Bell County - TNP One 345 kV Line Project | Expansion of 345 kV Switchyard at TNP One associated with East Bell County TNP One 345 kV Line Project |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com |  | 2010-12-01 |  | 345 | 0 | 0 | 0 | 0 | ROBERTSON | ROBERTSON | 2006-11-30 | 2007-01-02 | Wait for SIA and AIR permit for Oak Grove | 39950 |  | See Oncor Electric Delivery Entry for this project, 10TPIT0037
Old Project | Change in Service Date. Change from 6/1/2010 12/1/2010 | 09TPIT0121 | Sun Switch - Sacroc 138 kV line | Rebuild 138 kV line | Change in relative priority and/or resource limitations |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R812-E | 2010-12-01 |  | 138 | 0 | 1.8 | 0 | 0 | SCURRY | SCURRY |  |  |  |  | Y
Old Project | No Change | 07TPIT0236 | N. Terrell Tap - Rose Hill 138 kV line | Rebuild existing line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3059-E | 2010-12-01 |  | 138 | 0 | 8.68 | 0 | 0 | KAUFMAN | KAUFMAN |  |  |  | 2715, 2717, 2714, 2723, 2719 | Y
Old Project | No Change | 08TPIT0069 | Lake Creek - East Waco 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R470-E | 2010-12-01 |  | 138 | 0 | 10.5 | 0 | 0 | MCLENNAN | MCLENNAN |  |  |  | 3410, 3452, 3438 | Y
Old Project | No Change | 08TPIT0111 | Lufkin Switching Station - Texas Foundries Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R389-E | 2010-12-01 |  | 138 | 0 | 0.73 | 0 | 0 | ANGELINA | ANGELINA |  |  |  | 3326, 3327, 3328 | Y
Old Project | No Change | 09TPIT0047 | N. Waco - NE. Waco 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R477-E | 2010-12-01 |  | 138 | 0 | 1.9 | 0 | 0 | MCLENNAN | MCLENNAN |  |  |  | 3551, 3552 | Y
Old Project | No Change | 09TPIT0117 | Stryker Creek - Dialville 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R644-E | 2010-12-01 |  | 138 | 0 | 15.2 | 0 | 0 | CHEROKEE | CHEROKEE |  |  |  |  | Y
Old Project | No Change | 09TPIT0118 | Fisher Road - Wichita Falls 138 kV line | Upgrade existing 138 kV line. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R191-E | 2010-12-01 |  | 138 | 0 | 1.45 | 0 | 0 | WICHITA | WICHITA |  |  |  |  | Y
Old Project | Change in Service Date. Change from 6/11/2010 12/1/2010 | 08TPIT0044 | Circuit 1013 Double Breaker at Decker Power Plant | Install one 138 kV, 3000 Amp, 63 kA circuit breaker and two switches to connect Ckt 1013 (Decker to McNeil) to the Decker MB2 Bus. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P138 | 2010-12-01 |  | 138 | 0 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9187, 9188 | N |  | The double breaker configuration will not be reflected in the SSWG models because the planning models are bus based.
Old Project | No Change | 09TPIT0072 | Jupiter 69 kV to 138 kV voltage conversion | Converts voltage for the substation | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2010-12-31 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 806 | Y |  | This project is related to "Jupiter-Apollo line 69 kV to 138 kV voltage conversion" and "Jupiter-Lawler line 69 kV to 138 kV voltage conversion" projects
Old Project | No Change | 09TPIT0073 | Jupiter-Apollo line 69 kV to 138 kV voltage conversion | Converts voltage for the line | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2010-12-31 |  | 138 | 0 | 2 | 0 | 0 | DALLAS |  |  |  |  | 806, 802 | Y |  | This project is a line voltage conversion and reconductor for solving overload
Old Project | No Change | 09TPIT0074 | Jupiter-Lawler line 69 kV to 138 kV voltage conversion | Converts voltage for the line | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2010-12-31 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  |  |  |  | 806, 815 | Y |  | This project is a line voltage conversion and reconductor for solving overload
Old Project | No Change | 09TPIT0075 | Lawler 69 kV to 138 kV voltage conversion | Converts voltage for the substation | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2010-12-31 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 815 and 820 | Y |  | This project is related to "Jupiter-Lawler line 69 kV to 138 kV voltage conversion" and "Lawler-Fairdale line 69 kV to 138 kV voltage conversion" projects
Old Project | No Change | 09TPIT0076 | Lawler-Fairdale line 69 kV to 138 kV voltage conversion | Converts voltage for the line | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2010-12-31 |  | 138 | 0 | 2 | 0 | 0 | DALLAS |  |  |  |  | 815, 805 | Y |  | This project is a line voltage conversion and reconductor for solving overload
Old Project | No Change | 09TPIT0039 | Woodrow to Kings Row 69kV Transmission Line | Reconstruct 4.0 miles of existing 69V transmission line | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600483 | 2011-03-31 |  | 69 | 0 | 4 | 0 | 0 | DENTON | DENTON |  |  | NA | 901, 909 | N
Old Project | No Change | 09TPIT0053 | Princeton, Climax to New Princeton Station | Build a 138kV line from Climax Station to New Princeton Station to Longneck Station |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com |  | 2011-04-01 |  | 138 | 10 | 0 | 42 | 0 | COLLIN | COLLIN
Old Project | Change in Service Date. Change from 6/30/2010 4/1/2011 | 09TPIT0032 | Williamson 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Williamson substation. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P063 | 2011-04-01 |  | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS |  |  |  | 9295 | Y
Old Project | No Change | 05TPIT0079 | Port Aransas: add 1-14.4 MVAR 69 kV cap bank | Add 4 breaker 69 kV ring bus on high side and install 1-14.4 MVAR capacitor bank at Port Aransas substation |  | AEP GROUP 029 | AEP/TCC | Michael Glueck 918-599-2653 | 1136 | 2011-04-30 |  | 69 | 0 | 0 | 0 | 14.4 | ARANSAS
Old Project | No Change | 07TPIT0073 | Venus - Cedar Hill 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5098-E | 2011-05-01 |  | 345 | 0 | 20.53 | 0 | 0 | ELLIS | DALLAS |  |  |  | 1906, 1904, 2420 | Y
Old Project | No Change | 09TPIT0105 | Rattlesnake Road Switch - Lake Creek 345 kV line | Upgrade existing 345 kV line |  | R499 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R499A-E | 2011-05-01 |  | 345 | 0 | 1.5 | 0 | 0 | MCLENNAN | MCLENNAN |  |  |  |  | Y
Old Project | No Change | 09TPIT0124 | Jacksboro Switch - Willow Creek - Parker 345 kV line | Rebuild 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R531-E | 2011-05-01 |  | 345 | 43.6 | 43.6 | 0 | 0 | JACK | PARKER |  |  |  |  | Y |  | Project will be submitted to ERCOT for RPG review.
Old Project | No Change | 10TPIT0037 | Bell County East - TNP One 345 kV line (Oncor Electric Delivery part of project) | Install 345 kV switching station and construct a double-circuit 345 kV line |  | R704A, R705 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R494-E | 2011-05-01 |  | 345 | 88 | 0 | 0 | 0 | ROBERTSON | BELL | 2006-11-30 |  | 2007-07-01 | 39950, 3687 | Y
Old Project | No Change | 11TPIT0034 | Sargent Road 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M486-E | 2011-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS | [5 empty] | Y
Old Project | No Change | 09TPIT0009 | N Edinburg to Frontera, build 345 kV dbl crct Line | Addition North Edinburg to Frontera 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substation at Frontera |  | AEP GROUP 206 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 288 | 2011-05-01 |  | 345 | 22.4 | 0 | 0 | 0 | HIDALGO | HIDALGO
Old Project | Change in Service Date. Change from 12/1/2010 5/1/2011 | 10TPIT0018 | Austin Ranch - Colony 138 kV line | Upgrade existing 138 kV line | Change in relative priority and/or resource limitations |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3004-E | 2011-05-01 |  | 138 | 0 | 4.6 | 0 | 0 | DENTON | COLLIN |  |  |  | 2518, 2378 | Y
Old Project | No Change | 07TPIT0018 | Lewisville Switch - TNMP Highland 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5067-E | 2011-05-01 |  | 138 | 0 | 1.6 | 0 | 0 | DENTON | DENTON |  |  |  | 645, 1970 | Y
Old Project | No Change | 10TPIT0019 | Everman - Cleburne Switch 138 kV line sections | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3034-E | 2011-05-01 |  | 138 | 0 | 8.5 | 0 | 0 | TARRANT | JOHNSON |  |  |  | 2279, 2210, 2209, 2208, 1883 | Y
Old Project | No Change | 11TPIT0015 | Sherry - Park Row 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5121-E | 2011-05-01 |  | 138 | 0 | 2.8 | 0 | 0 | TARRANT | TARRANT |  |  |  | 1919, 1920, 2257, 2258 | Y
Old Project | No Change | 11TPIT0031 | Celina SE 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3066-E | 2011-05-01 |  | 138 | 0 | 0 | 0 | 36.8 | COLLIN | [5 empty] | Y
Old Project | No Change | 11TPIT0032 | NW Carrollton - Collin 138 kV line | Rebuild existing 138 kV line for double-circuit operation. |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M368-E | 2011-05-01 |  | 138 | 16.93 | 16.93 | 0 | 0 | DALLAS | COLLIN |  |  |  |  | Y
Old Project | No Change | 11TPIT0033 | Saginaw - American MFG Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5070-E | 2011-05-01 |  | 138 | 0 | 1.37 | 0 | 0 | TARRANT | TARRANT |  |  |  |  | Y
Old Project | No Change | 11TPIT0022 | Trading Post 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Trading Post substation. |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P119 | 2011-05-01 |  | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS |  |  |  | 9282 | Y
Old Project | No Change | 11TPIT0014 | Muenster - St. Jo (BEC) 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R186B-E | 2011-05-01 |  | 69 | 0 | 7.8 | 0 | 0 | COOKE | COOKE |  |  |  | 1712, 1716 | Y
Old Project | No Change | 11TPIT0038 | CSU Northgate Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2011-05-06 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS | [5 empty] | N
Old Project | No Change | 11TPIT0005 | Talley Rd - New 138kV Substation | Loop new 138kV substation into future 138kV Medina Lake to CPS line (06TPIT0080) |  | T-0049 | CPS | PM: Hector Torres | S-0383 | 2011-05-11 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5422 | Y |  | There are no transformers associated with this project
Old Project | Change in Service Date. Change from 12/31/2010 5/15/2011 | 09TPIT0044 | E. Richardson - Apollo 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line | Studies indicate timing of project should be changed. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3033-WA | 2011-05-15 |  | 138 | 0 | 2.32 | 0 | 0 | DALLAS | DALLAS |  |  |  | 802, 2690 | Y
Old Project | No Change | 10TPIT0047 | Zenith Switching Station | Build a new 345 kV Zenith substation. Loop ckt.99 Singleton - Obrien, ckt.98 Singleton - T.H. Wharton, ckt 98 T.H. Wharton - Obrien into the new substation. |  |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2011-05-31 |  | 345 | 0 | 0.5 | 0 | 0 | HARRIS | HARRIS | 2007-04-28 | 2007-07-16 | 2007-08-21 | 44900 | Y |  | Added to Houston Area Constraint Mitigation Project, Phase II per discussion with ERCOT.
Old Project | No Change | 07TPIT0019 | Beltline-Lyons 138 kV line | Line upgrade | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2011-05-31 |  | 138 | 0 | 2.4 | 0 | 0 | DALLAS |  |  |  |  | 847, 819 | Y |  | This project is a line upgrade for serving new load at Beltline
Old Project | No Change | 07TPIT0020 | Beltline-Oates 138 kV line | Line upgrade | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2011-05-31 |  | 138 | 0 | 1.6 | 0 | 0 | DALLAS |  |  |  |  | 847, 831 | Y |  | This project is a line upgrade for serving new load at Beltline
Old Project | No Change | 07TPIT0022 | Beltline 138 kV new substation | New load serving | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2011-05-31 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 847 | Y |  | This project is related to 07TPIT0019 and 07TPIT0020 projects
Old Project | No Change | 10TPIT0038 | College-Brand 138 kV line | Line reconductor | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2011-05-31 |  | 138 | 0 | 4.2 | 0 | 0 | DALLAS |  |  |  |  | 829, 827 | Y |  | This project is a line reconductor for solving overload. This line was called as Fairdale-Brand 138 kV line
Old Project | No Change | 11TPIT0035 | McCree 69 kV, install 14.0 MVAR Cap Bank | Install 14 MVAR capacitor bank to support local low voltage problems | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2011-05-31 |  | 69 | 0 | 0 | 0 | 14 | DALLAS |  |  |  |  | 832 | Y |  | This project is a capacitor bank installing for supporting local load voltage problems
Old Project | No Change | 07TPIT0042 | 2nd Lewisville Auto | Install (2nd) 345/138 kV autotransformer at Lewisville station |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2011-06-01 |  | 345 | 0 | 0 | 700 | 0 | DENTON |  |  |  |  | 646645 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
Old Project | No Change | 09TPIT0054 | LA Heights - 138kV Breaker Installations | Install line breakers at LA Heights A & B. | Delayed due to Budget Constraints | T-0117 | CPS | S: Darrell Clifton | S-0308 | 2011-06-01 |  | 138 | 0 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5285 5286 | Y |  | This is a line terminal addition, there are no additional tranformer capacity or transmission circuit miles associated with this project
Old Project | No Change | 10TPIT0001 | Trumbo - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Leon Creek to Pleasanton Rd line | Accelarated by Disribution Planning | T-0082 | CPS | Blake Williams | S-0181 | 2011-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5429 | Y |  | There are no transformers associated with this project
Old Project | No Change | 11TPIT0039 | Dresden to LA Heights - 138kV line upgrade | Upgrade the existing Dresden to LA Heights 138kV transmission line |  |  | CPS | Blake Williams |  | 2011-06-01 |  | 138 | 0 | 3.29 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5130 5285 5286 | Y |  | There are no transformers associated with this project
Old Project | No Change | 11TPIT0036 | Caddo - New Substation | Construct a new 138-26.18-KV substation |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2011-06-01 |  | 138 | 0 | 0 | 0 | 0 | WILSON |  |  |  |  | See Project Title | N
Old Project | No Change | 11TPIT0037 | Santa Clara - New Substation | Build a new 138-26.18 kV 22.4 MVA substation on the GVEC McQueeney(7606)-Cibolo(7608) 138 kV transmission line |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2011-06-01 |  | 138 | 0 | 0 | 22.4 | 0 | GUADALUPE |  |  |  |  | See Project Title | N
Old Project | No Change | 07TPIT0050 | Decker to Techridge 138kV Partial Reconductor | This project calls for the rerouting of the existing Ckt 975 (Decker to Techridge) from Yager corner to the Tecnridge substation. The rerouting will adopt 3000 Amps bundled 795 ACSS Drake. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P061 PLAN_117_P071 | 2011-06-01 |  | 138 | 0 | 4.49 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9195, 9190 | Y
Old Project | Change in Service Date. Change from 5/1/2011 6/1/2011 | 11TPIT0009 | Dunlap 138kV substation | Establish a new 138kV Dunlap substation with (2) 30MVA transformers. The substation will cut into existing Ckt 921 (Austrop - Decker). | Comments- The substation will be built as the first stage to serve the increasing customer load. |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P208 | 2011-06-01 |  | 138 | 0.1 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  | 9194 | Y
Old Project | No Change | 07TPIT0055 | Frisco to Kruegerville Rebuild | Rebuild existing Frisco to Kruegerville with1590 or Acss conductor | Delayed - no overload |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2011-06-01 |  | 138 | 0 | 11.7 | 0 | 0 | COLLIN | DENTON |  |  |  | 6621994681 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | No Change | 10TPIT0010 | Coppell to Roanoke Reconductor | Reconductor existing Coppell to Roanoke 138kv line with 959ACSS conductor |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2011-06-01 |  | 138 | 0 | 17 | 0 | 0 | TARRANT | DALLAS |  |  |  | 1852561556555640 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
New Project | New Project | 10TPIT0083 | Mustang Capacitor Bank | Install 100mvar capacitors at future Mustang sub |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2011-06-01 |  | 138 | 0 | 0 | 0 | 100 | DENTON |  |  |  |  | 654 | N
Old Project | No Change | 10TPIT0012 | Barclay to Silver City Rebuild | Rebuild existing Barclay to Silver City 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2011-06-01 |  | 69 | 0 | 17 | 0 | 0 | FALLS | MILAM |  |  |  | 69,65 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | No Change | 08TPIT0032 | Gilleland 345/138kV autotransformer | Install a 600 MVA 345/138kV autotransformer at the new Gilleland switching substation | Resource constraints and Right of Way issues |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2011-06-30 |  | 345 | 0 | 0 | 480 | 0 | TRAVIS | TRAVIS |  |  |  | The 345kV bus is 9053 and the 138kV bus is 9054 | Y
Old Project | No Change | 07TPIT0027 | CPS Lytle to TCC Lytle: Build 138 kV Line | Add CPS Lytle to TCC Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle |  | AEP GROUP 028 CPS S-0046 | AEP/CPS | Paul Hassink (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 21 | 2011-06-30 |  | 138 | 4 | 0 | 0 | 0 | BEXAR | MEDINA |  |  |  | 5290, 8962 | Y
Old Project | No Change | 08TPIT0018 | Uvalde to Texas Research, build 138 kV line, double circuit capable | Construct Uvalde to CPS Texas Research 138 kV line with 2x795 ACSR |  | AEP GROUP 291 | AEP/CPS | Brian Johnson (AEP) 918-599-2653 Hector Torres (CPS) 210-353-2404 | 1522 | 2011-06-30 |  | 138 | 77.5 | 0 | 0 | 0 | UVALDE | MEDINA |  |  |  | 5430, 8234 | Y
Old Project | No Change | 06TPIT0068 | Hamilton Road to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System |  | AEP GROUP 301 | AEP/TCC | Brian Johnson 918-599-2653 | 1544 | 2011-06-30 |  | 138 | 0 | 8.67 | 0 | 0 | VAL VERDE | VAL VERDE
Old Project | No Change | 06TPIT0082 | Buena Vista to Picacho, reconductor 138 kV line | Reconductor Del Rio 138 kV System |  | AEP GROUP 301 | AEP/TCC | Brian Johnson 918-599-2653 | 1547 | 2011-06-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE
Old Project | No Change | 06TPIT0083 | Del Rio to Buena Vista, reconductor 138 kV line | Reconductor Del Rio 138 kV System |  | AEP GROUP 301 | AEP/TCC | Brian Johnson 918-599-2653 | 1546 | 2011-06-30 |  | 138 | 0 | 2.82 | 0 | 0 | VAL VERDE | VAL VERDE
Old Project | No Change | 06TPIT0084 | Hamilton Road to Del Rio reconductor 138 kV line | Reconductor Del Rio 138 kV System |  | AEP GROUP 301 | AEP/TCC | Brian Johnson 918-599-2653 | 1545 | 2011-06-30 |  | 138 | 0 | 3 | 0 | 0 | VAL VERDE | VAL VERDE
Old Project | No Change | 07TPIT0024 | Lytle: Add 138/69 kV Auto | Add CPS Lytle to TCC Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle |  | AEP GROUP 028 | AEP/TCC | Paul Hassink 918-599-2653 | 74 | 2011-06-30 |  | 138 | 0 | 0 | 93 | 0 | MEDINA
Old Project | No Change | 07TPIT0083 | Picacho to CFE, construct new 138 kV line | Convert Amistad to CFE Amistad 12.5 kV distribution to 138 kV line |  | AEP GROUP 301 | AEP/TCC | Brian Johnson 918-599-2653 | 1548 | 2011-06-30 |  | 138 | 8.8 | 0 | 0 | 0 | VAL VERDE | VAL VERDE
Old Project | Change in Service Date. Change from 5/31/2011 6/30/2011 | 08TPIT0077 | Bluff Creek to Steamboat, new 138 kV line | Build Bluff Creek to Steamboat 138 kV line and add Steamboat substation with 69/138 kV autotransformer | Schedule Update | AEP GROUP 341 | AEP/TNC | Brett Madison 918-599-2653 | 2073 | 2011-06-30 |  | 138 | 12 | 0 | 0 | 0 | TAYLOR | TAYLOR
New Project | New Project | 11TPIT0040 | Uvalde 138 kV Substation Upgrade | Construct Uvalde to CPS Texas Research 138 kV line with 2x795 ACSR | NEW | AEP GROUP 291 | AEP | Brian Johnson (AEP) 918-599-2653 |  | 2011-06-30 |  | 138 | 0 | 0 | 0 | 0 | UVALDE
Old Project | Change in Service Date. Change from 6/1/2011 6/30/2011 | 08TPIT0132 | Melon Creek to Tatton: Build 69 KV Line | Construct Melon Creek substation on Airco to Rincon 138 kV line with 138/69 kV 50 MVA auto and build new 69 kV line from Melon Creek to Tatton | Cost and Schedule Update | AEP GROUP 100 | AEP/TCC | Paul Hassink 918-599-2653 | 2028 | 2011-06-30 |  | 69 | 7.7 | 0 | 0 | 0 | REFUGIO | ARANSAS
Old Project | No Change | 08TPIT0020 | Zorn/Clear Springs-Gilleland Creek-Hutto Switch 345-kV line | Construct a 345 kV double circuit (2x1590 ACSR) line between Zorn/Clearsprings and Hutto Switch and other ONCOR and AE projects. Upgrade the 7.5-mile McNeil (7334)-Gilleland(7336) 795 ACSR 138-kV transmission line to 1433 ACSS/TW. |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | Not yet assigned | 2011-08-31 |  | 345 | 140 | 7.5 | 0 | 0 | WILLIAMSON | GUADALUPE | 2001-12-01 | 2001-12-01 | 2002-02-01 | 7042, 7050, 9054, 3690 | Y |  | Harris Branch substation replaced with Gilleland Creek substation as an in-line termination point for one of the
Old Project | Change in Service Date. Change from 6/1/2011 10/1/2011 | 07TPIT0078 | Devine to Lytle: Rebuild 69 kV Line | Add CPS Lytle to TCC Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Cost and Schedule Update | AEP GROUP 028 | AEP/TCC | Paul Hassink 918-599-2653 | 1778 | 2011-10-01 |  | 69 | 0 | 7 | 0 | 0 | MEDINA | MEDINA |  |  |  |  | Y
Old Project | No Change | 08TPIT0045 | Glen Rose, Spunky to Glen Rose | Build 138kV line from BEC Spunky substation near Granbury to new TNMP Squaw Creek substation site near Glen Rose. |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com |  | 2011-12-01 |  | 138 | 7 | 0 | 42 | 0 | SOMERVELL | SOMERVELL |  |  |  | BEC - 356 TNMP-37705 | Y
Old Project | No Change | 07TPIT0096 | Pockrus Substation Transmission Circuit Breaker Addition | Install transmission circuit breakers and reconfigure 138kV bus | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | 600852 | 2011-12-01 |  | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 917 | Y
Old Project | No Change | 11TPIT0021 | Nassau Bay to Nassau Bay Sw. Rebuild | Rebuild existing 138 kV 4/0 line from Nassau Bay to Nassau Bay Sw. with 1033 double-circuit construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2011-12-01 |  | 138 | 0 | 1.21 | 0 | 0 | HOOD | HOOD |  |  |  | 364373451455 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
Old Project | Change in Service Date. Change from 6/1/2011 1/30/2012 | 07TPIT0077 | Big Foot to Devine: Rebuild 69 kV Line | Add CPS Lytle to TCC Lytle 795 ACSR 138 kV line and 93 MVA 69/138 kV autotransformer at Lytle | Cost and Schedule Update | AEP GROUP 028 | AEP/TCC | Paul Hassink 918-599-2653 | 1777 | 2012-01-30 |  | 69 | 0 | 6.1 | 0 | 0 | FRIO | MEDINA |  |  |  |  | Y
Old Project | Change in Service Date. Change from 6/1/2011 3/1/2012 | 09TPIT0031 | Circuit 972 (McNeil to Howard Lane) Reconductor | Reconductor the last span of the Ckt 972 (McNeil to Howard Lane) going into McNeil substation with bundled 795 ACSR Drake conductor. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P085 | 2012-03-01 |  | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9079, 9217 | Y
Old Project | Change in Service Date. Change from 6/1/2011 4/1/2012 | 07TPIT0086 | Circuit 978 (Seaholm to Warren) Reconductor | Reconductor the last span of the Ckt 978 (Seaholm to Warren) going into Warren substation with bundled 795 ACSR Drake conductor. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P086 | 2012-04-01 |  | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9132, 9286 | Y
Old Project | Change in Service Date. Change from 6/1/2011 5/1/2012 | 10TPIT0017 | Allen Switch - Plano Custer - Collin Junction 138 kV line | Upgrade existing double-circuit 138 kV line | Studies indicate timing of project should be changed. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3047-E | 2012-05-01 |  | 138 | 0 | 9 | 0 | 0 | COLLIN | COLLIN |  |  |  | 2509, 2525, 2510,2526,2524 | Y
Old Project | No Change | 11TPIT0012 | Euless - Grapevine Ball Street 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5131-E | 2012-05-01 |  | 138 | 0 | 5.9 | 0 | 0 | TARRANT | TARRANT |  |  |  | 2016, 2021 | Y
Old Project | No Change | 12TPIT0005 | Kemp South 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3067-E | 2012-05-01 |  | 138 | 0 | 0 | 0 | 36.8 | KAUFMAN | [5 empty] | Y
Old Project | Change in Service Date. Change from 6/1/2011 5/1/2012 | 10TPIT0022 | Ckt 918 Oak Hill to Brodie Lane Reconductor | Reconductor the last span of the Ckt 918 going into Oak Hill sub with bundled 795 ACSR Drake capable of 2000 Amperes |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P084 | 2012-05-01 |  | 138 | 0 | 0.1 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9169, 9247 | Y
Old Project | Change in Service Date. Change from 6/1/2011 5/1/2012 | 11TPIT0023 | Lakeway 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Lakeway substation. | Delayed due to budget constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P124 | 2012-05-01 |  | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS |  |  |  | 9235 | Y
Old Project | No Change | 07TPIT0210 | Hilltop - White Settlement 69 kV line | Rebuild 4/0 ACSR section of line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5135-E | 2012-05-01 |  | 69 | 0 | 14.33 | 0 | 0 | PARKER | TARRANT |  |  |  | 502, 1588, 2089 | Y
Old Project | No Change | 08TPIT0026 | Apollo-Lookout 138 kV line | Line upgrade | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2012-05-31 |  | 138 | 0 | 2.8 | 0 | 0 | DALLAS |  |  |  |  | 802, 828 | Y |  | This project is a line upgrade for serving new load at Lookout
Old Project | No Change | 08TPIT0027 | Lookout 138 kV new substation | New load serving | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2012-05-31 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 828 | Y |  | This project is related to 08TPIT0026 and 08TPIT0029 projects
Old Project | No Change | 08TPIT0029 | Firewheel-Lookout 138 kV line | Line upgrade | On Hold For Funding |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2012-05-31 |  | 138 | 0 | 1.3 | 0 | 0 | DALLAS |  |  |  |  | 821, 828 | Y |  | This project is a line upgrade for serving new load at Lookout
Old Project | Change in Service Date. Change from 6/30/2011 5/31/2012 | 10TPIT0051 | Alamito Creek to Presidio, Replace existing 69kV line with new 69kV line | Replace Alamito Creek to Presidio line with 795 ACSR | Schedule Update | AEP GROUP 358 | AEP/TNC | Brett Madison 918-599-2653 | 2170 | 2012-05-31 |  | 69 | 0 | 60 | 0 | 0 | PRESIDIO | PRESIDIO
Old Project | Change in Service Date. Change from 6/30/2011 6/1/2012 | 08TPIT0033 | Gilleland 345/138 kV Project | Establish a 345kV switching station adjacent to LCRA's Gilleland station. Establish a new 138kV circuit from Gilleland to Techridge and maintain a normally close tie between AEN and LCRA's switchyard at Gilleland. | Delay-Resource constraints and Right of Way issues |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P195 PLAN_117_P207 | 2012-06-01 |  | 345 | 8 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9053, 9054 | Y
Old Project | No Change | 11TPIT0024 | TCC - 138kV Line Reroutes | The following 138kV lines will be rerouted: Cagnon - AMDTP - AMD becomes Cagnon - AMD; Cagnon - AMDTP - Pinn becomes Cagnon - Pinn; Pinn - SWRI becomes Pinn - Westside Helotes - Bandera #2 becomes Helotes - Grissom; Construct a new 138kV line from TCC - SWRI |  | S-0384 | CPS | T: Kevin Phillips | T-0106 | 2012-06-01 |  | 138 | 6.3 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5200 5020 5185 5423 5419 | Y |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0004 | Sulpher Springs - New 138kV Substation | Loop new 138kV substation into the existing 138kV Sommers to Beck line |  |  | CPS | Blake Williams | S-0385 | 2012-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5416 | Y |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0009 | Masterson Rd - New 138kV Substation | Loop new 138kV substation into the existing 138kV Cagnon to Valley Rd line |  |  | CPS | Blake Williams |  | 2012-06-01 |  | 138 | 20 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5296 | Y |  | There are no transformers associated with this project
Old Project | No Change | 12TPIT0006 | Olmos(7613) - New Substation | Build a 138-13.08 kV 22.4 MVA substation on the Olmos switching station site |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2012-06-01 |  | 138 | 0 | 0 | 22.4 | 0 | GUADALUPE |  |  |  |  | See Project Title | Y
Old Project | No Change | 12TPIT0007 | FM-725 - New Substation | Build a 138-26.18 kV 22.4 MVA substation on the GVEC McQueeney(7606) - Schumansville(7609) 138 kV transmission line |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2012-06-01 |  | 138 | 0 | 0 | 22.4 | 0 | BEXAR |  |  |  |  | See Project Title | N
Old Project | Change in Service Date. Change from 10/30/2011 6/1/2012 | 07TPIT0060 | Techridge to Howard Lane 138kV Reconductor | The project calls for Circuit 1004 (Techridge to Howard Lane) to be reconductored using 795 ACSS Drake conductors to increase the capacity to 3000 Amp. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P080 PLAN_117_P194 | 2012-06-01 |  | 138 | 0 | 1.27 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9190, 9217 | Y
Old Project | No Change | 10TPIT0025 | Rinard Creek 138kV substation | Establish a new 138kV Rinard Creek substation with (2) 30MVA transformers. The substation will cut into existing Ckt 987 (Lytton Springs to Slaughter Lane). | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P151 PLAN_117_P152 | 2012-06-01 |  | 138 | 0.1 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  | 9262 | Y
Old Project | No Change | 15TPIT0000 | Bird Pond Substation | Install (3) Breaker ring to include (2) 138 lines and (1) 138/12.5 transformer |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2012-06-11 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS | [5 empty] | N
Old Project | No Change | 10TPIT0031 | Dunlap Autotransformer | The original proposal is to add the 3rd autotransformer at Austrop. The extended outage necessary for the project has resulted in the alternative to install a 600MVA auto at the Dunlap substation. The Clear Springs to Gilleland 345kV circuit will terminate on the 345kV bus at Dunlap. In addition, the existing ckt 921 will be converted to 345kV and terminate at the 345kV bus at Dunlap. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P132 | 2012-08-01 |  | 345 | 0 | 0 | 600 | 0 | TRAVIS | TRAVIS |  |  |  | 9044, 9045 | Y
Old Project | No Change | 08TPIT0087 | Climax-Longneck Upgrade | Rebuild existing Climax-Longneck 69 kV line to 138 kV operation. |  |  | TNMP | Allen Aars, 972-317-5110,Allen.Aars@tnmp.com |  | 2012-10-01 |  | 138 | 0 | 4.2 | 42 | 0 | COLLIN | COLLIN |  |  |  | 37250, 37260, 37280 | N
Old Project | No Change | 12TPIT0008 | Reconstruct 2 miles - Kings Row to Denton North 69kV Transmission Line | Reconstruct 2 miles of existing 69V transmission line | On schedule | None | DENTON | Chuck Sears, (940) 349-7111, cxsears@cityofdenton.com | Not Assigned | 2012-12-31 |  | 69 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  | NA | 912, 909 | N
Old Project | Change in Service Date. Change from 5/1/2012 5/31/2013 | 11TPIT0020 | Oklaunion to Bowman, Build 345 kV line | Oklaunion to Bowman: Build a new 50 mile 345 kV line | Schedule Update | AEP GROUP 408 | AEP/TXU | Paul Hassink 918-599-2653 | 3136 | 2013-05-31 |  | 345 | 50 | 0 | 0 | 0 | WILBARGER | ARCHER | [5 empty] | ERCOT 5 yr plan project
Old Project | No Change | 11TPIT0026 | Cagnon - Install a Third 345kV Autotransformer | Install one 600 MVA autotransformer. |  |  | CPS | Blake Williams |  | 2013-06-01 |  | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR |  |  |  | 5056 | Y |  | There are no transmission line additions associated with this project
Old Project | No Change | 07TPIT0036 | North McCamey to Twin Buttes 345 kV Line | 12/02 plan recommends the construction of a 345kV 2x1590 ACSR line between North McCamey and Twin Buttes |  | AEP GROUP 016 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 1240, LCRA#1005054 | 2013-06-01 |  | 345 | 120 | 0 | 0 | 0 | UPTON | IRION | 2004-03-03 | 2003-03-29 | 2003-05-09 |  | N | ACTUAL ENERGIZE DATE HAS NOT BEEN DETERMINED AND WILL BE TRIGGERED BY 1500 MW OF WIND GENERATION IN THE MCCAMEY AREA | Dependent on Wind Farm Subscription
Old Project | No Change | 07TPIT0037 | North McCamey - Odessa 345 kV Line | 12/02 plan recommends the construction of a 345 kV 2x1590 ACSR line between North McCamey and Odessa and 2x600 MVA autotransformers at North McCamey |  | AEP GROUP 016 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 1296 | 2013-06-01 |  | 345 | 50 | 0 | 1200 | 0 | UPTON | ECTOR | 2003-03-03 | 2003-03-29 | 2003-05-09 |  | N | ACTUAL ENERGIZE DATE HAS NOT BEEN DETERMINED AND WILL BE TRIGGERED BY 2000 MW OF WIND GENERATION IN THE MCCAMEY AREA | Dependent on Wind Farm Subscription
Old Project | No Change | 07TPIT0038 | North McCamey Three 345/138 kV autotransformers | 12/02 plan recommends the addition of Three 345/138kV autotransformers North McCamey |  | AEP GROUP 016 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 1294, LCRA#1005055 | 2013-06-01 |  | 345 | 0 | 0 | 1800 | 0 | UPTON |  | 2004-03-03 | 2003-03-29 | 2003-05-09 |  | N | ACTUAL ENERGIZE DATE HAS NOT BEEN DETERMINED AND WILL BE TRIGGERED BY 1500 MW OF WIND GENERATION IN THE MCCAMEY AREA | Dependent on Wind Farm Subscription
Old Project | No Change | 08TPIT0002 | Frontera to South McAllen 345 kV line | Construct a 345 kV transmission line from Frontera to South McAllen. |  | AEP GROUP 236 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 292 | 2013-06-01 |  | 345 | 12 | 0 | 0 | 0 | HIDALGO | HIDALGO | [5 empty] | ACTUAL ENERGIZE DATE HAS NOT BEEN DETERMINED.
Old Project | No Change | 11TPIT0001 | Lobo to Rio Bravo, build 345 kV line | Construct 345 kV line from Lobo to Rio Bravo and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 206 | AEP/TCC | Paul Hassink 918-599-2653 | 880 | 2013-06-01 |  | 345 | 30 | 0 | 0 | 0 | WEBB | WEBB
Old Project | No Change | 13TPIT0011 | Palo Alto - New 138kV Substation | Loop new 138kV substation into the existing 138kV Leon Creek to Chavaneaux line |  |  | CPS | Blake Williams |  | 2013-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5330 | Y |  | There are no transformers associated with this project
Old Project | No Change | 11TPIT0004 | Rio Bravo to Wormser, Reconductor 138 kV line | Construct 345 kV line from Lobo to Rio Bravo and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 206 | AEP/TCC | Paul Hassink 918-599-2653 | 1305 | 2013-06-01 |  | 138 | 0 | 9.86 | 0 | 0 | WEBB | WEBB
Old Project | No Change | 11TPIT0017 | Wormser to Santa Nino: Reconductor 138 KV Line | Construct 345 kV line from Lobo to Rio Bravo and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 206 | AEP/TCC | Paul Hassink 918-599-2653 | 2209 | 2013-06-01 |  | 138 | 0 | 3.25 | 0 | 0 | WEBB | WEBB
New Project | New Project | 13TPIT0014 | Decatur Capacitor Bank | Install 15mvar capacitor bank at Decatur |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2013-06-01 |  | 138 | 0 | 0 | 0 | 15 | WISE |  |  |  |  | 583 | N
Old Project | No Change | 06TPIT0070 | Alamito Creek to Cienega, rebuild 69 kV Line | Rebuild Alamito Creek to Cienega 69 kV line from #2 to 795 ACSR |  | AEP GROUP 022 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 53, LCRA#1002509 | 2013-06-01 |  | 69 | 0 | 23 | 0 | 0 | PRESIDIO | PRESIDIO |  |  |  |  | N | ACTUAL ENERGIZE DATE HAS NOT BEEN DETERMINED.
New Project | New Project | 13TPIT0013 | Perry to Midway Rebuild | Rebuild Perry to Midway with 959ACSS |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2013-06-01 |  | 69 | 0 | 12.4 | 0 | 0 | Falls | Falls |  |  |  | 92185 | N
New Project | New Project | 13TPIT0012 | Zorn Autotransformer Addition | Add a new 345-138 kV 478 MVA autotransformer at the Zorn substation (7042). |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2013-06-30 |  | 345 | 0 | 0 | 478 | 0 | GUADALUPE |  | 2008-01-30 | 2008-06-10 | N/A | SEE PROJECT DESCRIPTION | Y
Old Project | No Change | 10TPIT0027 | West Batesville, Install 138 kV ring bus | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus |  | AEP GROUP 383 | AEP/TCC | Paul Hassink 918-599-2653 | 2168 | 2013-06-30 |  | 138 | 0 | 0 | 0 | 0 | ZAVALA
Old Project | No Change | 10TPIT0028 | Escondido to West Batesville, build 138 kV Line | West Batesville: Construct bundled 2x795 ACSR 138 kV line, add 138 kV circuit breaker and convert to 4 breaker ring bus |  | AEP GROUP 383 | AEP/TCC | Paul Hassink 918-599-2653 | 2169 | 2013-06-30 |  | 138 | 46.2 | 0 | 0 | 0 | MAVERICK | ZAVALA
Old Project | No Change | 10TPIT0005 | Trading Post to Patton Lane New 138kV Circuit (new) | Establish a new 138kV transmission circuit between Trading Post and Patton Lane substation. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P055 PLAN_117_P076 PLAN_117_P156 | 2013-12-01 |  | 138 | 12 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9282, 9253 | Y
Old Project | Change in Service Date. Change from 6/1/2013 12/1/2013 | 10TPIT0043 | Parmer 138kV substation | Establish a 138kV Parmer substation that cuts into the existing Circuit 975 (Decker to Techridge) near the Yager corner |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P090 PLAN_117_P091 | 2013-12-01 |  | 138 | 0.1 | 0 | 100 | 0 | TRAVIS | TRAVIS |  |  |  | 9252 | Y
Old Project | Change in Service Date. Change from 6/1/2013 12/1/2013 | 13TPIT0008 | Burleson to Fiesta to Central Austin to Koenig to Northland 138kV conversion | Convert the existing 69kV circuits from Burleson to Northland to 138kV operation. The circuits will be rated at 2000 Amps. |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | N/A | 2013-12-01 |  | 138 | 0 | 8 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9120, 9121, 9244, 9269, 9227, 9128, 9129 | Y
Old Project | No Change | 08TPIT0061 | Angleton - Liverpool ckt.04 | Raise conductors to increase thermal ratings | Deferred |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2014-02-15 |  | 138 | 0 | 10.5 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 42110, 42870 | N |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. IDEV reflects change in project status.
Old Project | Change in Service Date. Change from 6/1/2013 4/1/2014 | 13TPIT0009 | Koenig Lane to Justin Lane to McNeil 138kV conversion | Convert the existing 69 kV circuits from Koenig to Justin Lane to McNeil to 138kV operation. |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | N/A | 2014-04-01 |  | 138 | 0 | 5.25 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9227, 9079 | Y
Old Project | No Change | 14TPIT0000 | CSU Graham Rd Substation | Install (3) Breaker ring to include (2) 138 lines and tap to College Station Utilities |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2014-05-06 |  | 138 | 0 | 0 | 0 | 0 | BRAZOS | [5 empty] | N
Old Project | Change in Service Date. Change from 6/1/2013 6/1/2014 | 07TPIT0048 | Bergstrom to Carson Creek 138kV circuit | Establish a new 138kV transmission circuit from Bergstrom to Carson Creek substation with bundled 795 ACSR Drake conductors. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P074 PLAN_117_P031 PLAN_117_P168 | 2014-06-01 |  | 138 | 2.3 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9163, 9175 | Y
Old Project | Change in Service Date. Change from 6/1/2013 6/1/2014 | 07TPIT0049 | Bergstrom to Sand Hill 138kV circuit | Establish a new 138kV transmission circuit from Bergstrom to Sand Hill switchyard with bundled 795 ACSR Drake conductors. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P075 PLAN_117_P169 PLAN_117_P056 | 2014-06-01 |  | 138 | 4 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9163, 9216 | Y
Old Project | Change in Service Date. Change from 6/1/2013 6/1/2014 | 08TPIT0034 | McNeil to Summit new 2nd 138kV circuit | Establish a 138kV transmission line between McNeil and Summit substation using bundled 795 ACSR Drake conductors. | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P069 PLAN_117_P136 PLAN_117_P137 | 2014-06-01 |  | 138 | 2 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9079, 9279 | Y
Old Project | No Change | 10TPIT0004 | Lakeway to Trading Post New 138kV Circuit (new) | Establish a new 138kV transmission circuit between Lakeway and Trading Post substation. | Under Evaluation |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | N/A | 2014-06-01 |  | 138 | 3.8 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9282, 9235 | N
Old Project | Change in Service Date. Change from 6/1/2013 6/1/2014 | 11TPIT0008 | Rainey St 138kV substation | Establish a new 138kV Rainey St substation with (2) 50MVA transformers. The substation will cut into existing Ckt 1015 (Pedernales to Seaholm). | Delayed to 2014 due to slower growth. |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P158 PLAN_117_P166 PLAN_117_P167 | 2014-06-01 |  | 138 | 0.1 | 0 | 100 | 0 | TRAVIS | TRAVIS |  |  |  | 9261 | Y
Old Project | Change in Service Date. Change from 6/1/2013 6/1/2014 | 11TPIT0011 | East 138kV substation | Establish a 138kV East substation with (2) 30MVA transformers and 4 distribution circuits with underground get-a-ways. The station will cut into existing Ckt 975 (Decker - Techridge). | Delay - Budget Constraints |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | PLAN_117_P142 PLAN_117_P143 PLAN_117_P144 | 2014-06-01 |  | 138 | 0.1 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  | 9195 | Y
Old Project | Change in Service Date. Change from 6/1/2013 6/1/2014 | 13TPIT0010 | Decker Plant to Dessau Rebuild | Replace each triple lattice structures with two double circuit structures and reconductor to 3000 Amps. |  |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | N/A | 2014-06-01 |  | 138 | 0 | 12 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9187, 9271, 9193 | Y
Old Project | No Change | 10TPIT0048 | Koppe Bridge Substation | Install (4) Breaker ring to include (2) 69 lines and (1) 69/12.5 transformer |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2014-09-10 |  | 69 | 0 | 0 | 0 | 0 | BRAZOS | [5 empty] | N
Old Project | No Change | 10TPIT0049 | Koppe Bridge Transmission | Build 69 kV line(s) to serve station |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2014-09-10 |  | 69 | 10 | 0 | 0 | 0 | BRAZOS | BRAZOS |  |  |  |  | N
Old Project | No Change | 10TPIT0003 | Hidden Valley to Lakeway New 138kV Circuit (new) | Establish a new 138kV transmission circuit between Lakeway and Hidden Valley substation. | Under Evaluation |  | AUSTIN ENERGY | Reza Ebrahimian (512) 322-6740 Reza.ebrahimian@austinenergy.com | N/A | 2014-12-01 |  | 138 | 4 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9207, 9235 | N
Old Project | No Change | 11TPIT0003 | Rio Bravo, 345 kV SS with 345/138 kV autotransformer | Construct 345 kV line from Lobo to Rio Bravo and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 206 | AEP/TCC | Paul Hassink 918-599-2653 | 1309 | 2015-03-15 |  | 345 | 0 | 0 | 675 | 0 | WEBB
Old Project | Change in Service Date. Change from 6/30/2013 3/15/2015 | 08TPIT0129 | Harbor SS: Build 138 KV line cut-in | Build New Harbor Distribution Substation and cut-in to the Nueces Bay to Morris Street 138 KV Line | Schedule Update | AEP GROUP 255 | AEP/TCC | Michael Glueck 918-599-2653 | 2237 | 2015-03-15 |  | 138 | 0.7 | 0 | 0 | 0 | NUECES | NUECES
Old Project | Change in Service Date. Change from 10/1/2013 3/15/2015 | 08TPIT0130 | Harbor SS: Build 138/12 KV Station | Build New Harbor Distribution Substation and cut-in to the Nueces Bay to Morris Street 138 KV Line | Schedule Update | AEP GROUP 255 | AEP/TCC | Michael Glueck 918-599-2653 | 2238 | 2015-03-15 |  | 138 | 0 | 0 | 0 | 0 | NUECES
Old Project | No Change | 08TPIT0005 | Frontera, add SS with 345/138 kV autotransformer | Addition North Edinburg to Frontera to South McAllen 345 kV line with bundled 1590 ACSR conductor and double circuit capable structures and 345/138 kV substation at Frontera |  | AEP GROUP 276 | AEP/TCC | Paul Hassink 918-599-2653 | 1061 | 2015-03-31 |  | 345 | 0 | 0 | 675 | 0 | HIDALGO
Old Project | No Change | 11TPIT0002 | Sol to Rio Bravo, build 345 kV line | Construct 345 kV line from Rio Bravo to Sol to N Edinburg and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 276 | AEP/TCC | Paul Hassink 918-599-2653 | 630 | 2015-03-31 |  | 345 | 122.4 | 0 | 0 | 0 | WEBB | HIDALGO
Old Project | No Change | 13TPIT0005 | Sol, Build 345 KV SS | Construct 345 kV line from Rio Bravo to Sol to N Edinburg and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 276 | AEP/TCC | Paul Hassink 918-599-2653 | 631 | 2015-03-31 |  | 345 | 0 | 0 | 0 | 0 | HIDALGO
Old Project | No Change | 13TPIT0006 | N. Edinburg to Sol: Build 345 KV Line | Construct 345 kV line from Rio Bravo to Sol to N Edinburg and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer |  | AEP GROUP 276 | AEP/TCC | Paul Hassink 918-599-2653 | 3064 | 2015-03-31 |  | 345 | 15 | 0 | 0 | 0 | HIDALGO | HIDALGO
Old Project | No Change | 13TPIT0007 | Frontera to Sol: Build 345 KV Line | Frontera to Sol: Build 12.4 Miles of 2-1590 ACSR double circuit 345 KV |  | AEP GROUP 276 | AEP/TCC | Paul Hassink 918-599-2653 | 288 | 2015-03-31 |  | 345 | 12.4 | 0 | 0 | 0 | HIDALGO | HIDALGO
Old Project | Change in Service Date. Change from 5/15/2014 4/1/2015 | 13TPIT0001 | Ranchito: Build 138 KV station with 138/69 KV Auto and Ring Bus | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer | Schedule Change | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1329 | 2015-04-01 |  | 138 | 0 | 0 | 150 | 0 | CAMERON
Old Project | No Change | 00TPIT0004 | DeCordova - Benbrook 345 kV line upgrade | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5034-E | 2015-05-01 |  | 345 | 0 | 27 | 0 | 0 | HOOD | TARRANT |  |  |  | 1873, 1890 | N
Old Project | No Change | 07TPIT0001 | Liggett - Trinity Switch 345 kV line | Construct Liggett - Trinity 345 kV line |  | M5014-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5015-E | 2015-05-01 |  | 345 | 12.8 | 0 | 0 | 0 | DALLAS | TARRANT |  |  |  | 2095, 2097 | N
Old Project | No Change | 07TPIT0002 | Trinity Switch 345/138 kV autotransformer | Create Trinity Switch and install a 600 MVA 345/138 kV autotransformer |  | M5015-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5014-E | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | TARRANT |  |  |  |  | 2096, 2097 | N
Old Project | No Change | 07TPIT0118 | Lavon 345/138 kV Switching Station | Construct 345/138 kV switching station |  | M375B, M375C | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375A-E | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  |  |  |  | 2475, 2476 | N
Old Project | No Change | 07TPIT0120 | Liggett 345/138 kV autotransformer | Replace the existing 450 MVA 345/138 kV autransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5107-E | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  | 2008-06-10 | 2008-06-25 | N/A | 1923, 1926 | N
Old Project | No Change | 07TPIT0126 | Tricorner - Seagoville Switch 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4044-E | 2015-05-01 |  | 345 | 0 | 9.4 | 0 | 0 | DALLAS | DALLAS |  |  |  | 2432, 2433 | N
Old Project | No Change | 07TPIT0140 | Trinidad - Watermill 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4045-E | 2015-05-01 |  | 345 | 0 | 52 | 0 | 0 | HENDERSON | DALLAS |  |  |  | 2427, 3123 | N
Old Project | No Change | 09TPIT0001 | West Denton - NW Carrollton 345 kV circuit (Oncor Electric Delivery portion) | Add second Circuit from West Denton to NW Carrollton |  | R198A and R198C | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R198B-E | 2015-05-01 |  | 345 | 26.9 | 0 | 0 | 0 | DENTON | DALLAS |  |  |  | 988, 2361 | N
Old Project | No Change | 09TPIT0042 | Collin 345/138 kV autotransformer | Install second 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M318-E | 2015-05-01 |  | 345 | 0 | 0 | 600 | 0 | COLLIN |  |  |  |  | 2370, 2372 | N
Old Project | No Change | 10TPIT0020 | Krum W. 345 kV Switch and Anna Switch - Krum W. Switch 345 kV line | Establish new 345 kV switching station and construct a double-circuit 345 kV line |  | R198B and R198C | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R198A-E | 2015-05-01 |  | 345 | 100 | 0 | 0 | 0 | DENTON | COLLIN |  |  |  | 1730, 2373 | N
Old Project | No Change | 10TPIT0021 | Krum W. Switch - W. Denton 345 kV circuit (Oncor Electric Delivery portion only) | Add second 345 kV circuit |  | R198A and R198B | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R198C-E | 2015-05-01 |  | 345 | 6 | 0 | 0 | 0 | DENTON | DENTON |  |  |  | 988, 1730 | N
Old Project | Change in Service Date. Change from 5/1/2015 5/1/2015 | 08TPIT0128 | Midland East - Stanton East - Big Spring West - Big Spring Switch 138 kV line | Rebuild existing 138 kV line | Project deferred waiting on RPG review. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R622-E | 2015-05-01 |  | 138 | 0 | 45.2 | 0 | 0 | MIDLAND | HOWARD | 2008-02-01 |  |  | 1023, 1324, 1322 | N |  | Project is currently being reviewed by ERCOT.
Old Project | No Change | 06TPIT0036 | Ennis Switch - Ennis 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M280-E | 2015-05-01 |  | 138 | 0 | 6.32 | 0 | 0 | ELLIS | ELLIS |  |  |  | 2324, 2326 | N
Old Project | No Change | 06TPIT0042 | Lake Wichita Switch - Wichita Falls Switch 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R168-E | 2015-05-01 |  | 138 | 0 | 6.3 | 0 | 0 | ARCHER | WICHITA |  |  |  | 1447, 1449 | N
Old Project | No Change | 06TPIT0047 | Elkton - Tyler West 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R323-E | 2015-05-01 |  | 138 | 0 | 4.98 | 0 | 0 | SMITH | SMITH |  |  |  | 3106, 3139 | N
Old Project | No Change | 07TPIT0110 | Mildand East - Windwood 138 kV line upgrade | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R221-E | 2015-05-01 |  | 138 | 0 | 1.7 | 0 | 0 | MIDLAND | MIDLAND |  |  |  | 1023, 1116 | N
Old Project | No Change | 07TPIT0119 | Lavon Switch - Allen Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375B-E | 2015-05-01 |  | 138 | 8.9 | 0 | 0 | 0 | COLLIN | COLLIN |  |  |  | 2475, 2477, 2509 | N
Old Project | No Change | 07TPIT0122 | Royse - Dalrock 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3035-E | 2015-05-01 |  | 138 | 0 | 6.8 | 0 | 0 | ROCKWALL | ROCKWALL |  |  |  | 2472, 2733, 2735 | N
Old Project | No Change | 09TPIT0066 | Boggy Creek 138 kV Switching Station and associated line | Construct 138 kV switching station and add second circuit to a 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R488-E | 2015-05-01 |  | 138 | 3.5 | 0 | 0 | 0 | BELL | BELL |  |  |  | 3424, 3415, 3425, 13645 | N
Old Project | No Change | 09TPIT0067 | Bonham Switching Station 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R516-E | 2015-05-01 |  | 138 | 0 | 0 | 100 | 0 | FANNIN |  |  |  |  | 1760, 1761 | N
Old Project | No Change | 10TPIT0009 | Trinity Switch - Hurst 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5040-E | 2015-05-01 |  | 138 | 0 | 4 | 0 | 0 | TARRANT | TARRANT |  |  |  | 2096, 2115 | N
Old Project | No Change | 10TPIT0032 | Arco (TMPA) - Krugerville 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5129-E | 2015-05-01 |  | 138 | 0 | 5.6 | 0 | 0 | DENTON | DENTON |  |  |  | 1994, 1993 | N
Old Project | No Change | 10TPIT0034 | Leon Switch #2 138/69 kV autotransformer replacement | Replace existing 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R517-E | 2015-05-01 |  | 138 | 0 | 0 | 100 | 0 | EASTLAND |  |  |  |  | 1624, 1626 | N
Old Project | No Change | 11TPIT0027 | East Richardson Switch - Ben Davis Switch (TMPA) 138 kV line | Create a new 138 kV line by reconfiguring existing lines |  | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375D-E | 2015-05-01 |  | 138 | 0 | 0 | 0 | 0 | COLLIN | DALLAS |  |  |  |  | N
Old Project | No Change | 06TPIT0092 | Wichita Falls Switch - Wichita Falls Basin 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R168A-E | 2015-05-01 |  | 69 | 0 | 1 | 0 | 0 | ARCHER | WICHITA |  |  |  | 1449, 1508 | N
Old Project | No Change | 08TPIT0110 | Temple - Little River 69 kV line | Rebuild existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R097-E | 2015-05-01 |  | 69 | 0 | 7.4 | 0 | 0 | BELL | BELL |  |  |  | 3645, 3644 | N
Old Project | No Change | 09TPIT0068 | W. Weatherford - Weatherford 69 kV line | Rebuild existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R515-E | 2015-05-01 |  | 69 | 0 | 7.5 | 0 | 0 | PARKER | PARKER |  |  |  | 1586, 1585 | N
Old Project | No Change | 08TPIT0071 | North Lake 345/138 kV autotransformer | Install a 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3020-E | 2015-05-15 |  | 345 | 0 | 0 | 600 | 0 | DALLAS |  |  |  |  | 2334, 2333 | N
Old Project | No Change | 06TPIT0143 | Temple Switch - S. Temple 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R448-E | 2015-05-15 |  | 138 | 0 | 4.4 | 0 | 0 | BELL | BELL |  |  |  | 3415, 3612, 3602, 3611 | N
Old Project | No Change | 07TPIT0012 | Trinity Switch - Richland 138 kV line | Upgrade existing 138 kV line |  | M5014-E | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5069-E | 2015-05-15 |  | 138 | 0 | 0.5 | 0 | 0 | TARRANT | TARRANT |  |  |  | 2096, 2100 | N
Old Project | No Change | 07TPIT0138 | Oates (GPL) - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M322-E | 2015-05-15 |  | 138 | 0 | 1.5 | 0 | 0 | DALLAS | DALLAS |  |  |  | 831, 2739 | N
Old Project | No Change | 08TPIT0007 | Austin Ranch - Hebron 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3002-E | 2015-05-15 |  | 138 | 0 | 0.7 | 0 | 0 | DENTON | DENTON |  |  |  | 2376, 2377 | N
Old Project | No Change | 08TPIT0068 | Collin - Frisco (BEC) 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M596-E | 2015-05-15 |  | 138 | 0 | 1.7 | 0 | 0 | COLLIN | DENTON |  |  |  | 2370, 681 | N
Old Project | No Change | 09TPIT0041 | Collin - Custer (BEC) 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3029-E | 2015-05-15 |  | 138 | 0 | 3.5 | 0 | 0 | COLLIN | COLLIN |  |  |  | 2370, 655 | N
Old Project | No Change | 09TPIT0043 | Coppell - North Lake 138 kV line | Construct 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M549-E | 2015-05-15 |  | 138 | 4.8 | 0 | 0 | 0 | DALLAS | DALLAS |  |  |  | 2015, 2386 | N
Old Project | No Change | 09TPIT0050 | Rowlett - Garland Bobtown Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3032-E | 2015-05-15 |  | 138 | 0 | 4.1 | 0 | 0 | DALLAS | DALLAS |  |  |  | 2736, 2739 | N
Old Project | No Change | 09TPIT0051 | Salado Switch - Cedar Valley Switch (BEC) 138 kV line and switching stations | Establish two new 138 kV switching stations and connect them with a new 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R469-E | 2015-05-15 |  | 138 | 7 | 0 | 0 | 0 | BELL | BELL |  |  |  | 117, 3640 | N
Old Project | No Change | 11TPIT0028 | Allen Switch - West Plano Switch 138 kV line | Create a new 138 kV line by reconfiguring existing lines and adding circuit to existing structures |  | M375A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M375C-E | 2015-05-15 |  | 138 | 3.5 | 0 | 0 | 0 | COLLIN | COLLIN |  |  |  | 2510, 2691, 2673 | N
Old Project | No Change | 12TPIT0002 | South McAllen 345 KV SS to South McAllen 138 KV SS: Build 138 kV line | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1276 | 2015-05-31 |  | 138 | 0 | 0.5 | 0 | 0 | HIDALGO
Old Project | No Change | 00TPITno06 | Loma Alta - Ranchito or la Palma 345-kV line | Install 345-kV line from Loma Alta to La Palma or Ranchito |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2015-06-01 |  | 345 | 20 | 0 | 0 | 0 | CAMERON
Old Project | No Change | 00TPITno07 | Loma Alta - Rio Hondo 345-kV line | Install 345-kV line from Loma Alta to Rio Hondo |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2015-06-01 |  | 345 | 25 | 0 | 0 | 0 | CAMERON
Old Project | No Change | 00TPITno10 | Loma Alta 345kV station and autotransformer | Construct a 345 substation and connect to the existing Loma Alta 138 substation. |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2015-06-01 |  | 345 | 0 | 0 | 600 | 0 | CAMERON
Old Project | No Change | 00TPITno14 | LaPalma to Ranchito, new 345 kV line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1060 | 2015-06-30 |  | 345 | 10 | 0 | 0 | 0 | CAMERON | CAMERON
Old Project | No Change | 00TPITno15 | Ranchito, New SS with 345/138 kV autotransformer | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1059 | 2015-06-30 |  | 345 | 0 | 0 | 675 | 0 | CAMERON
Old Project | No Change | 08TPIT0006 | South McAllen, new SS with 345/138 kV autotransformer | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 293 | 2015-06-30 |  | 345 | 0 | 0 | 675 | 0 | HIDALGO
Old Project | No Change | 13TPIT0000 | Frontera to South McAllen, build 345 KV line | Add Frontera to South McAllen 345 kV line with bundled 1590 ACSR and double circuit capable structures and 345/138 kV substations at Frontera and South McAllen |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 292 | 2015-06-30 |  | 345 | 12.18 | 0 | 0 | 0 | HIDALGO | HIDALGO
Old Project | No Change | 12TPIT0003 | LaPalma to Ranchito: Reconductor 138 KV Line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1519 | 2015-06-30 |  | 138 | 0 | 10.5 | 0 | 0 | CAMERON | CAMERON
Old Project | No Change | 13TPIT0002 | Ranchito to Military Highway: Reconductor 138 KV Line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1332 | 2015-06-30 |  | 138 | 0 | 10 | 0 | 0 | CAMERON | CAMERON
Old Project | No Change | 13TPIT0004 | Ranchito to Brownsville SS 69 KV: Rebuild 69 kV line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 1331 | 2015-06-30 |  | 69 | 0 | 9.3 | 0 | 0 | CAMERON | CAMERON
Old Project | No Change | 07TPIT0234 | Collin Switch - NW. Carrollton 345 kV line | Upgrade existing 345 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3061-E | 2016-05-01 |  | 345 | 0 | 19.3 | 0 | 0 | COLLIN | DALLAS | 2006-10-01 | 2007-02-01 | N/A | 2372, 2361 | N |  | The ERCOT Staff determined this project is not economically justified in their February 2007 study.
Old Project | No Change | 07TPIT0069 | Sterrett - Sardis 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M361-E | 2016-05-01 |  | 138 | 0 | 1.95 | 0 | 0 | ELLIS | ELLIS |  |  |  | 2317, 203 | N
Old Project | No Change | 08TPIT0109 | Payne - Collin Switching Station 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R519-E | 2016-05-01 |  | 138 | 0 | 31.75 | 0 | 0 | GRAYSON | COLLIN | 2008-01-07 |  |  | 1758, 1757, 2350, 2366, 2349, 2364, 2370 | N
Old Project | No Change | 08TPIT0153 | Elkton - Athens North Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R651-E | 2016-05-01 |  | 138 | 0 | 29.1 | 0 | 0 | HENDERSON | HENDERSON | 2007-11-26 |  |  | 3177, 3178, 3172, 3131 | Y
Old Project | No Change | 09TPIT0122 | Shamburger - Tyler NW 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R820-E | 2016-05-01 |  | 138 | 0 | 6.3 | 0 | 0 | SMITH | SMITH |  |  |  |  | N
Old Project | No Change | 07TPIT0014 | Plano West - Richardson Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M364-E | 2016-05-15 |  | 138 | 0 | 1.9 | 0 | 0 | COLLIN | DALLAS |  |  |  | 2673, 2685 | N
Old Project | No Change | 09TPIT0024 | Electra - KMA Tap 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R185-E | 2016-05-15 |  | 69 | 0 | 9.9 | 0 | 0 | WICHITA | WICHITA |  |  |  | 1538, 1536 | N
Old Project | No Change | 00TPITno19 | Ranchito to South McAllen, new 345 kV line | Construct 345 kV line from LaPalma to Ranchito to South McAllen and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer |  | AEP GROUP 236 | AEP/TCC | Paul Hassink 918-599-2653 | 295 | 2016-05-31 |  | 345 | 38 | 0 | 0 | 0 | CAMERON | HIDALGO
Old Project | No Change | 07TPIT0011 | Watermill 138 kV series reactors | Install two-ohm 138 kV series reactor on autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4021-E | 2017-05-01 |  | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 2427, 2430 | N
Old Project | Change in Service Date. Change from 6/30/2015 6/1/2017 | 09TPIT0037 | Blossom - New 138 kV Substation | Loop new 138 kV substation into the existing 138kV Harmony Hills to Skyline line | Delayed by Distribution Planning | S-0768 | CPS | S: Darrell Clifton | T-0021 | 2017-06-01 |  | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5022 | N |  | There are no transformers associated with this project
Old Project | Change in Service Date. Change from 4/1/2016 5/1/2018 | 09TPIT0046 | N. Midlothian - Midlothian TXI Tap 138 kV line | Upgrade existing 138 kV line | Studies indicate timing of project should be changed. |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3031-E | 2018-05-01 |  | 138 | 0 | 6.2 | 0 | 0 | ELLIS | ELLIS |  |  |  | 2310, 2311, 2313 | N
Old Project | Change in Service Date. Change from 5/1/2016 6/1/2020 | 09TPIT0011 | Cagnon to Hillcountry - 345kV 2nd Circuit | Build second 345 kV line from Cagnon to Hill Country. The circuit will be installed on existing transmission structures |  |  | CPS | Blake Williams | T-0053 | 2020-06-01 |  | 345 | 19.5 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5056 5211 | N |  | There are no transformers associated with this project
Old Project | Change in Service Date. Change from 5/1/2016 6/1/2020 | 09TPIT0012 | Hill Country to Skyline - 345 kV 2nd Circuit | Build second 345 kV line from Hillcountry to Skyline. The second circuit will be installed on existing transmission structures |  |  | CPS | Blake Williams | T-0052 | 2020-06-01 |  | 345 | 11 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5211 5371 | N |  | There are no transformers associated with this project

## TPITCompletedNoCost08012008
AUGUST BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) COMPLETED PROJECTS As Of 08/01/2008
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) | Associated Projects (project number) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (TSP Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Transformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | Location County (Start If Line) | End Location If Line County | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers ( CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Requested Additional Information | Other
09TPIT0078 | Loma Alta 138-kV Substation | Facilitate substation for a new 138/12.5-kV transformer | The Load has been installed instead on the 69-kV Bus. The substation upgrade to 138kV portion was part of another project. |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-06-02 | 2008-07-31 | 138 | 0 | 0 | 28 | 0 | CAMERON |  |  |  |  | 5943 | Y
08TPIT0114 | Plastipak 138 kV new substation | New load serving |  |  | GARLAND |  |  | 2008-07-31 | 2008-07-31 | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 808 | Y
08TPIT0115 | Plastipak-Fairdale 138 kV line | Line upgrade |  |  | GARLAND |  |  | 2008-07-31 | 2008-07-31 | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  |  |  |  | 808, 805 | Y
08TPIT0160 | Greens Bayou - Normandy Tap ckt.77 | Verified conductors clearance to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-07-30 | 2008-07-30 | 138 | 0 | 8.95 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40716, 41171 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0195 | Texas Gulf-New Gulf tap ckt.04 | Verified conductors clearance to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-12-01 | 2008-07-15 | 138 | 0 | 0 | 0 | 0 | WHARTON | WHARTON |  |  |  | 43340, 43011 | Y |  | 1) No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2) IDEV reflects change in project in-service date.
08TPIT0118 | South Lane City - New Gulf tap - Texas Gulf ckt.60 | Raised conductors to increase thermal ratings to 90/120deg C. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-07-30 | 2008-07-15 | 138 | 0 | 10.56 | 0 | 0 | WHARTON | WHARTON |  |  |  | 43190, 43012, 43340 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
08TPIT0076 | Jack Creek (Formally Kurten Switch) 138 kV Double Circuit to Tabor | Construct a double circuit 138-kV line from Jack Creek through Kurten into Tabor; break the Dansby to Steephollow 138-kV line so that the portion to Steephollow ties into Tabor and the portion to Dansby ties into Kurten |  | 07TPIT0133, 07TPIT0134, 07TPIT0020, 08TPIT0075, 08TPIT0076 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2008-09-01 | 2008-07-08 | 138 | 6 | 8 | 0 | 0 | BRAZOS | BRAZOS | 2005-10-01 | 2005-11-01 | 2006-01-01 | 32859, 32870, 32879, 32881, 32882 | Y |  | There were no new transformers added with this project. The transformers are covered under 08TPIT0075, 07TPIT0134, 07TPIT0133
07TPIT0134 | Tabor Substation Upgrade | Install 6 Breaker 138kV Ring, Install 7 Breaker 69kV Ring, 138/69 150 MVA Auto |  | 07TPIT0133, 07TPIT0134, 07TPIT0020, 08TPIT0075, 08TPIT0076 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2008-05-01 | 2008-07-08 | 138 | 0 | 0 | 150 | 0 | BRAZOS |  | 2005-10-01 | 2005-11-01 | 2006-01-01 | 32870, 32882 | Y |  | New transmission lines installed are covered under 08TPIT0076.
06TPIT0165 | MVEC W. Edinburg-MVEC Palmhurst | Rebuild 138kV line from W. Edinburg to Palmhurst Substations | Material Issues | 04TPTI0025 | MVEC | Loretta C. Gallaga (956) 514-1289 lgallaga@stec.org | 791294 | 2008-12-08 | 2008-07-08 | 138 | 0 | 3.5 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
08TPIT0208 | TXDOT FM88 | Relocate 138kV line from MVEC Weslaco to AEP Weslaco Switch |  | 08TPIT0207 | MVEC | Loretta C. Gallaga (956) 514-1289 lgallaga@stec.org | 1189902 | 2008-09-08 | 2008-07-08 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | N |  | TXDOT Project to relocate line due to road widening. The line did not change.
08TPIT0166 | Texas City 69F Reroute | Reroute 1.4 miles of 69 kV transmission line to outside of BP's Texas City Refinery | Construction has started for this project |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2008-07-08 | 2008-07-08 | 69 | 0 | 1.4 | 0 | 0 | GALVESTON | GALVESTON |  |  |  |  | Y
07TPIT0065 | Gainesville - Muenster 69 kV line and Muenster 69 kV capacitors | Upgrade existing 69 kV line and install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R186-WAC | 2008-08-15 | 2008-07-01 | 69 | 0 | 13.84 | 0 | 18.4 | COOKE | MONTAGUE |  |  |  | 1709, 1712, 1716 | Y
05TPIT0044 | Asherton, add 14.4 MVAR cap on 138kV & 1-14.4 MVAR Cap on 69 kV | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | In Service | AEP GROUP 290 | AEP/TCC | Brian Johnson 918-599-2653 | 1451 | 2008-05-08 | 2008-06-30 | 138 | 0 | 0 | 0 | 28.8 | DIMMIT | [5 empty] | Y
06TPIT0015 | Airline to Naval Base, rebuild 69 kV Line | Rebuild Airline to Naval Base 69 kV transmission line from 477 MCM to 795 ACSR |  | AEP GROUP 029 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 3, LCRA#1003909 | 2008-06-15 | 2008-06-27 | 69 | 0 | 8 | 0 | 0 | NUECES | NUECES |  |  |  |  | Y
08TPIT0119 | East Bernard - Orchard - Fort Bend ckt.60 | Reconductored 138kV ckt.60 East Bernard to Fort Bend and upgraded substations limiting equipment to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-06-30 | 2008-06-24 | 138 | 0 | 18.33 | 0 | 0 | WHARTON | FORT BEND |  |  |  | 44190, 44540, 44300 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added.
08TPIT0195 | Bandera - Add 69kV Breaker | Add 69kV Breaker to Bandera 69kV Bus |  |  | Bandera Electric | Brian D. Bartos (830) 796-6074 b.bartos@banderaelectric.com | 115770 | 2008-06-08 | 2008-06-11 | 69 | 0 | 0 | 0 | 0 | BANDERA | BANDERA |  |  |  |  | Y
08TPIT0075 | Jack Creek (Formally Kurten Switch) 138 kV (4) Breaker Ring | Install (4) Breaker ring to accept Kurten Line, Tabor Line, 600 MVA 345/138 Auto |  | 07TPIT0133, 07TPIT0134, 07TPIT0020, 08TPIT0075, 08TPIT0076 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2008-05-01 | 2008-06-08 | 345 | 0 | 0 | 600 | 0 | BRAZOS |  | 2005-10-01 | 2005-11-01 | 2006-01-01 | 32859 | Y |  | New transmission lines installed are covered under 08TPIT0076.
07TPIT0133 | Kurten Substation Upgrade to 138kV | Install (1) Breaker to accept Jack Creek Line and Dansby Line |  | 07TPIT0133, 07TPIT0134, 07TPIT0020, 08TPIT0075, 08TPIT0076 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com |  | 2008-05-01 | 2008-06-08 | 138 | 0 | 0 | 0 | 0 | BRAZOS |  | 2005-10-01 | 2005-11-01 | 2006-01-01 | 32881 | Y |  | New transmission lines installed are covered under 08TPIT0076.
08TPIT0198 | Praxair Texas City #2 Station- TNMP 69-A Tap | TNMP will tap its existing 69kV line along SH146 to provide service to Praxair Texas City #2 Station | Line construction has been completed. Working on SCADA and Meter install. |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com |  | 2008-05-08 | 2008-06-08 | 69 | 0 | 0 | 60 | 0 | GALVESTON | GALVESTON |  |  |  | 39345, 39346 | Y
07TPIT0135 | Abilene Elm Creek to Abilene Shelton Street, Rebuild 69 kV line | Re-build 2.62 miles Abilene Elm Creek to Shelton 69 kV line @ 795 ACSS | In Service | AEP GROUP 341 | AEP/TNC | John Pulay 918-599-2653 | 1989 | 2008-06-30 | 2008-06-02 | 69 | 0 | 2.62 | 0 | 0 | TAYLOR | TAYLOR |  |  |  |  | Y
05TPIT0021 | Copperas Cove - Ding Dong (BEC) 138 kV line (Oncor Electric Delivery portion) | Construct 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R036A-WAC | 2008-07-01 | 2008-06-01 | 138 | 15.7 | 0 | 0 | 0 | CORYELL | BELL |  |  |  | 3630, 115, 3628, 3630 | Y
08TPIT0148 | Eskota Switching Station | Install 138 kV breaker to connect new wind farm |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R806-E | 2008-07-01 | 2008-06-01 | 138 | 0 | 0 | 0 | 0 | HOWARD |  |  |  |  | 1030, 1058, 1029 | Y
06TPIT0097 | Walnut 69 kV to 138 kV voltage conversion | Converts voltage for the substation |  |  | GARLAND |  |  | 2008-05-31 | 2008-05-31 | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 823 | Y
07TPIT0247 | Hillje 69 kV Substation | Construct Hillje Substation in the 69 kV line between Round Mott Switch and Louise. | In Service |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2008-05-31 | 2008-05-31 | 69 | 0 | 0 | 5 | 0 | WHARTON |  | N/A |  |  | 5532 | Y
05TPIT0143 | Weslaco SS, add 2-43.2 MVAR capacitor, cut-in Pharr to Harlingen SS 138 kV Line | Install capacitor banks at various locations in the East Valley area | In Service | AEP GROUP 293 | AEP/TCC | Rich Haley 918-599-2653 | 1648 | 2008-09-30 | 2008-05-30 | 138 | 0 | 0 | 0 | 86.4 | CAMERON | [5 empty] | Y
08TPIT0191 | Olmito, Construct 138 kV Distribution Substation | Olmito: Construct a new substation with cut-in, between Military Highway and Palo Alto 138kV line | In Service | AEP GROUP 255 | AEP/TCC | Rich Haley 918-599-2653 |  | 2008-08-29 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
08TPIT0192 | Military Highway to Palo Alto 138kV line, cut-in Olmito at 138kV | Olmito: Construct a new substation with cut-in, between Military Highway and Palo Alto 138kV line | In Service | AEP GROUP 255 | AEP/TCC | Rich Haley 918-599-2653 |  | 2008-08-29 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
07TPIT0162 | S.R. Bertron - Fairmont ckt.06 | Raised conductors and partially reconductored ckt.06 to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-05-31 | 2008-05-30 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 41400, 41310, 41631, 42610 | Y |  | No transformer capacity to be added.
06TPIT0095 | Walnut-Fairdale line 69 kV to 138 kV voltage conversion | Converts voltage for the line |  |  | GARLAND |  |  | 2008-05-30 | 2008-05-30 | 138 | 0 | 1.92 | 0 | 0 | DALLAS |  |  |  |  | 823, 803 | Y
06TPIT0024 | Seaton - Poage 69 kV line | Upgrade existing 69 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R045-WAC | 2008-05-15 | 2008-05-30 | 69 | 0 | 11.9 | 0 | 0 | BELL | BELL |  |  |  | 131, 3635 | Y
07TPIT0075 | Add dynamic reactive device Phase 2 | Added dynamic reactive device at Crosby 138 kV bus | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-06-30 | 2008-05-23 | 138 | 0 | 0 | 0 | 140 | HARRIS | HARRIS | 2006-03-08 | 2006-07-12 | 2006-08-30 | 40392 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. IDEV reflects addition of the SVC model.
08TPIT0182 | Graham Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R542-WAF | 2008-05-01 | 2008-05-21 | 138 | 0 | 0 | 0 | 0 | YOUNG | [5 empty] | Y
06TPIT0245 | Bluff Creek, Install 1 - 57.6 Mvar Cap Bank | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | In Service | AEP GROUP 354 | AEP/TNC | Ashley Beasley 918-599-2653 | 2125 | 2008-05-15 | 2008-05-20 | 138 | 0 | 0 | 0 | 57.6 | TAYLOR | [5 empty] | Y
08TPIT0188 | Paul Davis Tap terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R695-WA & R800-WA | 2008-05-01 | 2008-05-20 | 138 | 0 | 0 | 0 | 0 | DAWSON | [5 empty] | Y
06TPIT0050 | Cagnon to Lytle - New 138 kV line | Build new 138 kV line from Cagnon to Lytle. This project has been broken out into 3 phases. Phase 1: Cagnon - TX Research (Dec07) Phase 2: TX Research - Lytle (May08) | 12 Step Public Review Caused Delay of Start | T-0072 | CPS | PM: Ulrich Skerhut 210-353-2923 | T-0011 | 2008-05-15 | 2008-05-16 | 138 | 21.7 | 0 | 0 | 0 | BEXAR | MEDINA |  |  |  | 5055 5083 5290 | Y |  | There are no transformers associated with this project
08TPIT0186 | Mustang Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R699-WA | 2008-05-01 | 2008-05-16 | 138 | 0 | 0 | 0 | 0 | ANDREWS | [5 empty] | Y
07TPIT0174 | Morris 138 kV, add 1-28.8 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In Service | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2040 | 2008-05-15 | 2008-05-15 | 138 | 0 | 0 | 0 | 28.8 | Val VERDE | Val VERDE |  |  |  |  | Y
06TPIT0228 | Athens load conversion and second 138 kV line | Convert load to 138 kV service and add second 138 kV source |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R369-WAC | 2008-05-01 | 2008-05-15 | 138 | 2 | 0 | 0 | 0 | HENDERSON | HENDERSON |  |  |  | 3239, 3238 | Y
08TPIT0139 | Longshore 345 kV Switching Station | Construct 345 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R682-WAC | 2008-05-15 | 2008-05-14 | 345 | 0 | 0.22 | 0 | 0 | HOWARD |  |  |  |  | 1030, 1058, 1029 | Y
09TPIT0028 | Goldthwaite | Upgrade the 138-69 kV 25 MVA auto-transformer (T1) at the Goldthwaite substation(7070) to 45 MVA. |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | Not yet assigned | 2008-06-29 | 2008-05-13 | 138 | 0 | 0 | 45 | 0 | MILLS |  |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0144 | Add dynamic reactive device Phase 1 | Added dynamic reactive device at Bellaire South 138 kV bus | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-06-30 | 2008-05-12 | 138 | 0 | 0 | 0 | 140 | HARRIS | HARRIS | 2006-03-08 | 2006-07-12 | 2006-08-30 | 47016 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. IDEV reflects addition of the SVC model.
06TPIT0054 | Rangerville, add 7.2 Mvar cap | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | In Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1324 | 2008-05-08 | 2008-05-08 | 69 | 0 | 0 | 0 | 7.2 | CAMERON | [5 empty] | Y
07TPIT0139 | Temple Pecan Creek - Lake Creek 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R408A-WA | 2008-06-01 | 2008-05-01 | 138 | 0 | 28.5 | 0 | 0 | BELL | MCLENNAN | 2007-04-23 | 2007-05-21 | N/A | 3410, 3420 | Y
07TPIT0241 | Drumright 138 kV Switching Station | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R671-WAC | 2008-05-31 | 2008-05-01 | 138 | 0 | 0 | 0 | 0 | GLASSCOCK |  |  |  |  | 1335, 1336, 1331, 1328 | Y
08TPIT0178 | China Grove Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R687-WA to R690-WA | 2008-05-01 | 2008-05-01 | 138 | 0 | 0 | 0 | 0 | MITCHELL | [5 empty] | Y
08TPIT0017 | Olney to Shannon Rebuild | Rebuild the existing Olney to Shannon 69KV line with 795 138KV construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-05-01 | 69 | 0 | 28.5 | 0 | 0 | YOUNG | CLAY |  |  |  | 788776772 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0185 | Leon Switch terminal equipment upgrade | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R541-E | 2008-05-01 | 2008-05-01 | 69 | 0 | 0 | 0 | 0 | EASTLAND | [5 empty] | Y
06TPIT0099 | Fairdale load 69 kV to 138 kV voltage conversion | Converts voltage for its load |  |  | GARLAND |  |  | 2008-04-30 | 2008-04-30 | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 803 | Y
08TPIT0141 | Manvel | Installed new 69kV 7.2 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-05-31 | 2008-04-30 | 69 | 0 | 0 | 0 | 7.2 | BRAZORIA | BRAZORIA |  |  |  | 44440 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
04TPIT0148 | Walnut-Fairdale 69 kV line | Line upgrade |  |  | GARLAND |  |  | 2008-04-30 | 2008-04-30 | 69 | 0 | 2 | 0 | 0 | DALLAS |  |  |  |  | 823, 803 | Y
06TPIT0110 | Hidalgo to S McAllen, upgrade 69 kV line | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substatio | In Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1315 | 2008-06-30 | 2008-04-18 | 138 | 0 | 3.7 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
06TPIT0132 | Hidalgo, upgrade 2 transformers & distribution equipment | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | In Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1707 | 2008-05-31 | 2008-04-18 | 138 | 0 | 0 | 0 | 0 | HIDALGO | [5 empty] | Y
08TPIT0143 | Lampasas-Adamsville-Evant | Upgrade the Lampasas(7064)-Adamsville(7066)-Evant(7068) 138 kV transmission line (T-128) from 4/0 ACSR (84 MVA) to 795 ACSR (220 MVA |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2008-06-30 | 2008-04-15 | 138 | 0 | 26 | 0 | 0 | LAMPASAS | CORYELL | 2007-02-19 | 2007-03-12 | N/A | SEE PROJECT DESCRIPTION | Y
08TPIT0046 | Nolanville - Harker Heights 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R050-WAC | 2008-05-15 | 2008-04-15 | 138 | 0 | 7 | 0 | 0 | BELL | BELL |  |  |  | 3617, 3618 | Y
07TPIT0154 | Putnam, Replace existing 69/138 kV Autotransformer | Putnam, replace 69/138 kV Autotransformer with 90 MVA | In Service | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2147 | 2008-04-30 | 2008-04-11 | 138 | 0 | 0 | 90 | 0 | CALLAHAN | [5 empty] | Y
09TPIT0089 | Waterport - Loma Alta 138-kV Circuit | Add a new 138-kV circuit to Loma Alta Substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-04-11 | 2008-04-11 | 138 | 0 | 4.29 | 0 | 0 | CAMERON |  |  |  |  | 59450, 5962 | Y
08TPIT0100 | Twin Oak circuit breakers | Install 345 kV circuit breakers to connect a new power plant |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R498-WA | 2008-06-01 | 2008-04-08 | 345 | 0 | 0 | 0 | 0 | ROBERTSON |  |  |  |  | 3400, 13691, 13692 | Y
08TPIT0189 | Benbrook Switch terminal equipment upgrade | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5120-WAF | 2008-05-01 | 2008-04-07 | 345 | 0 | 0 | 0 | 0 | TARRANT | [5 empty] | Y
08TPIT0183 | Key Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R698-WAF & R805-WAF | 2008-05-01 | 2008-04-05 | 138 | 0 | 0 | 0 | 0 | DAWSON | [5 empty] | Y
08TPIT0197 | Reconfigure ckt.03 EXXON - S.R. Bertron and ckt.88 Baytown - Rohmas substation. | Reconfigured ckt.03 EXXON - S.R. Bertron and ckt.88 Baytown - Rohmas substation to create two new circuits ckt.03 EXXON - Baytown and ckt.88 S.R. Bertron - Rohmas to ensure reliable service to the customers in the Baytown area. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-04-10 | 2008-04-03 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40570, 40170, 41405, 41350 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0121 | Morgan Creek 345/138 kV autotransformer | Install third 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R608-WAF | 2007-12-01 | 2008-04-01 | 345 | 0 | 0 | 300 | 0 | MITCHELL |  | 2006-09-20 | 2006-10-18 | N/A | 1030, 1032 | Y
09TPIT0034 | Bunker to Hood Rebuild | Rebuild existing Bunker to Hood 138kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-04-01 | 138 | 0 | 9.1 | 0 | 0 | HOOD | HOOD |  |  |  | 363352306 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
10TPIT0014 | Olney Auto | Increase 138/69 autotransformer capacity at Olney |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-06-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | YOUNT |  |  |  |  | 788787 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
08TPIT0199 | Capote Substation (7598)- Convert to 138 kV Operation | 138 kV conversion involves switching, relocation of jumpers and other minor work. |  |  | GVEC | Barry Kremling (830) 857-1200 bkremling@GVEC.org |  | 2008-04-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | GUADALUPE |  |  |  |  | See Project Title | Y
08TPIT0180 | Exxon Sharon Ridge Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R802-WA & R803-WA | 2008-05-01 | 2008-04-01 | 138 | 0 | 0 | 0 | 0 | SCURRY | [5 empty] | Y
09TPIT0017 | Pancake to Gatesville Rebuild | Rebuild existing Pancake to Gatesville with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-04-01 | 69 | 0 | 4 | 0 | 0 | CORYELL | CORYELL |  |  |  | 157158 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0039 | Hasse to Downing Upgrade/Rebuild | Rebuild or Upgrade existing Hasse to Downing line with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-04-01 | 69 | 0 | 7.3 | 0 | 0 | COMANCHE | COMANCHE |  |  |  | 277281 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0040 | Jack Creek Sub: new 345 sub near Kurten | New 345 KV sub with one 600 MVA 345-138 autotransformer | On Schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T06012 | 2008-05-07 | 2008-03-31 | 345 | 0 | 0 | 600 | 0 | BRAZOS |  | 2005-09-01 | 2005-11-01 | 2006-01-01 | ? | Y
08TPIT0113 | Flatonia Autotransformer Addition | Add a new 138-69 kV 45 MVA autotransformer at the Flatonia substation (7248). |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2008-06-30 | 2008-03-31 | 138 | 0 | 0 | 30 | 0 | FAYETTE |  |  |  |  | SEE PROJECT DESCRIPTION | Y
07TPIT0085 | Hi-Line to Hidalgo, upgrade 69 kV line to 138 kV | Add Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Stewart Road 69 kV to 138 kV and convert Hidalgo and Dyer substations to 138 kV | In Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1792 | 2008-03-31 | 2008-03-31 | 69 | 0 | 2 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
08TPIT0181 | Gail Substation terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R801-WAF & R804-WAF | 2008-05-01 | 2008-03-29 | 138 | 0 | 0 | 0 | 0 | BORDEN | [5 empty] | Y
08TPIT0159 | Satsuma - Gertie ckt.76 | Verified conductors clearance to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-05-31 | 2008-03-26 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 46302, 45802 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0117 | Seaway Teague - W. Fairfield 138 kV line | Upgrade existing 138 kV line |  | R478 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R478A-WAC | 2008-05-15 | 2008-03-25 | 138 | 0 | 13 | 0 | 0 | FREESTONE | FREESTONE | 2007-02-13 | 2007-03-06 | N/A | 3392, 3501, 3503 | Y
08TPIT0194 | Lane City: Upgrade Series Reactor to 2000 Amps | Upgrade Lane City substation bus and series reactors | In Service | AEP GROUP 387 | AEP/TCC | Dave Goetz 918-599-2653 | 2234 | 2008-03-08 | 2008-03-24 | 138 | 0 | 0 | 0 | 0 | WHARTON | [5 empty] | Y
08TPIT0201 | Disconnect and remove Simson 69kV Substation from CenterPoint Energy's system. | Disconnected and removed customer owned Simson substation from CNP's ckt.23 Deepwater - S.R. Bertron. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2008-03-15 | 2008-03-18 | 69 | 0.02 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40470, 41460,41415 | Y |  | 1)_No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. 2)_PSS/E bus #41460 will be removed from the base cases.
07TPIT0114 | E. Mesquite - W. Mesquite 138 kV line | Upgrade existing 138 kV line | Line work was completed on 12/6/2007, but E. Mesquite terminal upgrade will not be completed until 4/30/2008. | M4038 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M4041-WACF | 2008-04-30 | 2008-03-14 | 138 | 0 | 2.7 | 0 | 0 | DALLAS | DALLAS |  |  |  | 2754, 2756 | Y
00TPITno18 | Waterport 138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 0 | 28 | 0 | CAMERON |  |  |  |  | 59450 | Y |  | `
00TPITno00 | Airport - Waterport 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 8.8 | 0 | 0 | CAMERON |  |  |  |  | 59460, 59450 | Y
07TPIT0105 | Airport Substation138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2008-03-09 | 2008-03-09 | 138 | 0 | 0 | 28 | 0 | CAMERON |  |  |  |  | 59460 | Y |  | The existing 138/69-kV and a 69/12.5-kV transformers will remain.
08TPIT0036 | Austrop to Decker Reconductor Last Three Spans of the circuit. | Reconductor the remaining three spans of Circuit 921 (Austrop to Decker) coming into the Decker Plant switchyard with triple bundle 795 ACSR Drake conductors. | Comments: The three spans have been replaced but the rerating will not be done until the breakers are changed out before Summer 2009. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | PLAN_117_P003 | 2008-03-01 | 2008-03-08 | 138 | 0 | 0.58 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9187, 7328 | Y
08TPIT0187 | Olefin Switch terminal equipment upgrade | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R684-WA - R686-WA | 2008-05-01 | 2008-03-05 | 138 | 0 | 0 | 0 | 0 | ECTOR | [5 empty] | Y
06TPIT0104 | Convert Circuit 822 (Burleson to Cardinal Lane) and 824 (Cardinal Lane to Seaholm) from 69kV to 138kV. | Convert the 69kV circuit 822 (Burleson to Cardinal Lane) and Circuit 824 (Cardinal Lane to Seaholm) to 138kV capable of carrying at least 3000 Amps. | The reconductoring of both Circuit 822 and 824 is now complete. They will still operate at the 69kV level and switch to 138kV after the new Cardinal Lane substation completion in June 2008. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_4268 3230_117_4269 3230_117_4274 3230_117_4275 | 2008-02-08 | 2008-03-01 | 138 | 0 | 5.7 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | 9120,9179,9299, 9132 | Y
08TPIT0016 | Covington to Grandview Upgrade or Rebuild | Rebuild Covington to Grandview |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-03-01 | 138 | 0 | 9.9 | 0 | 0 | JOHNSON | JOHNSON |  |  |  | 444443436 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0155 | Putnam, Add 138 kV phase shift transformer | Putnam, Add 138 kV phase shift transformer on the Abilene South to Putnam 138 kV line | In Service | AEP GROUP 354 | AEP/TNC | Dave Goetz 918-599-2653 | 2148 | 2008-03-10 | 2008-02-28 | 138 | 0 | 0 | 150 | 0 | CALLAHAN | [5 empty] | Y
05TPIT0077 | North Padre to Mustang Island, rebuild 69 kV line | Rebuild North Padre (8856) to Port Aransas (8436) 69 kV transmission line from 4/0 ACSR to 795 ACSS |  | AEP GROUP 029 | LCRA TSC / AEP | Julius Horvath (512) 369-4104 julius.horvath@lcra.org | 140, LCRA#1003910 | 2008-02-25 | 2008-02-25 | 69 | 0 | 6.7 | 0 | 0 | NUECES | NUECES |  |  |  | SEE PROJECT DESCRIPTION | Y
08TPIT0161 | Tomball - Tomball Distribution Tap ckt.81 | Verified equipment rating at Tomball to increase emergency rating. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2193 |  | 2008-05-31 | 2008-02-15 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 46510, 46512 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
06TPIT0170 | College Station Post Oak Substation to Southwood Valley Substation Line Reconducter | Reconducter College Station Post Oak substation to Southwood Valley Substation with 1033 ACSS | Material Deliveries |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2008-02-08 | 2008-02-08 | 138 | 0 | 3 | 0 | 0 | BRAZOS | BRAZOS |  |  |  |  | Y |  | Transmission Rebuilt on Line
05TPIT0256 | College Station Switch Station to Post Oak Substation Line Reconducter | Reconductor College Station Switch Station to Post Oak Station with 1033 ACSS | Material Deliveries |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2008-02-07 | 2008-02-08 | 138 | 0 | 1.7 | 0 | 0 | BRAZOS | BRAZOS |  |  |  |  | Y |  | Transmission Rebuilt on Line
07TPIT0127 | Bandera to Hamilton Wolfe to Med. Center - Reconductor | Reconductor existing 138 kV line with 1-1272 ACSR. Phase 1: Med. Center to Hamilton Wolfe (Dec 07) Phase 2: Bandera to Hamilton Wolfe (Feb 08) | Distribution Conflicts & Budget Delays | T-0084 | CPS | PM: Ulrich Skerhut 210-353-2923 | T-0084 | 2008-02-08 | 2008-02-08 | 138 | 0 | 1.7 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5020 5300 5187 | Y |  | There are no transformers associated with this project
06TPIT0059 | Stewart Road, build 138/69 kV SS with 2-28.8 MVar caps | Construct a new Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | In Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1318 | 2008-01-25 | 2008-01-25 | 138 | 0 | 0 | 93 | 57.6 | HIDALGO | [5 empty] | Y
06TPIT0120 | Stewart Rd to Hi-Line , build 138/69 kV double circuit line | Construct a new Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | In Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1319 | 2008-01-25 | 2008-01-25 | 138 | 3 | 0 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
07TPIT0101 | Hi-Line to Stewart Rd tap, upgrade 69 kV line to 138 kV | Add Stewart Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Stewart Road 69 kV to 138 kV and convert Hidalgo and Dyer substations to 138 kV | In-Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1791 | 2008-05-01 | 2008-01-25 | 69 | 0 | 3 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
05TPIT0075 | San Diego, add 69 kV breakers and 1 - 7.2 MVAR 69 kV cap | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2043 | 2007-11-30 | 2008-01-25 | 69 | 0 | 0 | 0 | 7.2 | JIM WELLS | [5 empty] | Y
08TPIT0144 | Glasscock Capacitor Bank Addition | Add a 138 kV 31.2 MVAR capacitor bank at Glasscock (7523). |  |  | LCRA TSC | Julius Horvath (512) 369-4104 julius.horvath@lcra.org |  | 2008-06-30 | 2008-01-24 | 138 | 0 | 0 | 0 | 31.2 | WILLIAMSON |  |  |  |  | SEE PROJECT DESCRIPTION | Y
07TPIT0179 | Paducah: Add a 20 MVAR 138 KV Shunt Reactor | Replace 69/138 kV auto at Paducah with an 90 MVA 69/138 kV with LTC and add 20 MVAR 138 kV shunt reactor | In-Service | AEP GROUP 289 | AEP/TNC | Brett Madison 918-599-2653 | 1994 | 2008-01-18 | 2008-01-18 | 138 | 0 | 0 | 0 | -20 | COTTLE | [5 empty] | Y
08TPIT0170 | Jewett - Seaway Teague 138 kV line | Upgrade existing 138 kV line |  | R478A | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R478-WAF | 2008-05-01 | 2008-01-16 | 138 | 0 | 10.75 | 0 | 0 | LEON | FREESTONE | 2007-02-13 | 2007-03-06 | N/A |  | Y
12TPIT0001 | Texas Research Park - New Substation | Install new 138kV substation. May be part of T-0049 or T-0072. |  | S-0225 | CPS | PM: Janna Junkin 210-353-2524 | T-0072 | 2007-12-14 | 2008-01-09 | 138 | 0.1 | 0 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5430 | Y |  | There are no transformers associated with this project
08TPIT0064 | Hood to Decordova Rebuild | Rebuild existing Hood to Decordova 138kv line | Brazos to rebuild TXUED portion of line |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2008-01-01 | 138 | 0 | 2.2 | 0 | 0 | HOOD | HOOD |  |  |  | 2277363 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0182 | Hilltop Lakes to Petteway Rebuild | Rebuild the existing Hilltop Lakes Switch to Petteway 69KV line with 795 and 138KV construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-01-01 | 2008-01-01 | 69 | 0 | 8.28 | 0 | 0 | ROBERTSON | ROBERTSON |  |  |  | 43,93 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0033 | Gatesville to Fort Gates Switch Rebuild | Rebuild existiing Gatesville to Fort Gates Switch 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2009-06-01 | 2008-01-01 | 69 | 0 | 7.5 | 0 | 0 | CORYELL | CORYELL |  |  |  | 157250 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0256 | Bethel Capacitor Bank | Install 7.2 mvar of capacitors at Bethel |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2008-01-01 | 69 | 0 | 0 | 0 | 7.2 | ELLIS |  |  |  |  | 204 | Y |  | There are no circuit breakers, transmission line or transformer capacity associated with this project
07TPIT0215 | Mulberry Creek 345 kV terminal equipment | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R634-WAF, R635-WAF | 2007-05-01 | 2007-12-31 | 345 | 0 | 0 | 0 | 0 | TAYLOR |  |  |  |  | 6230, 6235 | Y
07TPIT0264 | County Road 101, Install tap structures with switches | Interconnect Enterprise's Load to AEP's Permian Basin to Barrilla 138 kV line | In-Service | AEP GROUP 393 | AEP/TNMP | Brett Madison 918-599-2653 | 2270 | 2007-12-31 | 2007-12-31 | 138 | 0 | 0 | 0 | 0 | REEVES | [5 empty] | Y
07TPIT0168 | Burleson 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3044-WAF | 2007-12-15 | 2007-12-31 | 138 | 0 | 0 | 0 | 55.2 | TARRANT |  |  |  |  | 2209 | Y
07TPIT0144 | Wharton - South Lane ckt.60 | Reconductored 138kV ckt.60 Wharton to South Lane and upgraded limiting equipment at South Lane. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-12-31 | 2007-12-28 | 138 | 0 | 10.88 | 0 | 0 | WHARTON | WHARTON |  |  |  | 43570, 44131, 42985, 43190 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project. 2)_No transformer capacity to be added.
08TPIT0091 | Lon Hill 138 kV, add 2-57.6 MVAR Cap Banks | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2039 | 2007-12-01 | 2007-12-27 | 138 | 0 | 0 | 0 | 115.2 | Val VERDE | Val VERDE |  |  |  |  | Y
07TPIT0239 | Tonkawa 345 kV Switching Station | Construct 345 kV switching station |  | R677B | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R677-WAF | 2007-12-01 | 2007-12-21 | 345 | 0 | 0 | 0 | 0 | SCURRY |  |  |  |  | 1030, 1430, 1048, 1049, 1057 | Y
07TPIT0145 | Wharton - Caney - East Bernard ckt.60 | Reconductored 138kV ckt.60 Wharton to East Bernard and upgraded limiting equipment at East Bernard to increase thermal ratings. Caney loop upgrade was excluded from this project. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-12-31 | 2007-12-21 | 138 | 0 | 14.9 | 0 | 0 | WHARTON | WHARTON |  |  |  | 43570, 44130, 44190 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project. 2)_No transformer capacity to be added.
07TPIT0167 | Mexia 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R479-WAF | 2007-12-15 | 2007-12-21 | 138 | 0 | 0 | 0 | 18.4 | LIMESTONE |  |  |  |  | 3631, 3632 | Y
06TPIT0072 | McQueeney-New Berlin | Upgrade the 8.2-mile McQueeney(7606)-New Berlin(7612) 4/0 ACSR 69-kV transmission line to 795 ACSR 138-kV. |  |  | GVEC | David Tomczyszyn (830) 857-1110 dtomczyszyn@GVEC.org |  | 2007-11-30 | 2007-12-20 | 138 | 0 | 8.2 | 70 | 0 | GUADALUPE |  |  |  |  | SEE PROJECT DESCRIPTION | Y | SEE PROJECT DESCRIPTION
09TPIT0113 | Beeville, add +/-10 MVAR DRCS | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 1773 | 2007-12-10 | 2007-12-20 | 69 | 0 | 0 | 0 | 40 | BEE | [5 empty] | Y
06TPIT0231 | Ferris 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3028-WAF | 2007-12-15 | 2007-12-20 | 69 | 0 | 0 | 0 | 18.4 | ELLIS |  |  |  |  | 2342 | Y
06TPIT0088 | North Herty - Lufkin East 138 kV line | Upgrade existing 138 kV line to operate at an elevated conductor temperature |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R338-WACF | 2008-05-01 | 2007-12-19 | 138 | 0 | 9.47 | 0 | 0 | ANGELINA | ANGELINA |  |  |  | 3319, 3326 | Y
06TPIT0039 | DeLeon 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R107-WAF | 2007-12-15 | 2007-12-18 | 69 | 0 | 0 | 0 | 9.2 | COMANCHE |  |  |  |  | 1633 | Y
06TPIT0234 | Oak Creek 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R283-WAF | 2007-12-15 | 2007-12-18 | 69 | 0 | 0 | 0 | 9.2 | NOLAN |  |  |  |  | 1406 | Y
07TPIT0066 | Itasca 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R452-WAF | 2007-12-15 | 2007-12-18 | 69 | 0 | 0 | 0 | 9.2 | HILL |  |  |  |  | 3532 | Y
07TPIT0214 | Morgan Creek 345 kV terminal equipment | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R630-WAF, R631-WAF, R632-WAF | 2007-12-01 | 2007-12-17 | 345 | 0 | 0 | 0 | 0 | MITCHELL |  |  |  |  | 1030 | Y
07TPIT0062 | Cleburne W. 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M338-WAF | 2007-12-15 | 2007-12-17 | 138 | 0 | 0 | 0 | 18.4 | JOHNSON |  |  |  |  | 2291 | Y
07TPIT0240 | Stanton East 138 kV Switching Station | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R675-WAF | 2007-12-01 | 2007-12-14 | 138 | 0 | 0 | 0 | 0 | MARTIN |  |  |  |  | 1326, 1023, 1324 | Y
07TPIT0245 | Convert Caney to a double tap substation | Converted Caney substation to a double tap configuration to improve reliability of the service provided to the customer and alleviated need for substation upgrade. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-12-31 | 2007-12-11 | 138 | 0.5 | 0 | 0 | 0 | WHARTON | WHARTON |  |  |  | 44130, 44131 | Y |  | 1)_Part of Colorado Bend Energy Center generating facility interconnection project, Phase II. 2)_No transformer capacity to be added.
07TPIT0228 | Odessa EHV - Odessa 2 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R208-WACF | 2007-12-15 | 2007-12-11 | 138 | 0 | 2.3 | 0 | 0 | ECTOR | ECTOR |  |  |  | 1027, 1126 | Y
07TPIT0229 | Shamburger 345/138 kV autotransformer replacement | Replace existing 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R392-WAF | 2007-12-15 | 2007-12-07 | 345 | 0 | 0 | 724 | 0 | SMITH |  | 2007-04-10 | 2007-05-02 | N/A | 3103, 3104 | Y
07TPIT0165 | Lavon Switch 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M3046-WA | 2007-11-15 | 2007-12-07 | 138 | 0 | 0 | 0 | 110.4 | COLLIN |  |  |  |  | 2694 | Y
07TPIT0244 | Vega 138 kV substation | Establish a new 138kV substation by cutting into the existing Ckt 928 (Barton - Patton Lane) | Comments- The substation was energized in December as planned. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | N/A | 2007-12-01 | 2007-12-01 | 138 | 0.1 | 0 | 50 | 0 | TRAVIS | TRAVIS |  |  |  | 9285 | Y
06TPIT0071 | Second Hawkins Auto | Install second auto at Hawkins for backup |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2007-12-01 | 138 | 0 | 0 | 40 | 0 | COOKE |  |  |  |  | 705707 | Y |  | There is no right of way, circuit miles,conductor type,structure type,reactive capability or circuit breakers associated with this project
08TPIT0038 | Granbury to Stephenville Rebuild | Rebuild existing Granbury to Stephenville 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2007-12-01 | 69 | 0 | 26.2 | 0 | 0 | ERATH | HOOD | 2006-10-25 | 2006-11-16 | N/A | 299303304305307 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0263 | Bellaire - Brays ckt.09 | Upgraded limiting equipment at Brays to increase thermal ratings. | In-Service | 08TPIT0156 | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-11-30 | 2007-11-30 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 47015, 47050 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored. Cost included in Project #08TPIT0156, Increase thermal rating of ckt.09 HOC to Brays.
09TPIT0080 | South Plant - Airport 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-12-03 | 2007-11-29 | 138 | 0 | 2.88 | 0 | 0 | CAMERON |  |  |  |  | 59500, 59460 | Y
09TPIT0079 | Sixth St - South Plant 138-kV Circuit | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-11-16 | 2007-11-28 | 138 | 0 | 2.7 | 0 | 0 | CAMERON |  |  |  |  | 59480, 59500 | Y
08TPIT0008 | Belton - South Harker Heights 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R449-WACF | 2007-12-15 | 2007-11-20 | 138 | 0 | 11.9 | 0 | 0 | BELL | BELL |  |  |  | 3610, 3633 | Y
07TPIT0235 | Nylon Tap - Olefin - General Tire 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R674-WACF | 2007-12-15 | 2007-11-20 | 138 | 0 | 1.4 | 0 | 0 | ECTOR | ECTOR |  |  |  | 1055, 1054, 1053 | Y
07TPIT0103 | Six Street 138-kV Substation | Convert Substation from 69-kV to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-11-16 | 2007-11-16 | 138 | 0 | 0 | 56 | 9.6 | CAMERON |  |  |  |  | 59480 | Y
07TPIT0106 | Power Plant - Sixth Street 138-kV Line | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-11-16 | 2007-11-16 | 138 | 0 | 2.63 | 0 | 0 | CAMERON |  |  |  |  | 59300, 59480 | Y
07TPIT0227 | Flat Creek - Lingleville - Stephenville 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R520B-WACF | 2007-12-07 | 2007-11-13 | 138 | 0 | 14.4 | 0 | 0 | ERATH | ERATH |  |  |  | 1640, 1641 | Y
07TPIT0237 | DeCordova - DeCordova Dam - Hood (BEC) 138 kV line (Oncor Electric Delivery section) | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M5130-WACF | 2007-11-15 | 2007-11-11 | 138 | 0 | 3.3 | 0 | 0 | HOOD | HOOD |  |  |  | 2277, 1891 | Y
06TPIT0069 | Picacho, add 138 kV SS with 1-28.8 MVAR capacitor bank | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | In-Service | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1550 | 2008-08-31 | 2007-11-10 | 138 | 0 | 0 | 0 | 28.8 | VAL VERDE | [5 empty] | Y
06TPIT0135 | Euless - Keller 138 kV line | Upgrade existing 138 kV line |  | M545 | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | M547-WACF | 2007-12-15 | 2007-11-02 | 138 | 0 | 28.8 | 0 | 0 | TARRANT | TARRANT |  |  |  | 565, 1957, 2016, 2026, 2027, 2029, 2034, 2035, 2037, 2038, 2050, 2051 | Y
07TPIT0109 | Midessa - Midland Airport 138 kV line upgrade | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R207-WACF | 2007-12-01 | 2007-11-02 | 138 | 0 | 7.2 | 0 | 0 | MIDLAND | MIDLAND |  |  |  | 1059, 1120 | Y
06TPIT0067 | Whitney to Covington Rebuild | Rebuild Whitney toCovington |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-11-01 | 2007-11-01 | 138 | 0 | 27.9 | 0 | 0 | BOSQUE | JOHNSON |  | 2003-12-01 | 2004-01-01 | 241444 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0057 | Hood - Spunky 138 Uprate or Rebuild | Uprate or rebuild with larger conductor the existing Hood to Spunky 138KV line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-12-01 | 2007-11-01 | 138 | 0 | 8.8 | 0 | 0 | HOOD | HOOD |  |  |  | 363356 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
09TPIT0026 | Upgrade Hasse 138/69 Autotransformer | Upgrade 40MVA 138/69KV auto at Hasse to 60 MVA |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2007-11-01 | 138 | 0 | 0 | 40 | 0 | COMANCHE |  |  |  |  | 277, 1649 | Y |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
06TPIT0227 | Lamesa 138 kV capacitor | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R274B-WAF | 2007-12-15 | 2007-10-26 | 138 | 0 | 0 | 0 | 18.4 | DAWSON |  |  |  |  | 1163 | Y
06TPIT0233 | North Emory (Formerly Liberty) 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R383-WAF | 2007-12-15 | 2007-10-26 | 138 | 0 | 0 | 0 | 18.4 | DELTA |  |  |  |  | 3171 | Y
07TPIT0254 | Matador: Install Breaker | Install Breaker/Upgrade Termination at Matador 69 kV station for IPP | In-Service | AEP GROUP 360 | AEP/TNC | Brett Madison 918-599-2653 | 2172 | 2007-09-30 | 2007-10-24 | 69 | 0 | 0 | 0 | 0 | MOTLEY | [5 empty] | Y
07TPIT0211 | Dollarhide 138 kV terminal equipment | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R639-WAF | 2007-05-01 | 2007-10-16 | 138 | 0 | 0 | 0 | 0 | WINKLER |  |  |  |  | 1149 | Y
05TPIT0257 | College Station Spring Creek Substation | Build new distibution substation in the College Station Switch Station to Greens Prairie Substation line | Weather delays |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2007-09-07 | 2007-10-07 | 138 | 2 | 0 | 50 | 0 | BRAZOS | BRAZOS |  |  |  |  | Y
07TPIT0088 | Sharyland HVDC Interconnect | Construct a 138 kV Transmission Line to implement a 150 MW High Voltage Direct Current Interconnection with Comision Federal De Electricidad. |  |  | SU | Mark E. Caskey, PE (956) 687-5600 mcaskey@su-power.com | PR.04.05067.CAP | 2007-09-22 | 2007-10-07 | 138 | 0.8 | 0 | 150 | 0 | HIDALGO | HIDALGO |  |  |  | 8824, 8825 | Y | PUCT Approved CCN Docket 28834
05TPIT0131 | Oak Hill 31.2 Mvar Capacitor bank | Install one 31.2 Mvar capacitor bank at Oak Hill substation. | Delay-Capacitor Contract Delay. |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_1443 | 2007-08-01 | 2007-10-01 | 138 | 0 | 0 | 0 | 31.2 | TRAVIS | TRAVIS |  |  |  | 9247 | Y
07TPIT0218 | Spraberry Switch 138 kV terminal equipment | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R637-WAF | 2007-05-01 | 2007-09-27 | 138 | 0 | 0 | 0 | 0 | MIDLAND |  |  |  |  | 1329 | Y
05TPIT0123 | Military Highway, add 2-57.6 MVAR capacitors | Install capacitor banks at various locations in the East Valley area | In-Service | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1646 | 2007-10-31 | 2007-08-29 | 138 | 0 | 0 | 0 | 115.2 | CAMERON | [5 empty] | Y
06TPIT0129 | Laredo, add 2-57.6 MVAr caps | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | In-Service | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1220 | 2007-05-01 | 2007-08-28 | 138 | 0 | 0 | 0 | 115.2 | WEBB | [5 empty] | Y
06TPIT0241 | Velasco to Freeport ckt.47 | Raised conductors and partially rebuilt ckt.47 to increase thermal ratings | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-08-15 | 2007-08-15 | 69 | 0 | 4.32 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 43370, 42640 | Y |  | No transformer capacity to be added.
06TPIT0242 | Velasco to Surfsi ckt.10 | Raised conductors and partially rebuilt ckt.10 to increase thermal ratings | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-08-15 | 2007-08-15 | 69 | 0 | 2.46 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 43370, 43310 | Y |  | No transformer capacity to be added.
06TPIT0243 | Freeport to Surfsi ckt.47 | Raised conductors and partially rebuilt ckt.47 to increase thermal ratings | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-08-15 | 2007-08-15 | 69 | 0 | 1.79 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 42640, 43310 | Y |  | 1)_Project cost included in Project # 07TPIT0142, Service to Freeport LNG. 2)_No transformer capacity to be added.
07TPIT0186 | Lamarque - West Galveston ckt.13 | Verifed conductors clearance to increase emergency rating to 72 MVA | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-08-15 | 2007-08-14 | 69 | 0 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  | 42860, 43410 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
06TPIT0053 | Rio Rico, add 10.8 Mvar cap | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substations | In-Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1323 | 2007-08-31 | 2007-08-09 | 69 | 0 | 0 | 0 | 10.8 | HIDALGO | [5 empty] | Y
07TPIT0079 | Hamilton, add +/-10 MVAR DRCS | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Brian Johnson 918-599-2653 | 1774 | 2007-08-01 | 2007-08-07 | 69 | 0 | 0 | 0 | 40 | UVALDE | [5 empty] | Y
07TPIT0128 | Bastrop West Capacitor Bank Addition | Install 138 kV, 31.2 MVAR shunt capacitor bank at Bastrop West(7555) |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2007-06-30 | 2007-08-02 | 138 | 0 | 0 | 0 | 31.2 | BASTROP |  |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0125 | Zacate Creek to Laredo Heights, upgrade 69 kV inner loop to 138kV | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | In-Service | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1301 | 2007-07-15 | 2007-08-01 | 138 | 0 | 1.8 | 0 | 0 | WEBB | WEBB |  |  |  |  | Y
05TPIT0087 | Laredo to Zacate Creek, upgrade 69 kV to 138 kV line | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | In-Service | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1302 | 2007-07-15 | 2007-08-01 | 138 | 0 | 2.61 | 0 | 0 | WEBB | WEBB |  |  |  |  | Y |  | Scope of this project includes 50% of the Laredo Plant Station costs for the new 138kV line terminals
05TPIT0186 | Zacate Creek, upgrade one transformer & distribution equipment | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | In-Service | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1704 | 2007-08-10 | 2007-08-01 | 138 | 0 | 0 | 40 | 0 | WEBB | [5 empty] | Y
06TPIT0164 | Laredo Heights, upgrade two transformers & distribution equipment | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Heights to 138 kV, convert Heights to 138 kV and transfer/convert Anna to 138 kV line | In-Service | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1996 | 2007-07-15 | 2007-08-01 | 138 | 0 | 0 | 80 | 0 | WEBB | [5 empty] | Y
08TPIT0019 | Leon Junction to Santa Fe Sw. Rebuild | Rebuild existing Leon Junction to Santa Fe Sw. with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-08-01 | 69 | 0 | 4.1 | 0 | 0 | CORYELL | CORYELL |  |  |  | 149145142 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
08TPIT0053 | WAP - Hillje ckt. | Built new 345 kV double circuit line from WA Parish to Hillje. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-07-31 | 2007-07-31 | 345 | 97.84 | 0 | 0 | 0 | FORT BEND | WHARTON | 2004-09-10 | 2004-11-01 | 2005-03-15 | 44000, 44330 | Y |  | No transformer capacity added.
07TPIT0173 | Three Rivers 138 kV, add 1-28.8 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In Service | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2041 | 2007-07-01 | 2007-07-31 | 138 | 0 | 0 | 0 | 28.8 | Val VERDE | Val VERDE |  |  |  |  | Y
07TPIT0171 | Sinton 69 kV, add 1-14.4 MVARCap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2033 | 2007-06-01 | 2007-07-28 | 69 | 0 | 0 | 0 | 14.4 | Val VERDE | Val VERDE |  |  |  |  | Y
06TPIT0149 | Beeville, add 2-14.4 Cap Banks | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 1773 | 2007-10-01 | 2007-07-23 | 69 | 0 | 0 | 0 | 40 | Val VERDE | [5 empty] | Y
04TPIT0025 | N. Edinburg to W. Edinburg, rebuild 138 kV line | Rebuild 138kV line from AEP N. Edinburg to MVEC W. Edinburg |  | 05TPIT0103 & 05TPIT0250 | MVEC | Loretta C. Gallaga (956) 463-1584 lgallaga@magicvalley.coop | 801145 | 2007-06-07 | 2007-07-05 | 138 | 0 | 4.6 | 0 | 0 | HIDALGO | HIDALGO | 2003-04-03 | 2003-06-06
07TPIT0190 | Magnolia Park - University ckt.70 | Upgrade limiting equipment at Magnolia Park and at University to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-09-01 | 2007-07-03 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 47700, 47751, 47750 | Y |  | No transformer capacity to be added and no transmission circuits to be built, rebuilt or reconductored.
07TPIT0187 | Galena - Gypsum tap ckt.20 | Verifed conductors clearance to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-07-03 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40611, 40751 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
05TPIT0167 | Palmhurst, upgrade second 69 kV distribution banks | Convert Moore Field and Palmhurst substations from 69 kV to 138 kV and connect to North Edinburg to Bates 138 kV line | In-Service | AEP GROUP 292 | AEP/TCC | Bill Eakin 918-599-2653 | 845 | 2007-07-15 | 2007-07-02 | 138 | 0 | 0 | 90 | 0 | HIDALGO | [5 empty] | Y
05TPIT0084 | Falcon SS, add 14.4 MVAR capacitor | Install Capacitor Banks at Bates, Falcon, Garza, and Rio Grande City. | In-Service | AEP GROUP 292 | AEP/TCC | Bill Eakin 918-599-2653 | 1532 | 2007-06-15 | 2007-07-01 | 138 | 0 | 0 | 0 | 14.4 | STARR | [5 empty] | Y
07TPIT0181 | Navo Capacitor Bank | Install 35mvar 138kv capacitors at Navo | No room at Panther Creek to add cap bank |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-07-01 | 138 | 0 | 0 | 0 | 37.5 | DENTON |  |  |  |  | 662649 | Y |  | There are no circuit breakers, transmission line or transformer capacity associated with this project
06TPIT0224 | Lehigh | Construct a new 138 kV substation, Lehigh, near the existing Centex(7508) substation. Install a 138/69 kV 45 MVA auto-transformer at the Lehigh substation. |  |  | PEC | Darrel Mitchell (830) 868-7155 Darrel.Mitchell@PECI.com |  | 2007-06-30 | 2007-07-01 | 138 | 0 | 0 | 45 | 0 | HAYS |  |  |  |  | SEE PROJECT DESCRIPTION | Y | The name of Kohler's Crossing Substaion has been changed to Lehigh Substation
07TPIT0176 | Port Lavaca 69 kV, add 1-7.2 MVAR Cap Banks | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In Service | AEP GROUP 297 | AEP/TCC | Dave Goetz 918-599-2653 | 2038 | 2007-07-01 | 2007-07-01 | 69 | 0 | 0 | 0 | 14.4 | Val VERDE | Val VERDE |  |  |  |  | Y
07TPIT0129 | Marion Circuit Breaker Replacement | Replace under-rated (IC) 345 kV circuit breakers at Marion (7044) |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2007-06-30 | 2007-06-30 | 345 | 0 | 0 | 0 | 0 | Guadalupe |  | 2004-10-01 | 2004-10-01 | 2004-11-01 | SEE PROJECT DESCRIPTION | Y
06TPIT0159 | Peoria to Forreston Uprating | Rebuild the existing Peoria to Forreston 69kv line for a 100 deg C. operating temp. |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-06-30 | 69 | 0 | 31 | 0 | 0 | HILL | HILL |  |  |  | 228224225 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
05TPIT0078 | Mustang Island to Port Aransas, rebuild 69 kV line | Rebuild North Padre to Port Aransas 69 kV transmission line from 4/0 ACSR to 795 ACSS |  | AEP GROUP 029 | LCRA TSC / AEP | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1285, LCRA#1003910 | 2007-06-30 | 2007-06-30 | 69 | 0 | 8.3 | 0 | 0 | NUECES | NUECES |  |  |  |  | Y
04TPIT0134 | Bates to Palmview, tap Palmhurst and upgrade 69 kV to 138 kV line | Convert Moore Field and Palmhurst substations from 69 kV to 138 kV and connect to North Edinburg to Bates 138 kV line | In-Service | AEP GROUP 292 | AEP/TCC | Bill Eakin 918-599-2653 | 1484 | 2007-07-15 | 2007-06-29 | 138 | 0 | 2 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
06TPIT0152 | Menger Creek substation addition | Construct a new bundled 795 ACSR 138 kV transmission line approximately 4 miles in length from a tap point (7663) on the Boerne Cico (7151) -to- CPS Helotes (5200) transmission line to the proposed Menger Creek Substation (7665). | Not Affiliated With AEP Projects |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1005925 | 2007-06-30 | 2007-06-29 | 138 | 4 | 0 | 0 | 0 | KENDALL |  | 2004-04-01 | 2004-04-01 | Endorsed | SEE PROJECT DESCRIPTION | Y
07TPIT0166 | Mountain Creek 138 kV capacitors | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4052-WACF | 2007-06-15 | 2007-06-29 | 138 | 0 | 0 | 0 | 110.4 | DALLAS |  |  |  |  | 2411, 2412 | Y
06TPIT0177 | West Denton Sub: Construct 345 bus, add 2 line terminals and add a 2nd 345 auto | Expand 345 kV breaker and a half substation with line terminals for the Jacksboro line and N.W. Carrollton line. Add a 2nd 345-138 kV autotransformer | On schedule | 06TPIT0011 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04010 | 2007-04-07 | 2007-06-28 | 345 | 0 | 0 | 600 | 0 | DENTON |  |  | 2004-01-21 |  | 988, 986 | Y
06TPIT0061 | Weslaco Unit, add 1-28.8 Mvar cap | Construct a new Steward Road 138/69 kV substation, cut-in to the South McAllen to Weslaco Unit 138 kV line and South McAllen to LaPalma 69 kV line, convert the South McAllen to Hidalgo to Steward Road 69 kV to 138 kV and convert Hidalgo and Dyer substatio | In-Service | AEP GROUP 073 | AEP/TCC | Ashley Beasley 918-599-2653 | 1322 | 2007-06-01 | 2007-06-27 | 138 | 0 | 0 | 0 | 28.8 | HIDALGO | [5 empty] | Y
11TPIT0006 | Liggett 138 kV series reactors | Install 5-ohm 138 kV series reactors at Liggett in both circuits to Hackberry |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5119-WACF | 2007-06-15 | 2007-06-20 | 138 | 0 | 0 | 0 | 0 | DALLAS |  | 2004-04-02 | 2005-06-16 |  | 1922, 1996, 1924, 2002 | N
08TPIT0051 | Hillje Switching Station | Built a new 345 kV Hillje substation. Loop ckt.1 STP-Holman into the new substation. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-30 | 2007-06-15 | 345 | 0 | 0.5 | 0 | 0 | WHARTON | WHARTON | 2004-09-10 | 2004-11-01 | 2005-03-15 | 44330 | Y |  | No transformer capacity added.
06TPIT0156 | Laredo Heights to Anna Street, upgrade 69 kV inner loop to 138kV | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Heights to 138 kV, convert Heights to 138 kV and transfer/convert Anna to 138 kV line | In-Service | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 2001 | 2007-06-15 | 2007-06-15 | 138 | 0 | 1.96 | 80 | 0 | WEBB | WEBB |  |  |  |  | Y
06TPIT0246 | Bluff Creek, Install 2 - 20 Mvar Reactors | Expand the Bluff Creek 345/138 kV station | In-Service | AEP GROUP 354 | AEP/TNC | Ashley Beasley 918-599-2653 | 2133 | 2007-05-15 | 2007-06-15 | 138 | 0 | 0 | 0 | -40 | TAYLOR | [5 empty] | Y
07TPIT0197 | Crabb River | Installed new 138kV 14.4 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-15 | 138 | 0 | 0 | 0 | 14.4 | FORT BEND | FORT BEND |  |  |  | 44170 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0198 | Alief | Installed new 138kV 7.2 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-12 | 138 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  | 44020 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
06TPIT0091 | Forney - East Mesquite 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M285-WACF | 2007-05-01 | 2007-06-11 | 138 | 0 | 10.6 | 0 | 0 | KAUFMAN | DALLAS |  |  |  | 2438, 2756, 2769 | Y
07TPIT0203 | Harrisburg | Installed new 69kV 7.2 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-11 | 69 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  | 40800 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0061 | Verde Creek-Kerrville Stadium | Upgrade the 14.1-mile Verde Creek(7146)-Kerrville Stadium(7138) 336 ACSR 138-kV transmission line to 795 ACSR. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1005354 | 2007-06-30 | 2007-06-08 | 138 | 0 | 14.01 | 0 | 0 | KERR | KERR |  |  |  | SEE PROJECT DESCRIPTION | Y
07TPIT0089 | Ben Davis - Royse 345 line: Reconductor | Reconductor 17 miles of line to increase capacity | Delivery of materials are contributing to delays on thi projects. |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05010 | 2007-06-07 | 2007-06-07 | 345 | 0 | 17 | 0 | 0 | DALLAS | ROCKWALL |  | 2005-06-16 |  | 970, 2461 | Y
07TPIT0170 | Wells Branch 138kV substation | Establish a new 138kV Wells Branch substation with (2) 30MVA transformers. The substation will cut into existing LCRA's T-387 (Howard Ln - Round Rock S) and T-136 (McNeil - Round Rock). |  |  | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3240_117_4879 3230_117_2879 | 2007-06-01 | 2007-06-07 | 138 | 0.1 | 0 | 60 | 0 | TRAVIS | TRAVIS |  |  |  | Bus 9288 | Y
07TPIT0191 | Bayou - Bigbay ckt.79 | Verifed conductors clearance to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-02 | 2007-06-07 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 42160, 42180 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
06TPIT0175 | McCree Sub: Install 138 kV, 30 MVAR Cap Bank | Install new 30 MVAR, 138 kV capacitor bank | Larger projects were priorotized resulting in the delay of this project. |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04002 | 2007-06-07 | 2007-06-07 | 138 | 0 | 0 | 0 | 30 | DALLAS |  |  |  |  | 835 | Y
08TPIT0063 | Branchville to Silver City Rebuild | Rebuild existing Branchville to Silver City 69kv line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2008-06-01 | 2007-06-07 | 69 | 0 | 9.9 | 0 | 0 | MILAM | MILAM |  |  |  | 65,61 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0222 | Wichita Falls 69 kV terminal equipment | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R507-WACF | 2007-05-01 | 2007-06-07 | 69 | 0 | 0 | 0 | 0 | WICHITA |  |  |  |  | 1449 | Y |  | INCLUDED W/ R168A
07TPIT0201 | South Houston | Installed new 69kV 7.2 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-04 | 69 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  | 43170 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0059 | North Weslaco Distribution, upgrade 2 transformers & distribution equipment | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | In-Service | AEP GROUP 068 | AEP/TCC | Rich Haley 918-599-2653 | 1281 | 2007-06-30 | 2007-06-01 | 138 | 0 | 0 | 12.5 | 0 | HIDALGO | [5 empty] | Y
07TPIT0243 | Abilene South to Bluff Creek, Reconductor 138 kV Line | Reconductor Abilene South to Bluff Creek 138 kV with with 1020 ACCC | In-Service | AEP GROUP 354 | AEP/TNC | Ashley Beasley 918-599-2653 | 2198 | 2007-06-30 | 2007-06-01 | 138 | 0 | 18.5 | 0 | 0 | TAYLOR | TAYLOR |  |  |  |  | Y
07TPIT0023 | Upgrade Seaton Autotransformer | Install second or larger auto at Seaton |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-10-01 | 2007-06-01 | 138 | 0 | 0 | 60 | 0 | BELL |  |  |  |  | 130131 | Y |  | There is no right of way, circuit miles,conductor type,structure type,reactive capability or circuit breakers associated with this project
07TPIT0149 | Intercontinental- Westfield ckt.67 | Raise conductors and upgrade in-series equipment at Intercontinental and Westfield to increase emergency rating. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-06-01 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 45910, 46570 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0035 | New Berlin-Hickory Forest-Capote-Seguin | Convert the 21.4-mile New Berlin(7612)-Hickory Forest(7225)-Capote(7598) transmission line for 138-kV operation and disconnect the line from Capote. Convert the Capote-Seguin 69 kV line to a double-circuit transmission line by adding a new 5.6-mile 795 A |  |  | GVEC | David Tomczyszyn (830) 857-1110 dtomczyszyn@GVEC.org | Not yet assigned | 2008-06-30 | 2007-06-01 | 138 | 0 | 31.7 | 45 | 0 | GUADALUPE |  |  |  |  | SEE PROJECT DESCRIPTION | Y | SEE PROJECT DESCRIPTION
07TPIT0031 | Poage to Leon Junction Rebuild | Rebuild the existing Poage to Leon Junction 69KV line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-06-01 | 69 | 0 | 24 | 0 | 0 | BELL | CORYELL |  |  |  | 126145 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0226 | Graham Switching Station | Add circuit breakers |  | R505A | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R505B-WACF | 2007-05-15 | 2007-05-29 | 138 | 0 | 0 | 0 | 0 | YOUNG |  |  |  |  | 1596 | Y
06TPIT0020 | Stryker Creek - Jacksonville 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R362-WACF | 2007-06-01 | 2007-05-25 | 138 | 0 | 16.4 | 0 | 0 | CHEROKEE | CHEROKEE |  |  |  | 3110, 3112, 3253 | Y
07TPIT0207 | Industrial | Installed new 138kV 7.2 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-24 | 138 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  | 40841 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
08TPIT0012 | Naaman-Apollo 69 kV line | Line upgrade |  |  | GARLAND |  |  | 2007-05-24 | 2007-05-24 | 69 | 0 | 5.66 | 0 | 0 | DALLAS |  |  |  |  | 825, 800 | Y
06TPIT0044 | Temple - Troy 69 kV line | Upgrade 69 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R089-WACF | 2007-05-15 | 2007-05-24 | 69 | 0 | 6.1 | 0 | 0 | BELL | BELL |  |  |  | 3581, 3644 | Y
07TPIT0216 | N. Wichita Falls 69 kV terminal equipment | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R508-WACF | 2007-05-01 | 2007-05-21 | 69 | 0 | 0 | 0 | 0 | WICHITA |  |  |  |  | 1503 | Y
07TPIT0212 | Graham 345 kV terminal equipment | Upgrade 345 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R633-F, R636-F | 2007-05-01 | 2007-05-17 | 345 | 0 | 0 | 0 | 0 | YOUNG |  |  |  |  | 1430 | Y
06TPIT0147 | Smithers 345 kV sub. | Upgrade fault duty rating of Smithers 345 kV to at least 63kA | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-15 | 345 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND | 2004-09-10 |  |  | 44650 | N |  | 1)_Change is not applicable for the SSWG base cases. 2)_No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0146 | WAP 345 kV sub. | Upgrade fault duty rating of WAP 345 kV to at least 63kA | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-15 | 345 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND | 2004-09-10 |  |  | 44000 | N |  | 1)_Change is not applicable for the SSWG base cases. 2)_No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0131 | North Mercedes Distribution, upgrade 2 transformers & distribution equipment | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | In-Service | AEP GROUP 068 | AEP/TCC | Rich Haley 918-599-2653 | 1282 | 2007-06-30 | 2007-05-15 | 138 | 0 | 0 | 25 | 0 | HIDALGO | [5 empty] | Y
06TPIT0058 | Laredo BtB, build 100 MW CFE tie | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | In-Service | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1475 | 2007-05-13 | 2007-05-15 | 138 | 0 | 0 | 100 | 0 | WEBB | [5 empty] | Y |  | The scope of this project includes the ring bus, line cut-ins and connections to the Laredo Plant Station.
07TPIT0223 | Commerce Switch - Wolfe City 138 kV line | Rebuild existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R509-WACF | 2007-05-15 | 2007-05-14 | 138 | 0 | 12.7 | 0 | 0 | HUNT | HUNT |  |  |  | 1809, 1816 | Y
07TPIT0169 | Barton 138 kV Switching Station | Establish new 138 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R505A-WACF | 2007-05-25 | 2007-05-11 | 138 | 0 | 0 | 0 | 0 | JACK |  |  |  |  | 1599, 1600 | Y
07TPIT0192 | Galena - Crown - Jefferson ckt.94 | Upgraded in-series equipment at Crown and at Jefferson to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-10 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40612, 40400, 41240 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0196 | H.O. Clarke | Installed new 138kV 100 MVAR capacitor bank on 138kV ckt.90 to Garrott. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-09 | 138 | 0 | 0 | 0 | 100 | HARRIS | HARRIS |  |  |  | 47155 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0200 | Hockley | Installed new 138kV 26.7 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-09 | 138 | 0 | 0 | 0 | 26.7 | HARRIS | HARRIS |  |  |  | 45880 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0112 | Gibbons Creek Sub: Install breakers for autotransformers | Install breakers on the high side of T3 and low side of each autotransformer and reconfigure relaying | On schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T06011 | 2007-05-15 | 2007-05-07 | 345 | 0 | 0 | 0 | 0 | GRIMES |  | 2005-09-01 | 2005-11-01 | 2006-01-01 | 967 & 964 | Y
07TPIT0193 | North Belt - Hidden tap ckt.95 | Upgraded limiting equipment at North Belt to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-30 | 2007-05-07 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 46110, 45862 | Y |  | 1)_Part of Northwest Reliability Project, Phase 2 TPIT Project #05TPIT0237. 2)_No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0142 | Built Quintana 69KV Substation | Serve substation by looping into ckt.47 Freeport - Surfsi | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-07 | 69 | 0 | 7.8 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 43135 | Y |  | No transformer capacity added.
07TPIT0204 | Seally | Installed new 138kV 10.8 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-04 | 138 | 0 | 0 | 0 | 10.8 | AUSTIN | AUSTIN |  |  |  | 44640 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
06TPIT0249 | S.R. Bertron - Diabox ckt.22 | Verify conductors clearance and upgrade limiting equipment to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-01 | 2007-05-02 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 41405, 40480 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0199 | West Chase | Installed new 138kV 14.4 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-05-02 | 138 | 0 | 0 | 0 | 14.4 | HARRIS | HARRIS |  |  |  | 44760 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0184 | Hillje substation-related construction | For relocating the terminations at the STP corridor to accommodate the new Hillje substation. |  | 08TPIT0051 | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_4273 | 2007-06-01 | 2007-05-01 | 345 | 0 | 0 | 0 | 0 | BASTROP | BASTROP | 2004-09-01 | 2004-11-01 | 2005-03-01 | Busses 9073, 44200 | Y
06TPIT0035 | DeSoto 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at DeSoto |  | M351 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M269-WACF | 2007-06-01 | 2007-05-01 | 345 | 0 | 0 | 600 | 0 | DALLAS |  |  |  |  | 2431, 2424 | Y
07TPIT0004 | Plano Tennyson 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at Plano Tennyson |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M366-WACF | 2007-05-01 | 2007-05-01 | 345 | 0 | 0 | 600 | 0 | COLLIN |  | 2004-04-02 | 2005-06-16 |  | 2522, 2523 | Y
06TPIT0085 | Royse - Terrell Switch 138/69 kV line | Rebuild existing 69 kV line for double-circuit with 69 kV and 138 kV circuits |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M359-WACF | 2007-05-15 | 2007-05-01 | 138 | 18.5 | 18.51 | 0 | 0 | ROCKWALL | KAUFMAN | 2004-04-02 | 2005-06-16 |  | 2471, 2721, 2722, 2729, 2463 | Y
07TPIT0177 | Weslaco SS bypass while upgrading North Weslaco Distribution | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | In Service | AEP GROUP 068 | AEP/TCC | Rich Haley 918-599-2653 | 2208 | 2007-04-30 | 2007-04-30 | 138 | 0 | 0 | 0 | 0 | HIDALGO | [5 empty] | Y | Will be in-service temp for around 12 months and this is a bypass of Weslaco Switching Station between North Alamo to North Weslaco while work is being done to Weslaco.
04TPIT0042 | Watermill - W. Levee (2nd) 345 kV circuit | Install Watermill - W. Levee (2nd) 345 kV circuit |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M462-WACF | 2007-05-01 | 2007-04-26 | 345 | 9 | 0 | 0 | 0 | DALLAS | DALLAS |  |  |  | 2398, 2997, 2427, 2428 | Y
07TPIT0202 | Britmoore | Increased reactive capability to 134.4MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-04-26 | 138 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  | 44120 | Y |  | No transformer capacity added. and no transmission circuits built, rebuilt or reconductored.
07TPIT0189 | Tomball - Tomball tap ckt.66 | Verified conductors clearance to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-04-20 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 46510, 46511 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0049 | Centerville 69 kV to 138 kV voltage conversion, and its new 138 kV connections to McCree and Oates | Converts voltage for the substation and new 138 kV lines to McCree and Oates |  |  | GARLAND |  |  | 2007-04-19 | 2007-04-19 | 138 | 0 | 4.7 | 0 | 0 | DALLAS |  |  |  |  | 810, 834, 831 | Y
08TPIT0052 | STP - Hillje ckt. | Built new 345 kV line from STP to Hillje. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-30 | 2007-04-18 | 345 | 19.4 | 0 | 0 | 0 | MATAGORDA | WHARTON | 2004-09-10 | 2004-11-01 | 2005-03-15 | 5915, 44330 | Y |  | No transformer capacity added.
07TPIT0164 | Golden 138 kV Switching Station | Establish new 138 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R627-WACF | 2007-05-18 | 2007-04-18 | 138 | 0 | 0.22 | 0 | 0 | SCURRY |  |  |  |  | 1064, 1067, 1315, 1068 | Y
06TPIT0203 | Laredo BTB Station, Rebuild and convert line to CFE to 230 kV. | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | In Service | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1482 | 2007-04-16 | 2007-04-16 | 230 | 0 | 0.4 | 0 | 0 | WEBB | WEBB |  |  |  |  | Y
07TPIT0205 | Addicks | Increased cap bank size to 120MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-04-16 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  | 45620 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0008 | Venus - Sherry 345 kV line | Construct Venus - Sherry 345 kV line |  | M571 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5032-WACF | 2007-05-15 | 2007-04-14 | 345 | 1.4 | 0 | 0 | 0 | ELLIS | TARRANT | 2006-05-25 | 2006-07-06 | 2006-10-17 | 1907, 1911, 1917 | Y
06TPIT0102 | Camp Wood,add 69 kV SS & 2-3.6MVAR caps | Add 69 kV Capacitor at Camp Wood Substation with two 69 kV breakers for line terminations | In Service | AEP GROUP 281 | AEP/TCC | Steve Guinty 918-599-2653 | 1395 | 2007-04-12 | 2007-04-12 | 69 | 0 | 0 | 0 | 7.2 | EDWARDS | [5 empty] | Y
07TPIT0206 | Fort Bend | Reduced cap bank size to 60MVAR. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-04-09 | 138 | 0 | 0 | 0 | -33.3 | FORT BEND | FORT BEND |  |  |  | 44300 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0003 | Skyline - Replace 345kV Autotransformer #2 & #4 | Replace the two 480 MVA autotransformers(#2 & #4) with one 600 MVA autotransformer. | Project Delayed Due To Manufacturing Delays. |  | CPS | Darrell Clifton 210-353-4386 | S-0118 | 2007-04-07 | 2007-04-08 | 345 | 0 | 0 | 600 | 0 | BEXAR | BEXAR |  |  |  | 5371 5369 5370 | Y |  | There is no transmission line additions associated with this project
05TPIT0170 | Dansby to Atkins 138 reconductor | Reconductor an existing 138 to 1033 ACSR - Currently 477 and 636 ACSR |  |  | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 808 | 2007-05-01 | 2007-04-07 | 138 | 0 | 9 | 0 | 0 | BRAZOS | BRAZOS |  |  |  | 32862, 32897 | Y |  | There were no new transformers added with this project.
09TPIT0014 | Brackettville to Hamilton Road, rebuild 138 kV line | Rebuild Uvalde to Hamilton Road 138 kV line from 4/0 to 795 ACSS |  | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 1717, LCRA#1003627 | 2007-04-15 | 2007-04-07 | 138 | 0 | 29 | 0 | 0 | VAL VERDE | KINNEY |  |  |  |  | Y
07TPIT0221 | W. Waco 138 kV terminal equipment | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R481-WACF | 2007-05-01 | 2007-04-07 | 138 | 0 | 0 | 0 | 0 | MCLENNAN |  |  |  |  | 3436 | Y
07TPIT0160 | Texas City, Freeway Park-Dickinson Transmission Upgrade | Reconductor 2-636 ACSR line running from Freeway Park to Dickinson to 2-636 ACSS conductor |  |  | TNMP | Rex McDaniel, 409-948-8451, Rex.McDaniel@tnmp.com | GCEC26510 | 2007-03-01 | 2007-04-07 | 138 | 0 | 5.6 | 0 | 0 | GALVESTON | GALVESTON |  |  |  | 38820, 38850 | Y
07TPIT0219 | Temple 69 kV terminal equipment | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R486-WACF | 2007-05-01 | 2007-04-07 | 69 | 0 | 0 | 0 | 0 | BELL |  |  |  |  | 3644 | Y
06TPIT0230 | DeCordova - Everman 345 kV line upgrade | Upgrade existing 345 kV line to operate at an elevated conductor temperature |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5106-WACF | 2007-05-15 | 2007-04-04 | 345 | 0 | 34.4 | 0 | 0 | HOOD | TARRANT | 2005-03-01 | 2005-06-16 |  | 1888, 1887 | Y
06TPIT0140 | Elm Creek Switching Station | Install new 345 kV switching station at the intersection of the existing 345kV lines from STP-Skyline, STP-Hill Country, and both lines from Marion to San Miguel. | Project Delayed Due to Site Acquisition | T-0073 | CPS | Ulrich Skerhut 210-353-2923 | S-0188 | 2007-04-01 | 2007-04-02 | 345 | 0 | 0 | 0 | 0 | GUADALUPE | GUADALUPE |  |  |  | 5133 | Y |  | This is the substation work associated with project 06TPIT0172, transmission line miles are not included here
06TPIT0172 | Elm Creek Transmission Reroute | Reroute 345kV lines (STP- Skyline, STP- Hill Country, Marion, San Miguel) to connect with future Elm Creek Switchyard | Reroute dependent on Substation Construction | S-0188 | CPS | Ulrich Skerhut 210-353-2923 | T-0073 | 2007-04-01 | 2007-04-02 | 345 | 1 | 0 | 0 | 0 | GUADALUPE | GUADALUPE |  |  |  | 5133 | Y |  | There are no transformers associated with this project
06TPIT0219 | Construct West Bay 138KV Substation, Phase 2. | Served substation by extending ckt.48 and built a second circuit from Stewart to West Bay. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-03-31 | 2007-04-02 | 138 | 28 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  | 43520 | Y |  | No transformer capacity added.
07TPIT0159 | Quail Switching Station | Construct 345 kV switching station. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R626-WACF | 2007-04-16 | 2007-04-01 | 345 | 0 | 0.7 | 0 | 0 | ECTOR |  |  |  |  | 1020, 1016,1030 | Y
06TPIT0101 | Bergstrom to Kingsbery Reconductor | Reconductor the existing circuit 1021 (Bergstrom to Kingsbery) with bundled 795 ACSR Drake conductors to increase the circuit capacity to 2000 Amperes. |  | N/A | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | 3230_117_4271 | 2007-04-01 | 2007-04-01 | 138 | 0 | 4 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | Busses 9163,9123 | Y
07TPIT0081 | Pearson 69/138 kV Switching Station | Construct new Pearson 69/138 kV switching station with 83 MVA auto in the Quhi-Castroville 69 kV line where it crosses the CPS Hondo-Lytle 138 kV line | In Service |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2007-04-01 | 2007-04-01 | 138 | 18.5 | 18.51 | 83 | 0 | Medina |  | N/A | N/A |  | 5805,5807,5290,5390 | Y
06TPIT0065 | Prairie Hill to Purdon Rebuild | Rebuild Prairie Hill to Purdon with 795 and 138KV construction |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-05-31 | 2007-04-01 | 69 | 0 | 24.24 | 0 | 0 | LIMESTONE | NAVARRO |  |  |  | 107194 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0143 | Colorado Bend Energy Center generating facility interconnection project, Phase I and Phase II. Built new 138kV Dyann substation. | Built a new 138 kV Dyann substation. Looped ckt.60 Wharton - South Lane into the new substation. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-04-30 | 2007-03-29 | 138 | 1.82 | 0 | 0 | 0 | WHARTON | WHARTON | 2006-03-29 |  |  | 42985, 48731, 48732, 48733, 48734, 48735, 48736 | Y |  | No transformer capacity added.
07TPIT0255 | Hayes | Increased cap bank size to 14.4 MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2007-03-28 | 138 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  | 44312 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0217 | Roanoke Switch 138 kV terminal equipment | Upgrade 138 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5124A-WACF M5124B-WACF M5124C-WACF M5124D-WACF | 2007-05-01 | 2007-03-25 | 138 | 0 | 0 | 0 | 0 | DENTON |  |  |  |  | 1850, 1852 | Y
06TPIT0021 | Belton - Nolanville 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R029-WACF | 2007-05-06 | 2007-03-23 | 138 | 0 | 5.1 | 0 | 0 | BELL | BELL |  |  |  | 3610, 3617 | Y
05TPIT0009 | Pleasant Valley - Iowa Park Tap 69 kV line | Construct 69 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R126D-WACF | 2007-05-01 | 2007-03-23 | 69 | 12.2 | 0 | 0 | 0 | WICHITA | WICHITA |  |  |  | 1451, 1516, 1517, 1518 | Y
06TPIT0148 | STP - Dow ckt.18 and ckt.27 | Replaced 2000 Amp equipment on both circuits from STP to DOW. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-03-15 | 2007-03-20 | 345 | 0 | 0 | 0 | 0 | MATAGORDA | BRAZORIA | 2004-09-10 |  |  | 5915, 42500 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0185 | WA Parish - Crabb River ckt.09 | Upgraded in-series equipment at Crabb River to increased thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-03-01 | 2007-03-19 | 138 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  | 44010, 44170 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0088 | Laredo to Anna Street, upgrade 69 kV Inner Loop to 138 kV ine | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | In Service | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 51 | 2007-02-28 | 2007-03-14 | 138 | 0 | 3.17 | 0 | 0 | WEBB | WEBB |  |  |  |  | Y
06TPIT0124 | Anna Street, upgrade two transformers & distribution equipment | Convert inner loop 795 MCM 69 kV line from Laredo Plant to Zacate Creek to 138 kV, convert Zacate Creek to 138 kV and transfer/convert Anna to 138 kV line | In Service | AEP GROUP 070 | AEP/TCC | Don Kendall 918-599-2653 | 1706 | 2007-03-14 | 2007-03-14 | 138 | 0 | 0 | 57.6 | 0 | WEBB | [5 empty] | Y
07TPIT0125 | Temple Pecan Creek - Temple Switch 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R408B-WACF | 2007-05-15 | 2007-03-11 | 138 | 0 | 4.4 | 0 | 0 | BELL | BELL |  |  |  | 3415, 3420 | Y
07TPIT0220 | Temple Switch 69 kV terminal equipment | Upgrade 69 kV terminal equipment |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R482-WACF | 2007-05-01 | 2007-03-11 | 69 | 0 | 0 | 0 | 0 | BELL |  |  |  |  | 3643 | Y |  | INCLUDED W/ R408B
06TPIT0013 | Cedar Hill Substation - DeSoto 138 kV line | Rebuild existing line for double-circuit operation |  | M269 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M351-WACF | 2007-05-15 | 2007-03-05 | 138 | 6.2 | 6.2 | 0 | 0 | DALLAS | DALLAS |  |  |  | 2424, 2425, 3057, 3053 | Y
06TPIT0040 | Denison North - Denison Tap 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R138-WACF | 2007-05-15 | 2007-03-03 | 138 | 0 | 2.05 | 0 | 0 | GRAYSON | GRAYSON |  |  |  | 1739, 1743 | Y
07TPIT0208 | Obrien 345 kV sub. | Upgraded fault duty rating of Obrien 345 kV to at least 63kA | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-03-01 | 2007-03-01 | 345 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  | 44500 | N |  | Change is not applicable for the SSWG base cases.
05TPIT0047 | Dilley SS, add 2-57.6 MVAR caps | Addition 2x57.6 MVAR capacitor banks at Dilley and Falfurrias | In Service | AEP GROUP 290 | AEP/TCC | Dean Meeks 918-599-2653 | 1247 | 2007-02-27 | 2007-02-27 | 138 | 0 | 0 | 0 | 115.2 | BROOKS | [5 empty] | Y
07TPIT0209 | South Plant Substation 138-kV Substation - Will be in service at 69kV until south loop is converted to 138kV | New 138-kV Substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2007-02-21 | 2007-02-21 | 138 | 0 | 0 | 28 | 4.8 | CAMERON |  |  |  |  | 59500 | Y | Substation will operate at 69-kV until upgrade is complete
08TPIT0037 | Asphalt Mines to Brackettville, rebuild 138 kV line | Rebuild Uvalde to Hamilton Road 138 kV line from 4/0 to 795 ACSS | Schedule Update | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 1716, LCRA#1003627 | 2007-02-28 | 2007-02-07 | 138 | 0 | 38.6 | 0 | 0 | KINNEY | UVALDE |  |  |  |  | Y
07TPIT0246 | Red Bluff 138 kV Substation | Construct Red Bluff Substation in the Vanderbilt to Danevang 138 kV line. Sub to have one 12/16/20 MVA 138/12 kV transformer and motor operated switches. | In Service |  | STEC | Dung Nguyen 361-485-6142 dnguyen@stec.org |  | 2007-02-07 | 2007-02-07 | 138 | 0 | 0 | 20 | 0 | JACKSON |  | N/A |  |  | 5588 | Y
07TPIT0150 | Add new 69/12kV substation at Harrisburg. | Served substation by connecting to the 69kV bus @Harrisburg substation switchyard. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-02-28 | 2007-02-06 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40800 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
08TPIT0001 | Uvalde to Asphalt Mines, rebuild 138 kV line | Rebuild Uvalde to Hamilton Road 138 kV line from 4/0 to 795 ACSS |  | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 95, LCRA#1003627 | 2007-02-28 | 2007-02-01 | 138 | 0 | 14.39 | 0 | 0 | UVALDE | UVALDE |  |  |  |  | Y
07TPIT0111 | Bluff Creek, Add 90 MVAR SVC on Bluff Creek Auto tertiary | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | In-Service | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2075 | 2007-01-30 | 2007-01-31 | 345 | 0 | 0 | 0 | +50/-40 | TAYLOR | [5 empty] | Y
06TPIT0226 | W.A. Parish - Oasis ckt.99 | Expanded W. A. Parish and Oasis substations to separate parallel bundled 345 kV W.A. Parish - Oasis Ckt.99 into two separate circuits. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-02-05 | 2007-01-31 | 345 | 0.18 | 0 | 0 | 0 | FORT BEND | BRAZORIA |  |  |  | 44000 , 43035 | Y |  | No transformer capacity added.
06TPIT0079 | Kendall-CPS Cagnon 345-kV line | Construct a 345 kV bundled 1590 ACSR line (approximately 45 miles) between Kendall (7046) and Cagnon (5056) | NOT AFFILIATED WITH AEP PROJECTS |  | LCRA TSC / CPS | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org / CPS Energy Don Stanton (210) 353-3125 DRStanton@cpsenergy.com | T-0026 | 2007-01-01 | 2007-01-31 | 345 | 45 | 0 | 0 | 0 | BEXAR | KENDALL | 2001-12-01 | 2001-12-01 | 2002-02-02 | 70465056 | Y
06TPIT0237 | Bluff Creek, 138 kV Termination for Buffalo Gap | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | In-Service | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2013 | 2007-01-31 | 2007-01-31 | 138 | 0 | 0 | 0 | 0 | TAYLOR | TAYLOR |  |  |  |  | Y
08TPIT0090 | Flatonia-Harwood | Increase the line-to-ground clearance on the Flatonia (7247) - Waelder (7232) - Thompsonville (7231) - Harwood (7230) 69 kV transmission line as necessary to increase the capacity of this circuit to its full conductor rating of 42 MVA. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2008-06-30 | 2007-01-18 | 69 | 0 | 24 | 0 | 0 | FAYETTE | GONZALES |  |  |  | SEE PROJECT DESCRIPTION | Y
07TPIT0056 | Hearne to Branchville Rebuild | Rebuild existing Hearne to Branchville with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-06-01 | 2007-01-05 | 69 | 0 | 9.6 | 0 | 0 | ROBERTSON | MILAM |  |  |  | 36,61 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0202 | Crane, replace existing DRCS with +50/-40 MVAR DRCS | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 1788 | 2006-12-31 | 2007-01-01 | 69 | 0 | 0 | 0 | +50/-40 | CRANE |  |  |  |  | 6615 | Y
05TPIT0142 | Weil Tract SS, add 2-28.8 MVAR capacitors | Install capacitor banks at various locations in the Corpus Chrisi area | In-Service | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1666 | 2006-12-30 | 2006-12-30 | 138 | 0 | 0 | 0 | 57.6 | NUECES | [5 empty] | Y
05TPIT0234 | Sandow - Rogers - Temple Switch 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R438-WACF | 2006-12-15 | 2006-12-28 | 138 | 0 | 38.7 | 0 | 0 | MILAM | BELL |  |  |  | 3675, 3430, 3415 | Y
06TPIT0236 | Flat Creek 138 kV Switch | Establish 138 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R504-WACF | 2006-12-23 | 2006-12-28 | 138 | 0 | 0 | 0 | 0 | ERATH |  |  |  |  | 1642, 1643 | Y
06TPIT0256 | Bammel - Vetran tap ckt.67 | Raised conductors to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-12-21 | 2006-12-21 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 45651, 46551 | Y |  | Project cost included in Northwest Area Phase 2, Project #05TPIT0237. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0237 | Northwest Reliability Project, Phase 2 | Converted Bammel to a sectionalized substation. Loop Bammel into ckt.67 TH Wharton - North Belt. Upgrade limiting equipment at TH Wharton East bus. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-12-30 | 2006-12-21 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 45651 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
04TPIT0113 | Robstown tap to City of Robstown, rebuild 69 kV line | Rebuild the 69 kV line section from City of Robstown to Robstown tap with 336 ACSS | In-Service | AEP GROUP 027 | AEP/TCC | Michael Glueck 918-599-2653 | 84 | 2007-02-15 | 2006-12-21 | 69 | 0 | 0.74 | 0 | 0 | NUECES | NUECES |  |  |  |  | Y
06TPIT0011 | Jacksboro Switch - W. Denton 345 kV line (Oncor Delivery portion) | Construct Jacksboro Switch - W. Denton 345 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R111-WACF | 2006-12-01 | 2006-12-20 | 345 | 72 | 0 | 0 | 0 | JACK | DENTON | 2003-08-25 | 2004-02-01 | 2004-04-01 | 1429, 988 | Y
06TPIT0229 | Bluff Creek, Expand Bluff Creek to 345/138 kV Station with second 345/138 kV Auto | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | In-Service | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2112 | 2006-12-15 | 2006-12-17 | 345 | 0 | 0 | 675 | 0 | TAYLOR | [5 empty] | Y
06TPIT0222 | Jefferson - South Channel ckt.06 | Upgraded in-series equipment at Jefferson and South Channel to increase emergency rating. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-12-31 | 2006-12-14 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 41240, 41370 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0162 | Sandow Switch 345/138 kV autotransformer and 138 kV bus | Install 345/138 kV autotransformer and 138 kV bus |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R460-WACF | 2006-12-01 | 2006-12-12 | 345 | 0 | 0 | 600 | 0 | MILAM |  | 2006-03-15 | 2006-03-17 | 2006-10-17 | 3429, 3430 | Y
06TPIT0012 | Venus - Liggett 345 kV line | Construct Venus - Liggett 345 kV line |  | M346 | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M571-WACF | 2006-12-15 | 2006-12-11 | 345 | 43.4 | 0 | 0 | 0 | ELLIS | DALLAS |  |  | 2001-08-01 | 1907, 1916 | Y
06TPIT0248 | McDonald Road Switching Station | Construct 138 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R625-WACF | 2006-12-31 | 2006-12-09 | 138 | 0 | 0.15 | 0 | 0 | GLASSCOCK |  |  |  |  | 1135, 1354, 1032, 1360 | Y
07TPIT0033 | Power Plant 138-kV Substation | Relocate two 138/69-kV 60 MVA autotransformer from Militar Hwy |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2006-11-30 | 2006-12-07 | 138 | 0 | 0 | 120 | 0 | CAMERON |  |  |  |  | 59300 | Y
07TPIT0030 | Military Hwy - Power Plant 138-kV Line | Upgrade existing 69-kV circuit to 138-kV |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2006-11-30 | 2006-12-07 | 138 | 0 | 2.29 | 0 | 0 | CAMERON |  |  |  |  | 8339, 59300 | Y
07TPIT0032 | Military Hwy 138-kV Substation | Facilitate the substation for a new 138-kV Circuit to Power Plant substation |  |  | BPUB | Ramon Sanz, Jr. (956) 983-6203 rsanz@brownsville-pub.com |  | 2006-11-30 | 2006-12-07 | 138 | 0 | 0 | 0 | 0 | CAMERON |  |  |  |  | 8339 | Y
07TPIT0194 | TH Wharton tap - Gears tap ckt.95 | Raised conductors to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-01-01 | 2006-12-07 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 45512, 45782 | Y |  | Part of Northwest Reliability Project, Phase 2, TPIT Project #05TPIT0237. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0209 | Crane, add 57.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 1753 | 2007-03-31 | 2006-12-05 | 138 | 0 | 0 | 0 | 28.8 | CRANE |  |  |  |  | 6615 | Y
06TPIT0127 | Laredo BtB to Laredo Power Plant, Falfurrias 138 kV cut-in | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | In-Service | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1481 | 2006-12-31 | 2006-12-01 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB |  |  |  |  | Y
06TPIT0176 | Ben Davis Sub: Add 345 terminal and install a 2nd 345-138 autotransformer | Expand 345 ring bus and add a 2nd 345-138 kV autotransformer | Problems scheduling clearences in the Garland area have contributed to the delay of the project. |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05008 | 2006-11-10 | 2006-11-26 | 345 | 0 | 0 | 600 | 0 | DALLAS |  |  |  |  | 970, 968 | Y
06TPIT0173 | Ben Davis - Royse/Allen 138 line: Reconductor/Rebuild | Reconductor/Rebuild the 4 miles of this double circuit line which belongs to TMPA to increase rating on each circuit | Problems scheduling clearences in the Garland area have contributed to the delay of the project. | 06TPIT0032 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04009 | 2006-11-10 | 2006-11-26 | 138 | 0 | 3.8 | 0 | 0 | DALLAS | COLLIN |  | 2003-08-15 |  | 968, 2462 and 968, 2467 | Y
07TPIT0163 | Flewellen – Fort Bend ckt.09 | Verified conductors rating to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-12-15 | 2006-11-15 | 138 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  | 44231, 44100, 44280 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0010 | Centerville Switch - Parkdale 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M468-WACF | 2006-12-01 | 2006-11-14 | 138 | 0 | 16.8 | 0 | 0 | DALLAS | DALLAS | 2004-04-02 | 2005-06-16 |  | 2439, 2445, 2450, 2443, 2401, 2402, 2913, 2914, 2915, 2916 | Y
05TPIT0041 | Falfurrias, add 28.8 MVAR caps | Addition 2x25 MVAR capacitor banks at Dilley and Falfurrias | In-Service | AEP GROUP 290 | AEP/TCC | Dean Meeks 918-599-2653 | 1246 | 2006-11-10 | 2006-11-10 | 138 | 0 | 0 | 0 | 28.8 | FRIO | [5 empty] | Y
06TPIT0151 | Falurrias SS, add +/-25 MVAR DRCS | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dean Meeks 918-599-2653 | 1775 | 2006-11-10 | 2006-11-10 | 69 | 0 | 0 | 0 | 50 | BROOKS | [5 empty] | Y
05TPIT0205 | Chinati, add 3.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 1767 | 2006-12-31 | 2006-11-09 | 69 | 0 | 0 | 0 | 3.6 | PRESIDIO |  |  |  |  | 6682 | Y
06TPIT0086 | Paris Switch - Anna Switch 345 kV line and Valley S. Switching Station | Construct Paris Switch - Valley S. - Anna Switch 345 kV line and Valley S. Switching Station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R109A-WACF | 2006-11-06 | 2006-11-06 | 345 | 88.7 | 0 | 0 | 0 | LAMAR | COLLIN | 2002-05-01 | 2002-06-01 | 2001-09-01 | 1729, 1692, 1690, 2373 | Y
07TPIT0183 | Stepehenville to Carlton Switch | Rebuild Stephenville to Carlton Switch 69KV line with 138kv const. And 795 conductor |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2007-11-01 | 2006-11-05 | 69 | 0 | 4.25 | 0 | 0 | ERATH | ERATH |  |  |  | 299297 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0163 | Odessa EHV 345/138 kV 300 MVA autotransformer replacement | Replace existing 300 MVA 345/138 kV autotransformer with a 450 MVA autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R291-WACF | 2007-05-07 | 2006-11-01 | 345 | 0 | 0 | 450 | 0 | ECTOR |  | 2006-06-26 | 2006-08-15 | N/A | 1026, 1027 | Y
07TPIT0080 | Zapata SS, add +/-25 MVAR DRCS | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dean Meeks 918-599-2653 | 1488 | 2006-09-30 | 2006-10-31 | 138 | 0 | 0 | 0 | 50 | ZAPATA | [5 empty] | Y
06TPIT0207 | Zapata SS, 6 BKR Ring Bus - 14.4 Cap Bank | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dean Meeks 918-599-2653 | 1488 | 2006-09-30 | 2006-10-31 | 138 | 0 | 0 | 0 | 28.8 | ZAPATA | [5 empty] | Y
05TPIT0089 | Hamilton Road, add 2-14.4 MVar caps on source side of PST | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | In-Service | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1444 | 2007-05-31 | 2006-10-28 | 138 | 0 | 0 | 0 | 28.8 | VAL VERDE | [5 empty] | Y |  | Cost included in 05TPIT0081
05TPIT0081 | Hamilton Road 138 kV, add 150 MVA-PST on Sonora 138 kV line | Addition of a 150 MVA PST in the Hamilton Road to Sonora 138 kV line | In-Service | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1446 | 2007-05-31 | 2006-10-28 | 138 | 0 | 0 | 150 | 0 | VAL VERDE | [5 empty] | Y |  | Includes costs for 05TPIT0089
05TPIT0238 | White Oak - Heights ckt.34 | Raised conductors and partially reconductered ckt.34, and upgraded limiting equipment at Heights to increase thermal ratings | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-31 | 2006-10-25 | 69 | 0 | 4.4 | 0 | 0 | HARRIS | HARRIS |  |  |  | 46620, 47680 | Y |  | No transformer capacity added.
08TPIT0058A | Greens Bayou 345/138 kV autotransformer. | Replaced 400MVA Autotransformer (A1) at Greens Bayou with 800MVA and swapped autotransformer (A1) and (A2) 138kV leads. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-11-01 | 2006-10-22 | 345 | 0 | 0 | 800 | 0 | HARRIS | HARRIS | 2004-09-10 |  |  | 40700, 40710 | Y |  | Part of Houston area constraint mitigation project. No transmission circuits built, rebuilt or reconductored.
06TPIT0253 | Disconnected Scott138KV Substation from CenterPoint Energy's system. | Disconnected customer owned Scott substation from CNP's ckt.60 Fort Bend - Orchard. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-10-22 | 2006-10-22 | 138 | 0 | 0 | 0 | 0 | FORT BEND | FORT BEND |  |  |  | 44630 | Y |  | Bus #44630 removed from the base cases. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0117 | Sauer Dip to Silber Dip ckt.73 | Reconfigured Wirt, Echo and Sauer substations. Replaced overhead lines with underground | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-31 | 2006-10-19 | 138 | 0 | 6.2 | 0 | 0 | HARRIS | HARRIS |  |  |  | 44120, 44627, 44621, 44625, 44623, 44211, 44210, 44214, 44791, 44790, 44793, 44657, 46070 | Y |  | No transformer capacity added.
06TPIT0118 | Sauer Dip to Silber Dip ckt.81 | Reconfigured Wirt, Echo and Sauer substations. Replaced overhead lines with underground | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-31 | 2006-10-19 | 138 | 0 | 6 | 0 | 0 | HARRIS | HARRIS |  |  |  | 44120, 44626, 44622, 44620, 44624, 44212, 44215, 44213, 44792, 44795, 44794, 44656 | Y |  | Cost included in Sauer Dip to Silber Dip ckt.73 Project #06TPIT0117. No transformer capacity added.
05TPIT0181 | Big Lake Substation, reconfigure to five position ring bus | Reconfigure Big Lake 138 kV to ring bus | In-Service | AEP GROUP 238 | AEP/TNC | Brett Madison 918-599-2653 | 261 | 2006-11-10 | 2006-10-13 | 138 | 0 | 0 | 0 | 0 | REAGAN | [5 empty] | Y
06TPIT0223 | Long Creek Switch | Construct 345 kV switching station |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R620-WACF | 2006-11-01 | 2006-10-06 | 345 | 0 | 0.2 | 0 | 0 | SHACKELFORD |  |  |  |  | 1437 | Y
06TPIT0063 | Powell to Meridian | Rebuild exisiting Powell to Meridian 69kv line with 138kv const. |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-12-01 | 2006-10-01 | 69 | 0 | 9.7 | 0 | 0 | BOSQUE | BOSQUE |  |  |  | 327319 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
07TPIT0146 | North Belt - Drilco ckt.67 | Verified in-series equipment rating at North Belt and Drilco to increase emergency rating. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-31 | 2006-09-12 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 46110, 45740 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0147 | Drilco - Inteq ckt.67 | Verified in-series equipment at Drilco and Inteq to increase emergency rating. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-31 | 2006-09-12 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 45740, 45900 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0148 | Inteq- Intercontinental ckt.67 | Verified equipment at Inteq and Intercontinental to increase emergency rating. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-05-31 | 2006-09-12 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 45900, 45910 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0169 | Gibbons Creek to College Station Switch | Rebuild Iola to Booneville 69kv line with 795 or 1433 ACSS conductor and 138kv construction Route line into College Station Switch, establish Keith switch station near existing Keith 69kv station Route existing Gibbons Creek to Steep Hollow line into station |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-08-01 | 2006-09-01 | 138 | 0 | 26 | 0 | 0 | GRIMES | BRAZOS |  |  |  | 964,1,2,13,17,3200 | Y |  | There is no reactive or transformer capability associated with this project
06TPIT0180 | Cap Rock: New 138 sub with ring bus and route Olinger - Greenvile line into sub | Construct a new 138 kV switching station to provide a source for Cap Rock Energy | On schedule |  | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05009 | 2006-08-06 | 2006-09-01 | 138 | 0 | 0 | 0 | 0 | HUNT |  |  |  |  | 971 | Y
06TPIT0244 | Looped new 138/35kV substation near Magnolia Park into ckt.08 Magnolia Park to Ninth | Serve substation by looping into ckt.08 Magnolia Park - Ninth | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-09-01 | 2006-08-31 | 138 | 0.08 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 47701 | Y |  | No transformer capacity added.
06TPIT0174 | Gibbons Creek - Keith Switch 138 line: Reconductor | Reconductor 2 miles of line to increase capacity and provide alternate path of power into Bryan/College Station area | On schedule | 06TPIT0157 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T04011 | 2006-10-06 | 2006-08-26 | 138 | 0 | 2 | 0 | 0 | GRIMES | GRIMES |  | 2004-04-20 |  | 2, 964 | Y
08TPIT0031 | Channelview | Installed new 138kV 80 MVAR capacitor bank on 138kV ckt.84 to Jacintoport. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-15 | 2006-08-09 | 138 | 0 | 0 | 0 | 80 | HARRIS | HARRIS |  |  |  | 40282 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
08TPIT0058C | Addicks 345/138 kV autotransformer. | Added second 600MVA Autotransformer (A2) at Addicks. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-15 | 2006-08-02 | 345 | 0 | 0 | 600 | 0 | HARRIS | HARRIS | 2004-09-10 |  |  | 45600, 45610 | Y |  | Part of Houston area constraint mitigation project. No transmission circuits built, rebuilt or reconductored.
06TPIT0157 | Jack County to Wise County Switch | Line from Jack County Plant to new station vicinity of Bridgeport | Construction/ROW delays |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-08-15 | 2006-08-01 | 138 | 16 | 0 | 0 | 0 | JACK | WISE |  | 2003-05-01 | 2003-08-01 | 579570 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0002 | Krum Switching Station | Install 138/69kv switching station at existing Krum 138kv station, route existing Decatur to Krum 69kv line into station |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-08-01 | 2006-08-01 | 138 | 0 | 0 | 60 | 0 | DENTON |  |  |  |  | 1989670673 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
05TPIT0049 | Big Foot, add 14.4 MVAR 138 kV capacitor | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | In-Service | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1450 | 2006-11-30 | 2006-07-31 | 138 | 0 | 0 | 0 | 14.4 | UVALDE | [5 empty] | Y |  | Includes costs for 06TPIT0201
05TPIT0100 | Crist Road 138 kV new substation | New load serving |  |  | GARLAND |  |  | 2006-07-01 | 2006-07-31 | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 850 | Y
05TPIT0098 | Ben Davis-Crist Road 138 kV line | Line upgrade |  |  | GARLAND |  |  | 2006-07-01 | 2006-07-31 | 138 | 0 | 1.5 | 0 | 0 | DALLAS |  |  |  |  | 968, 850 | Y
05TPIT0099 | Crist Road-McCree 138 kV line | Line upgrade |  |  | GARLAND |  |  | 2006-07-01 | 2006-07-31 | 138 | 0 | 5.5 | 0 | 0 | DALLAS |  |  |  |  | 850, 835 | Y
06TPIT0201 | Big Foot, add 7.2 MVAR 69 kV capacitor | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | In-Service | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 2069 | 2006-11-30 | 2006-07-31 | 69 | 0 | 0 | 0 | 7.2 | UVALDE | [5 empty] | Y |  | Cost included in 05TPIT0049
07TPIT0053 | Weslaco SS to N Alamo, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | Schedule Update | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 282, LCRA#1003359 | 2006-07-30 | 2006-07-30 | 138 | 0 | 6 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
05TPIT0080 | North Laredo SS, add 150 MVA PST on Asherton 138 kV line | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | In-Service | AEP GROUP 290 | AEP/TCC | Brian Johnson 918-599-2653 | 1440 | 2006-11-10 | 2006-07-28 | 138 | 0 | 0 | 150 | 0 | WEBB | [5 empty] | Y |  | Includes costs for 05TPIT00500 and 06TPIT0134
05TPIT0050 | North Laredo SS, add 28.8 MVAR cap on source side of PST | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | In-Service | AEP GROUP 290 | AEP/TCC | Brian Johnson 918-599-2653 | 1452 | 2006-11-30 | 2006-07-28 | 138 | 0 | 0 | 0 | 28.8 | WEBB | [5 empty] | Y |  | Cost included in 05TPIT0080
06TPIT0134 | North Laredo SS, add 28.8 MVAR cap on load side of PST | Install a 150 MVA PST at North Laredo substation with capacitors at Asherton and North Laredo. | In-Service | AEP GROUP 290 | AEP/TCC | Brian Johnson 918-599-2653 | 1689 | 2006-11-30 | 2006-07-28 | 138 | 0 | 0 | 0 | 28.8 | WEBB | [5 empty] | Y |  | Cost included in 05TPIT0080
06TPIT0128 | Laredo BtB to Laredo Power Plant, Milo 138 kV cut-in | Construct 100 MW asynchronous interconnection with CFE, with a new 138 kV switching station. | In-Service | AEP GROUP 290 | AEP/TCC | Don Kendall 918-599-2653 | 1711 | 2006-10-01 | 2006-07-28 | 138 | 0 | 0 | 0 | 0 | WEBB | WEBB |  |  |  |  | Y
05TPIT0067 | Canyon-San Marcos | Upgrade the 3.0-mile section of the Canyon(7200)-Camp Gary(7196) 4/0-ACSR 69-kV transmission line between Canyon(7200) and San Marcos(7192) to bundled 795-ACSR 138-kV. Terminate the Camp Gary(7196) 69-kV transmission line at San Marcos(7199). Relocate one of the 138/69-kV 45-MVA auto-transformers from Canyon(7200) to San Marcos(7192). Retire one of the 138/69-kV 45-MVA auto-transformers at Canyon(7200). | The original Buda-San Marcos project was split into two separate projects: San Marcos-Canyon (LCRA TSC) and Buda-Canyon (see PEC TPIT) |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1002336 | 2007-07-30 | 2006-07-18 | 138 | 0 | 15 | 45 | 0 | HAYS |  |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0182 | Baytown | Installed new 138kV 120 MVAR capacitor bank on 138kV ckt.88 to Cedar Bayou. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-07-14 | 138 | 0 | 0 | 0 | 120 | HARRIS | HARRIS |  |  |  | 40171 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
09TPIT0057 | Fayetteville-Willow Springs | Replace under-rated limiting line terminal equipment to increase Fayetteville (7286)-Willow Springs (7273) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2009-06-30 | 2006-07-11 | 138 | 0 | 0 | 0 | 0 | [6 empty] | Y |  | This project is included with theMcNeil-Gilleland and Jollyville-Avery Ranch projects.
09TPIT0058 | Jollyville-Avery Ranch | Replace under-rated limiting line terminal equipment to increase Jollyville (9223)-Avery Ranch (7534) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2009-06-30 | 2006-07-11 | 138 | 0 | 0 | 0 | 0 | [6 empty] | Y |  | This project is included with the McNeil-Gilleland and Fayetteville-Willow Springs projects.
06TPIT0217 | Flatonia-Plum | Replace under-rated limiting line terminal equipment at Flatonia (7248) to increase Flatonia (7248)-Plum (7274) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2006-06-01 | 2006-07-11 | 138 | 0 | 0 | 0 | 0 | [6 empty] | Y
06TPIT0190 | Katy | Installled new 138kV 14.4MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-06 | 2006-07-05 | 138 | 0 | 0 | 0 | 14.4 | WALLER | WALLER |  |  |  | 44421 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0058 | Jewett to Watson Chapel Rebuild,Hilltop Lakes - Iola Conversion | Rebuild existing Jewett to Watson Chapel line with 1033,convert Hilltop lakes to Iola to 138KV operation |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-07-01 | 2006-07-01 | 138 | 0 | 21 | 0 | 0 | LEON | ROBERTSON |  |  |  | 333392 | Y |  | There is no reactive or transformer capability associated with this project
05TPIT0095 | Rio Hondo, add 345/138 kV auto | Rebuild La Palma to Rio Hondo 138 kV with 2-795 ACSS, double circuit capable and add 345/138 kV autotransformer at Rio Hondo | In-Service | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1462 | 2006-05-31 | 2006-06-30 | 345 | 0 | 0 | 675 | 0 | CAMERON | [5 empty] | Y
06TPIT0213 | Bluff Creek, cut-in Red Creek to Mulberry Creek, 345 kV Termination | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | In-Service | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2011 | 2006-05-30 | 2006-06-30 | 345 | 0 | 0 | 0 | 0 | TAYLOR |  |  |  |  | 6444, 6230 | Y
06TPIT0221 | Bluff Creek, Expand Bluff Creek to 345/138 kV Station with first 345/138 kV Auto | Expand the Bluff Creek Switch Station to a 345/138 kV station, cutting in Red Creek to Mulberry Creek 345 kV line and cutting in the Oak Creek to Abilene South 138 kV line. | In-Service | AEP GROUP 341 | AEP/TNC | Ashley Beasley 918-599-2653 | 2072 | 2006-07-31 | 2006-06-30 | 345 | 0 | 0 | 675 | 0 | TAYLOR | [5 empty] | Y
08TPIT0058B | Tomball two 345/138 kV autotransformers. | Replaced two 600MVA Autotransformers (A1) and (A2) at Tomball with two 800MVA autos. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-06-30 | 2006-06-30 | 345 | 0 | 0 | 1600 | 0 | HARRIS | HARRIS | 2004-09-10 |  |  | 46500, 46510 | Y |  | Part of Houston area constraint mitigation project. No transmission circuits built, rebuilt or reconductored.
05TPIT0083 | Frontera, add 2-57.6 MVAR caps | Install Capacitor Banks at Bates, Falcon, Garza, and Rio Grande City. | In-Service | AEP GROUP 292 | AEP/TCC | Rich Haley 918-599-2653 | 1534 | 2006-09-30 | 2006-06-30 | 138 | 0 | 0 | 0 | 115.2 | STARR | [5 empty] | Y
05TPIT0048 | Airline, add 1-57.6 MVAR caps | Install capacitor banks at various locations in the Corpus Chrisi area | In-Service | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1607 | 2006-06-01 | 2006-06-30 | 138 | 0 | 0 | 0 | 57.6 | NUECES | [5 empty] | Y
06TPIT0114 | Nelson Sharpe, add 150 MVA PST in Davis line and 2-43.2 MVAR caps | Construct Nelson Sharpe 345/138 kV substation in the Lon Hill to Rio Hondo 345 kV line and add a phase-shifting transformer at Nelson Sharpe in Davis 138 kV line | In-Service | AEP GROUP 294 | AEP/TCC | Tommy Antill 918-599-2653 | 1628 | 2006-06-01 | 2006-06-30 | 138 | 0 | 0 | 150 | 86.4 | KLEBERG | [5 empty] | Y
06TPIT0206 | Convert 69kV Ellington substation to a 138kV double tap substation. | Converted 69kV Ellington substation to a 138kV double tap substation. Tap Ellington into ckt.07 Webster-Garden Villas and ckt.91 P.H. Robinson-Cougar. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-06-30 | 138 | 0.2 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 42581, 42582 | Y |  | No transformer capacity added.
06TPIT0078 | Sandy Creek | Construct a new 795 ACSR 69-kV transmission line (approximately three miles) between a new Sandy Creek(7127) substation and the Sunrise Beach(7400) substation. Add a 138/69-kV 45-MVA auto-transformer at the new Sandy Creek substation which is to be cut into the Ferguson(7126)-Pitsburg(7120) 138-kV transmission line. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1001623 | 2006-06-30 | 2006-06-30 | 69 | 2.6 | 0 | 45 | 0 | LLANO |  | 2003-09-01 | 2003-10-01 |  | SEE PROJECT DESCRIPTION | Y
05TPIT0107 | Coffee Port, add 1-28.8 MVAR capacitor | Install capacitor banks at various locations in the East Valley area | In-Service | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1649 | 2006-07-01 | 2006-06-29 | 138 | 0 | 0 | 0 | 28.8 | CAMERON | [5 empty] | Y
06TPIT0073 | Andice-Glasscock | Construct a new 795 ACSR (220-MVA) 138-kV transmission line (approximately eleven miles) between the Andice(7522) and Glasscock(7523) substations and add two 138-kV circuit breakers at the Glasscock(7523) substation. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 241201 | 2006-06-30 | 2006-06-28 | 138 | 11 | 0 | 0 | 0 | WILLIAMSON |  | 2001-10-01 | 2001-11-01 | Endorsed | SEE PROJECT DESCRIPTION | Y
05TPIT0136 | Santa Rosa, add 28.8 MVAR capacitor | Install capacitor banks at various locations in the East Valley area | In-Service | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1647 | 2006-06-01 | 2006-06-26 | 138 | 0 | 0 | 0 | 28.8 | CAMERON | [5 empty] | Y
07TPIT0259 | Spencer - Pasadena ckt.06 | Verified in-series equipment at Pasadena to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2006-06-26 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 43271, 43040 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0258 | Greens Bayou - Oates tap ckt.38 | Verified in-series equipment at Greens Bayou to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2006-06-26 | 69 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40720, 41192 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0260 | Obrien - Mason ckt.25 | Verified in-series equipment at Obrien and at Mason to increase thermal ratings. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2007-06-01 | 2006-06-25 | 138 | 0 | 0 | 0 | 0 | FORT BEND | HARRIS |  |  |  | 44510, 44450 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0066 | Coronado-Graphite Mine-Lampasas | Upgrade the 27.5-mile Coronado(7086)-Graphite Mine(7084)-Lampasas(7064) 336 ACSR 138-kV transmission line to 795 ACSR. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1004373 | 2006-06-30 | 2006-06-15 | 138 | 27.5 | 0 | 0 | 0 | BURNET | LAMPASAS |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0193 | Needville | Installed new 69kV 7.2MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-06-15 | 69 | 0 | 0 | 0 | 7.2 | HARRIS | HARRIS |  |  |  | 43000 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0002 | Harmony Hills to Castle Hills to Med. Center 138kV Reconductor | Reconductor existing 138 kV line with 2-795 ACSR & 2-1272 ACSR. |  |  | CPS | Gerald Ripps 210-353-2470 | T-0020 | Jun-06 | 2006-06-13 | 138 | 0 | 6.3 | 0 | 0 | BEXAR | BEXAR |  |  |  | 5195 5080 5455 | Y |  | There are no transformers associated with this project
06TPIT0240 | Freeport | Increased reactive capability to 21.6MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-08-01 | 2006-06-13 | 69 | 0 | 0 | 0 | 14.4 | BRAZORIA | BRAZORIA |  |  |  | 42640 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0192 | Franz | Installed new 138kV 43.2MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-24 | 2006-06-12 | 138 | 0 | 0 | 0 | 43.2 | HARRIS | HARRIS |  |  |  | 44261, 44262 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0063 | E. Levee - Reagan St. 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M4039-WACF | 2006-05-15 | 2006-06-11 | 138 | 0 | 1.6 | 0 | 0 | DALLAS | DALLAS | 2004-04-02 | 2005-06-16 |  | 2482, 2819 | Y
06TPIT0214 | Canyon-San Marcos | Tap the Canyon(7200)-Camp Gary(7196) 69kV transmission line with the San Marcos substation 3 miles from Canyon. The Canyon-San Marcos line will terminate at the 138kV San Marcos bus (7192) and the Camp Gary-San Marcos line will terminate at the 69kV San Marcos bus (7199). Upgrade the Canyon(7200)-San Marcos(7192) 4/0-ACSR 69-kV transmission line to bundled 795-ACSR 138-kV. Relocate one of the 138/69-kV 45-MVA auto-transformers from Canyon (7200) to San Marcos(7192). |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1002336 | 2006-06-01 | 2006-06-09 | 138 | 0 | 3 | 45 | 0 | HAYS |  |  |  |  | SEE PROJECT DESCRIPTION | Y
04TPIT0127 | Weil Tract, bypass/cut-in Citgo NOP to Lon Hill 138kV line | Cut-in the Citgo North Oak Park to Lon Hill 138 kV transmission line into Weil Tract substation |  | AEP GROUP 041 | LCRA TSC / AEP | Michael Glueck 918-599-2653 | 1578, LCRA#1005717 | 2006-06-01 | 2006-06-08 | 138 | 0 | 0 | 0 | 0 | NUECES | [5 empty] | Y
07TPIT0100 | N Mercedes to N Weslaco, upgrade 69 kV to 138 kV Line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station |  | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 1266 | 2006-07-01 | 2006-06-08 | 69 | 0 | 5 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
05TPIT0036 | Highway 9, cut-in Nueces Bay to Morris 138 kV line | Cut-in the Nueces Bay to Morris Street 138 kV line into Highway 9 substation | In-Service | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1577 | 2006-06-01 | 2006-06-06 | 138 | 0 | 0 | 0 | 0 | NUECES | NUECES |  |  |  |  | Y
06TPIT0219a | Construct West Bay 138KV Mobil Substation, Phase 1. | Served substation by re-energizing ckt.48 from Stewart to West Bay mobil substation. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-07-01 | 2006-06-06 | 138 | 0 | 0 | 0 | 0 | GALVESTON | GALVESTON |  |  |  | 43520 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0189 | East Capacitor Addition | Install 54 MVAR Capacitors at 69 kV |  | 1-328303321 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 418 | 2006-06-06 | 2006-06-06 | 69 | 0 | 0 | 0 | 54 | BRAZOS |  |  |  |  | 32896 | Y | There were no new transformers added with this project and/or this project was within an existing substation and there was no new transmission lines installed.
05TPIT0190 | Nall Capacitor Addition | Install 27 MVAR Capacitors at 69 kV |  | 1-328303301 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 809 | 2006-06-06 | 2006-06-06 | 69 | 0 | 0 | 0 | 27 | BRAZOS |  |  |  |  | 32872 | Y | There were no new transformers added with this project and/or this project was within an existing substation and there was no new transmission lines installed.
06TPIT0254 | Karsten | Increased reactive capability to 106.7 MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-06-05 | 2006-06-05 | 138 | 0 | 0 | 0 | 6.7 | BRAZORIA | BRAZORIA |  |  |  | 44410 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0045 | Tennessee Colony 138 kV capacitor | Install 138 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R327-WACF | 2006-05-15 | 2006-06-05 | 138 | 0 | 0 | 0 | 36.8 | ANDERSON |  |  |  |  | 3281 | Y
05TPIT0046 | Weil Tract SS, add 138 kV SS | Cut-in the Citgo North Oak Park to Lon Hill 138 kV transmission line into Weil Tract substation | In-Service | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1579 | 2006-06-01 | 2006-06-01 | 138 | 0 | 0 | 0 | 0 | NUECES | [5 empty] | Y
05TPIT0028 | Marquis 138 kV new substation and new 138 kV/69 kV autotransformer (100MVA) | New load serving and install a new 138 kV/69 kV autotransformer (100MVA) at Marquis substation |  |  | GARLAND |  |  | 2006-06-01 | 2006-06-01 | 138 | 0 | 0 | 100 | 0 | DALLAS |  |  |  |  | 848, 852 | Y
05TPIT0029 | Marquis-Shiloh 138 kV line | Line upgrade |  |  | GARLAND |  |  | 2006-06-01 | 2006-06-01 | 138 | 0 | 0.67 | 0 | 0 | DALLAS |  |  |  |  | 848, 830 | Y
05TPIT0027 | Fairdale/Kraft-Marquis 138 kV line | Line upgrade |  |  | GARLAND |  |  | 2006-06-01 | 2006-06-01 | 138 | 0 | 1 | 0 | 0 | DALLAS |  |  |  |  | 805/836, 848 | Y
06TPIT0130 | North Alamo Distribution, upgrade 2 transformers & distribution equipment | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station | In-Service | AEP GROUP 068 | AEP/TCC | Rich Haley 918-599-2653 | 1280 | 2006-04-28 | 2006-05-30 | 138 | 0 | 0 | 57.6 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
06TPIT0055 | W McAllen to S McAllen, reconductor 138 kV line | Reconductor West McAllen to South McAllen 138 kV with 795 ACSS. | In-Service | AEP GROUP 292 | AEP/TCC | Rich Haley 918-599-2653 | 1454 | 2006-05-28 | 2006-05-28 | 138 | 0 | 3.28 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
05TPIT0090 | Nelson Sharpe, add 345/138 kV autotransformer | Construct Nelson Sharpe 345/138 kV substation in the Lon Hill to Rio Hondo 345 kV line and add a phase-shifting transformer at Nelson Sharpe in Davis 138 kV line | In-Service | AEP GROUP 294 | AEP/TCC | Tommy Antill 918-599-2653 | 1471 | 2006-05-31 | 2006-05-27 | 345 | 0 | 0 | 675 | 0 | KLEBERG | [5 empty] | Y
06TPIT0220 | Freeport area 69kV system upgrade, Phase 1. | Converted all 69 kV load at Velasco to 138 kV and rearrange connections to remove common mode outage of Velasco 69 kV autotransformers | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-06-30 | 2006-05-26 | 138 | 0 | 0.02 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 43360, 43370 | Y |  | No transformer capacity added.
06TPIT0211 | Lamar Blossum 138/69 kV autotransformer | Replace existing 138/69 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R502-WACF | 2006-05-15 | 2006-05-26 | 138 | 0 | 0 | 100 | 0 | LAMAR |  |  |  |  | 1771, 1772 | Y
06TPIT0074 | Fayetteville-Pisek-Welcome-Salem | Convert the 24.1-mile Fayetteville(7286)-Pisek(7296)-Welcome(7577)-Salem(7289) 795 ACSR transmission line from 69-kV to 138-kV operation. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1006413 | 2006-06-30 | 2006-05-26 | 69 | 0 | 24.1 | 0 | 0 | FAYETTE | WASHINGTON |  |  |  | SEE PROJECT DESCRIPTION | Y
05TPIT0043 | North Denton Conversion and Rebuild North Denton to Spring | Convert existing 138/69kv tie between Bepc and Tmpa buses at North Denton to 138kv, Rebuild North Denton to Spring line with 1033 conductor |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-03-06 | 2006-05-24 | 138 | 0 | 17.9 | 0 | 0 | DENTON | DENTON |  |  |  | 684680672682 | Y | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0150 | Dilley SS, Install -40/+50 Mvar SVC | Add 125 MVAR of dynamic reactive support throughout the Laredo, Hamilton, Victoria and Del Rio areas | In-Service | AEP GROUP 297 | AEP/TCC | Dean Meeks 918-599-2653 | 1776 | 2006-05-01 | 2006-05-24 | 69 | 0 | 0 | 0 | 90 | FRIO | [5 empty] | Y
05TPIT0085 | Rio Grande City, add 28.8 MVar caps | Install Capacitor Banks at Bates, Falcon, Garza, and Rio Grande City. | In-Service | AEP GROUP 292 | AEP/TCC | Tim Stelljes 918-599-2653 | 1533 | 2006-06-16 | 2006-05-19 | 138 | 0 | 0 | 0 | 28.8 | STARR | [5 empty] | Y
05TPIT0108 | Decker to Techridge 138kV circuit | Establish a new 138kV circuit from Decker to Techridge subs. Rebuild part of LCRA's T146 to establish a second Dessau to McNeil 138 kV circuit with 3000A capacity. Reconductor existing Ckt 904 (Dessau to McNeil) to 3000 A capacity. |  | CKT 975 #1-320527853 CKT 904 #1-320527859 CKT 909 #1-320527862 | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget #1436, 1437, 4244, 24126 | 2006-05-31 | 2006-05-17 | 138 | 23.17 | 0 | 0 | 0 | TRAVIS | TRAVIS |  |  |  | Busses 9187,9190,9193,9079 | Y
07TPIT0051 | Humble | Installed new 138kV 60 MVAR capacitor bank on 138kV ckt.94 to Duessen. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-05-17 | 138 | 0 | 0 | 0 | 60 | HARRIS | HARRIS |  |  |  | 40831 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0097 | Raymondville, upgrade 138/69 kV auto | Upgrade Raymondville 138/69 kV autotransformer to 93 MVA | In-Service | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1560 | 2006-06-01 | 2006-05-15 | 138 | 0 | 0 | 93 | 0 | CAMERON | [5 empty] | Y
05TPIT0134 | Kleberg add 28.8 MVAR capacitor | Install capacitor banks at various locations in the East Valley area | In-Service | AEP GROUP 293 | AEP/TCC | Ashley Beasley 918-599-2653 | 1665 | 2006-07-31 | 2006-05-15 | 138 | 0 | 0 | 0 | 28.8 | CAMERON | [5 empty] | Y
06TPIT0184 | South Channel | Installed new 138kV 120 MVAR capacitor bank on 138kV ckt.06 to Jefferson. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-05-15 | 138 | 0 | 0 | 0 | 120 | HARRIS | HARRIS |  |  |  | 41371 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0185 | P.H. Robinson | Installed new 138kV 106.7 MVAR capacitor bank on 138kV ckt.92 to Garden Villas. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-15 | 2006-05-15 | 138 | 0.1 | 0 | 0 | 106.7 | GALVESTON | GALVESTON |  |  |  | 42011 | Y |  | No transformer capacity added.
06TPIT0215 | Construct Cavern 138KV Substation | Looped into Biport - Riwood ckt.82 | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-05-15 | 138 | 0.27 | 0 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 43300 | Y |  | No transformer capacity added.
05TPIT0137 | Silber Dip to White Oak ckt.81 | Raised conductors to increase thermal ratings | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-05-15 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 44656, 46615 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0076 | Comfort-Raymond Barker | Upgrade the 9.8-mile Comfort(7155)-Raymond Barker Tap (7157) 336 ACSR (64-MVA) 69-kV transmission line to 795 ACSR (220-MVA) 138-kV. Upgrade the 2-mile Raymond Barker Tap (7157)-Verde Creek (7146) 336 ACSR (128-MVA) 138-kV transmission line to 795 ACSR (220-MVA). Relocate the 138-69-kV 45-MVA auto-transformer from Comfort to Raymond Barker Tap. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1003053 | 2006-06-30 | 2006-05-15 | 138 | 0 | 11.8 | 45 | 0 | KENDALL | KERR |  |  |  | SEE PROJECT DESCRIPTION | Y
06TPIT0178 | North Denton Sub: Add 2 138 terminals for BEPC line and auto | Expand 138 kV bus for BEPC's Spring line and autotransformer | On schedule | 05TPIT0043 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | T05004 | 2006-05-15 | 2006-05-15 | 138 | 0 | 0 | 0 | 0 | DENTON |  |  |  |  | 985 | Y
06TPIT0212 | Lott 69 kV capacitors | Install 69 kV capacitors |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R468-WACF | 2006-05-15 | 2006-05-11 | 69 | 0 | 0 | 0 | 9.2 | FALLS |  |  |  |  | 3642 | Y
06TPIT0126 | Goodwin, upgrade 2 transformers & distribution equipment | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | In-Service | AEP GROUP 208 | AEP/TCC | George Carpenter 918-599-2653 | 1189 | 2006-04-30 | 2006-05-08 | 138 | 0 | 0 | 40 | 0 | HIDALGO | [5 empty] | Y
05TPIT0001a | Braunig to Kennedy 138 kV Reconductor (Elmendorf - Floresville Section) | Rebuild 138 kV line from Braunig to Elmendorf to Eagle Creek to Floresville to Stockdale to Kennedy. | Rebuild of entire line divided up to several projects, each rebuilding from one station to the next. | T-0762 | CPS | Gerald Ripps 210-353-2470 | T-0762 | Jun-06 | 2006-05-06 | 138 | 0 | 14 | 0 | 0 | BEXAR | WILSON |  |  |  | 5025 5132 5135 5155 5412 | Y |  | There are no transformers associated with this project
05TPIT0258 | North Denton Sub; Additition for DME Transformer | Install 25MVA, 138kV to 13.2 kV substation transformer served from TMPA 138kV bus | On schedule | None | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org | 600569 | 2006-05-01 | 2006-05-06 | 138 | 0 | 0 | 0 | 0 | DENTON | DENTON |  |  |  | 985 | Y
05TPIT0038 | Leon Creek to Pleasanton, rebuild 138 kV line | Reconductor Leon to Pleasanton 138kV line from 336 to 795 ACSR. | In-Service | AEP GROUP 044 | AEP/TCC | Brian Johnson 918-599-2653 | 1398 | 2006-05-31 | 2006-05-05 | 138 | 0 | 15.4 | 0 | 0 | ATASCOSA | BEXAR |  |  |  |  | Y
06TPIT0218 | Howard Lane-McNeil | Replace under-rated limiting line terminal equipment at Howard Lane(7335) and McNeil(7334) to increase Howard Lane(7335)-McNeil(7334) to the conductor's rating. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org |  | 2006-06-01 | 2006-05-05 | 138 | 0 | 0 | 0 | 0 | Travis | [5 empty] | Y
07TPIT0052 | Tomball | Increased cap bank size to 14.4 MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-05-04 | 138 | 0 | 0 | 0 | 3.6 | HARRIS | HARRIS |  |  |  | 46511 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0255 | Garden Villas | Increased reactive capability to 100.03 MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-04 | 2006-05-04 | 138 | 0 | 0 | 0 | 6.7 | BRAZORIA | BRAZORIA |  |  |  | 42700 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0057 | Uvalde, add 1-14.4 138 kV MVAr caps | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | In-Service | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1448 | 2006-05-01 | 2006-05-01 | 138 | 0 | 0 | 0 | 14.4 | UVALDE |  | 2006-01-10 | 2006-02-14 | 2006-07-18 |  | Y
06TPIT0106 | Eagle Pass Escondido, add 138 kV SS and 1-28.8 cap bank | Rebuild Asherton to Eagle Pass 138 kV line from 4/0 to 795 MCM ACSR | In-Service | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 1656 | 2006-05-31 | 2006-05-01 | 138 | 0 | 0 | 0 | 28.8 | MAVERICK | [5 empty] | Y
06TPIT0123 | Uvalde, add 14.4 69 kV MVAr caps | Addition of 69 kV and 138 kV capacitor banks in the Uvalde area | In-Service | AEP GROUP 235 | AEP/TCC | Brian Johnson 918-599-2653 | 884 | 2006-05-01 | 2006-05-01 | 69 | 0 | 0 | 0 | 14.4 | UVALDE |  | 2006-01-10 | 2006-02-14 | 2006-07-18 |  | Y
05TPIT0166 | Hearne to Hearne Southwest Rebuild | Rebuild existing Hearne - Hearne Southwest with 795 |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-04-01 | 2006-05-01 | 69 | 0 | 2.62 | 0 | 0 | ROBERTSON | ROBERTSON |  |  |  | 36,31 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
06TPIT0019 | Sterrett - Waxahachie Pump 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M281-WACF | 2006-05-15 | 2006-04-30 | 138 | 0 | 0.64 | 0 | 0 | ELLIS | ELLIS |  |  |  | 2316, 2317, 2319 | Y
06TPIT0141 | Chico Gifford Hill - BEC Wise County Switch - Decatur 138 kV line | Loop Chico Gifford Hill - Decatur 138 kV line into BEC's Wise County Switch |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R176-WACF | 2006-05-01 | 2006-04-30 | 138 | 0 | 0.5 | 0 | 0 | WISE | WISE |  |  |  | 1565, 1564 | Y
06TPIT0200 | Airline 138 kV, Install -40/+50 Mvar SVC | South Texas area 180 MVAR of dynamic reactive support | In-Service | AEP GROUP 297 | AEP/TCC | Michael Glueck 918-599-2653 | 2042 | 2006-05-01 | 2006-04-30 | 69 | 0 | 0 | 0 | 90 | NUECES | [5 empty] | Y
06TPIT0210 | Collin series reactor | Install 2-ohm 138 kV series reactor on the 345/138 kV autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M323-WACF | 2006-05-15 | 2006-04-29 | 138 | 0 | 0 | 0 | 0 | COLLIN |  |  |  |  | 2370, 2372 | N
06TPIT0208 | Alvarado 138/69 kV autotransformer | Replace existing autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M367-WACF | 2006-05-15 | 2006-04-29 | 138 | 0 | 0 | 50 | 0 | JOHNSON |  |  |  |  | 2298, 2297 | Y
06TPIT0196 | Bellaire 345/138 kV autotransformer. | Added 800MVA autotransformer (A2) at Bellaire, swap ckt.05 to Jeanetta and ckt.09 to Brays at Bellaire and upgrade fault duty rating of Bellaire North 138kV bus to at least 63kA. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-05-30 | 2006-04-27 | 345 | 0 | 0 | 800 | 0 | HARRIS | HARRIS |  |  |  | 47000, 47010 | Y |  | No transmission circuits built, rebuilt or reconductored.
06TPIT0093 | Tyler SE - Tyler GE 138 kV line | Upgrade 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R336-WACF | 2006-05-01 | 2006-04-27 | 138 | 0 | 1.03 | 0 | 0 | SMITH | SMITH |  |  |  | 3143, 3213 | Y
06TPIT0161 | Valley 345/138 kV autotransformer | Replace existing 450 MVA 345/138 kV autotransformer with a 600 MVA autotransformer |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R500-WACF | 2006-05-01 | 2006-04-23 | 345 | 0 | 0 | 600 | 0 | FANNIN |  |  |  |  | 1690, 1691 | Y
06TPIT0209 | Benbrook 345 kV circuit breaker | Install a 345 kV circuit breaker |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5097-WACF | 2006-05-15 | 2006-04-21 | 345 | 0 | 0 | 0 | 0 | TARRANT |  | 2004-04-02 | 2005-06-16 |  | 1870, 1935 | Y
05TPIT0007 | North McAllen to West McAllen, reconductor 138 kV line | Reconductor 138 kV North McAllen to West McAllen with 795 ACSS conductor | In-Service | AEP GROUP 064 | AEP/TCC | Rich Haley 918-599-2653 | 283 | 2006-04-20 | 2006-04-20 | 138 | 0 | 4.71 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
05TPIT0233 | Northwest Austin 138 kV Substation | Establish a new 138 kV substation with one 30 MVA transformer and cut the new substation in between Jollyville and Williamson substation. |  | #1-322406631 | AUSTIN ENERGY | James Armke (512) 322-6705 james.armke@austinenergy.com | Budget #2794, 4794, 2835, 7010,7011 | 2006-02-15 | 2006-04-19 | 138 | 0.2 | 0 | 30 | 0 | TRAVIS | TRAVIS |  |  |  | Bus 9245 | Y
06TPIT0139 | Pueblo to Eagle Pass Escondido, rebuild 138 kV line | Rebuild Asherton to Eagle Pass 138 kV line from 4/0 to 795 MCM ACSR | In-Service | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 1715, LCRA#1003626 | 2006-05-31 | 2006-04-15 | 138 | 0 | 7.22 | 0 | 0 | MAVERICK | MAVERICK |  |  |  |  | Y
06TPIT0033 | Anna Switch - Allen Switch 138 kV line | Upgrade 138 existing kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M292-WACF | 2006-05-01 | 2006-04-12 | 138 | 0 | 42 | 0 | 0 | COLLIN | COLLIN |  |  |  | 2374, 2529, 2532, 2553, 2530, 2533, 2531, 2509, 2510, 2549, 2548, 2547, 2546, 2544, 2560, 2561 | Y
06TPIT0094 | Stryker Creek - Troup 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R363-WACF | 2006-05-15 | 2006-04-10 | 138 | 0 | 15.53 | 0 | 0 | CHEROKEE | CHEROKEE |  |  |  | 3110, 3147 | Y
05TPIT0076 | N Weslaco to Weslaco SS, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station |  | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 1267, LCRA#1003359 | 2006-04-07 | 2006-04-07 | 138 | 0 | 1 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
06TPIT0107 | Goodwin to LaGrulla, upgrade 69 kV to 138 kV line | Convert Bates to Rio Grande City 69 kV line to 138 kV with 795 ACSR conductor (rebuild 4/0 section between La Grulla to Rio Grande City) | Schedule Update | AEP GROUP 208 | LCRA TSC / AEP | Georger Carpenter 918-599-2653 | 1288, LCRA#1004249 | 2006-05-06 | 2006-04-07 | 138 | 0 | 14.1 | 0 | 0 | STARR | STARR |  |  |  |  | Y
06TPIT0205 | Ben Davis- McCree 138 line Re-route for Crisrt Rd Sub | Provide source for new Garland Sub | On schedule | 05TPIT0100 | TMPA | Eric Schroeder 936-873-1124 eschroeder@texasmpa.org |  | 2006-04-07 | 2006-04-07 | 138 | 0 | 0 | 0 | 0 | DALLAS | DALLAS |  |  |  | 850 | Y
05TPIT0255 | Capacitor Bank Addition at Greens Prairie Substation | Adding two 27 Mvar zero sequence closing transmission capacitor banks at Greens Prairie Substation |  |  | COCS | Garry Lange 979 764 3682 glange@cstx.gov |  | 2006-02-06 | 2006-04-06 | 138 | 0 | 0 | 0 | 54 | BRAZOS | BRAZOS |  |  |  |  | Y |  | Adding two 27 Mvar zero sequence closing transmission capacitor banks at Greens Prairie Substation
08TPIT0055 | Jewett - TH Wharton 345 kV line upgrade | Upgrade tie lines from Jewett to TXU Electric Delivery tie point to increase thermal ratings to 1450 MVA or above. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R465-WACF | 2006-05-01 | 2006-04-03 | 345 | 0 | 32.04 | 0 | 0 | LEON | LEON | 2004-09-10 |  | 2005-03-01 | 45500, 3390 | Y
05TPIT0249 | FM 106 138kV Line Relocation | Relocate 1.8 Miles of 138kV Line between MVEC Central and MVEC East Rio Hondo due to TXDOT Road Widening Project |  |  | MVEC | Loretta C. Gallaga (956) 463-1584 lgallaga@magicvalley.coop | 711622 | 2006-04-01 | 2006-04-01 | 138 | 0 | 1.8 | 0 | 0 | CAMERON | CAMERON |  |  |  |  | N |  | This has not yet been reflected in the SSWG Base Case but will need to be added.
05TPIT0250 | MVEC W. Edinburg- MVEC Alton | Rebuild 138kV line from W. Edinburg to Alton |  | 04TPIT0025 & 05TPIT0103 | MVEC | Loretta C. Gallaga (956) 463-1584 lgallaga@magicvalley.coop | 801147 | 2006-03-01 | 2006-04-01 | 138 | 0 | 6.8 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
01TPIT0001 | AEPTC Weslaco Switch to MVEC | Built a tie line between the AEPTC Weslaco Switch and the MVEC cross valley 138 kV line |  |  | MVEC | Loretta C. Gallaga (956) 463-1584 lgallaga@magicvalley.coop |  | 2006-03-01 | 2006-04-01 | 138 | 6.8 | 0 | 0 | 0 | HIDALGO | HIDALGO |  |  |  |  | Y
00TPIT0001 | AEPTC Rio Hondo to MVEC 138 lines | Built two lines to tie between the AEPTC Rio Hondo 345 to 138 kV Substation and MVEC's 138 kV lines |  |  | MVEC | Loretta C. Gallaga (956) 463-1584 lgallaga@magicvalley.coop |  | 2006-04-01 | 2006-04-01 | 138 | 1.8 | 0 | 0 | 0 | CAMERON | CAMERON |  |  |  |  | Y
06TPIT0056 | Barney Davis, add 2-28.8 MVAR capacitors | Install capacitor banks at various locations in the Corpus Chrisi area | In-Service | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1591 | 2006-04-10 | 2006-03-31 | 138 | 0 | 0 | 0 | 57.6 | NUECES | [5 empty] | Y
05TPIT0207 | Sonora, add 2x14.4 MVAR caps | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 213 | AEP/TNC | Ashley Beasley 918-599-2653 | 1756 | 2006-03-31 | 2006-03-31 | 138 | 0 | 0 | 0 | 28.8 | SUTTON |  |  |  |  | 6515, 6513 | Y
05TPIT0222 | Friend Ranch, add +/-25 MVAR DRCS | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 213 | AEP/TNC | Ashley Beasley 918-599-2653 | 1754 | 2006-03-31 | 2006-03-31 | 69 | 0 | 0 | 0 | 50 | CROCKET |  |  |  |  | 6562 | Y
06TPIT0188 | Satsuma | Increased reactive capability to 14.4MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-04-01 | 2006-03-24 | 138 | 0 | 0 | 0 | 3.6 | HARRIS | HARRIS |  |  |  | 46300 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0189 | White Oak South | Increased reactive capability to 100MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-04-01 | 2006-03-23 | 138 | 0 | 0 | 0 | 6.7 | HARRIS | HARRIS |  |  |  | 46615 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0187 | North Belt | Increased reactive capability to 14.4MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-04-01 | 2006-03-23 | 138 | 0 | 0 | 0 | 3.6 | HARRIS | HARRIS |  |  |  | 46111 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0021 | Brand 138 kV substation upgrade | Substation upgrade |  |  | GARLAND |  |  | 2006-03-22 | 2006-03-22 | 138 | 0 | 0 | 0 | 0 | DALLAS |  |  |  |  | 827 | Y
06TPIT0251 | Velasco to Seaway Switch ckt.02 | Raised conductors to increase thermal ratings | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-03-20 | 2006-03-21 | 138 | 0 | 0 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 43360, 42195, 43220 | Y |  | Cost were very low for this project due to surveying and adjustments. No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0248 | Constructed Booster 138KV Substation | Serve substation by looping into ckt.02 Velasco - Seaway | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-03-15 | 2006-03-20 | 138 | 0.18 | 0 | 0 | 0 | BRAZORIA | BRAZORIA |  |  |  | 43360, 42195, 43220 | Y |  | No transformer capacity added.
08TPIT0070 | Liggett - Shady Grove 138 kV line | Upgrade existing 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M5063-WACF | 2006-12-15 | 2006-03-20 | 138 | 0 | 2.5 | 0 | 0 | DALLAS | TARRANT |  |  |  | 1922, 2270, 2271 | Y
05TPIT0094 | Venus - Cedar Hill Substation 138 kV line | Construct 138 kV line |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | M346-WACF | 2006-05-15 | 2006-03-16 | 138 | 6.9 | 0 | 0 | 0 | DALLAS | DALLAS |  |  |  | 1915, 2311, 1908, 2300, 2313, 2314, 3054, 3056, 3055, 3053 | Y
05TPIT0224 | Crane, add +/-25 MVAR DRCS | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 1753 | 2006-03-15 | 2006-03-15 | 69 | 0 | 0 | 0 | 50 | CRANE |  |  |  |  | 6615 | Y
06TPIT0103 | Clear Springs | Add a new 345/138 kV 478 MVA auto-transformer at the Clear Springs substation(7050). The existing 345 kV bus at the Clear Springs will be converted from a ring bus configuration to a double-bus double-breaker configuration. Upgrade the 7.2-mile Clear Springs(7680)-Geronimo(7604)-Seguin(7228) 138 kV transmission line (T-264) from 336 ACSR to single 1433.6 ACSS (492 MVA), double circuit capable. Upgrade the 7.2-mile Clear Springs(7680)-Freiheit(7462)-Hortontown(7175)-Comal(7176) 138 kV transmission line (T-264, T-394, and T-119) from 336 ACSR to Bundled 959 ACSS (784 MVA) single circuit. |  |  | LCRA TSC | Stuart Nelson (512) 369-4526 Stuart.Nelson@lcra.org | 1005349 | 2006-06-30 | 2006-03-14 | 345 | 0 | 0 | 478 | 0 | GUADALUPE |  | 2005-04-01 | 2005-06-01 | Endorsed | SEE PROJECT DESCRIPTION | Y | Reviewing proejct scope for Harris Branch auto-transformer. Considering the Gilleland site.
04TPIT0124 | Westside, add 2-28.8 MVAR capacitors | Install capacitor banks at various locations in the Corpus Chrisi area | In-Service | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1608 | 2006-04-01 | 2006-03-06 | 138 | 0 | 0 | 0 | 57.6 | NUECES | [5 empty] | Y
05TPIT0208 | Rio Pecos, upgrade 57.6 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 213 | AEP/TNC | Brett Madison 918-599-2653 | 250 | 2006-12-31 | 2006-03-03 | 138 | 0 | 0 | 0 | 57.6 | PECOS |  |  |  |  | 6601 | Y
06TPIT0194 | Bellaire | Increased reactive capability to 120MVAR. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-03-01 | 2006-03-02 | 138 | 0 | 0 | 0 | 20 | HARRIS | HARRIS |  |  |  | 47010 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0200 | Friend Ranch, add 28.8 MVAR cap | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 213 | AEP/TNC | Ashley Beasley 918-599-2653 | 1754 | 2006-03-31 | 2006-03-01 | 138 | 0 | 0 | 0 | 28.8 | CROCKET |  |  |  |  | 6562 | Y
06TPIT0066 | Spring to St Jo Rebuild | Rebuild existing 138kv Spring to St Jo line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-04-01 | 2006-03-01 | 138 | 0 | 23.4 | 0 | 0 | COOKE | COOKE |  |  |  | 684691695746 | Y |  | There is no reactive or transformer capability associated with this project
06TPIT0183 | Crosby | Increased reactive capability to 106.7MVAR | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-04-01 | 2006-03-01 | 138 | 0 | 0 | 0 | 6.7 | HARRIS | HARRIS |  |  |  | 40391 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
07TPIT0029 | Hilltop Lakes to Hilltop Lakes Switch Upgrade or Rebuild | Rebuild or uprate the existing Hilltop Lakes to Hilltop Lakes Switch 69KV line |  |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2006-05-01 | 2006-03-01 | 69 | 0 | 17.2 | 0 | 0 | LEON | ROBERTSON |  |  |  | 48,43 | Y |  | There are no circuit breakers, reactive capability or transformer capacity associated with this project
05TPIT0128 | Northwest Abilene, add 28.8 MVAR cap | Add 6-28.8 MVAR 138 kV capacitor banks in Abilene area | In-Service | AEP GROUP 287 | AEP/TNC | Ashley Beasley 918-599-2653 | 1631 | 2006-02-28 | 2006-02-28 | 138 | 0 | 0 | 0 | 28.8 | TAYLOR | [5 empty] | Y
05TPIT0109 | Fort Phantom, add 28.8 MVAR cap | Add 6-28.8 MVAR 138 kV capacitor banks in Abilene area | In-Service | AEP GROUP 287 | AEP/TNC | Ashley Beasley 918-599-2653 | 1632 | 2006-02-28 | 2006-02-28 | 138 | 0 | 0 | 0 | 28.8 | TAYLOR | [5 empty] | Y
06TPIT0153 | Constructed Franklin 138KV Substation, Phase 1. | Serve substation by looping into ckt.21 from Gable Street to Crockett | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-02-15 | 2006-02-17 | 138 | 0.06 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 47620 | Y |  | No transformer capacity added.
04TPIT0106 | Santa Rosa to N Mercedes, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station |  | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 1265, LCRA#1003359 | 2006-02-17 | 2006-02-17 | 138 | 0 | 5 | 0 | 0 | CAMERON | HIDALGO |  |  |  |  | Y
04TPIT0129 | Santa Rosa to Harlingen SS, upgrade 69 kV line | Convert Pharr to Weslaco SS to Harlingen SS 69 kV line to 138 kV from 4/0 to 795 ACSS and convert North Pharr to switching station |  | AEP GROUP 068 | LCRA TSC / AEP | Rich Haley 918-599-2653 | 42, LCRA#1003359 | 2006-02-17 | 2006-02-17 | 138 | 0 | 8 | 0 | 0 | CAMERON | CAMERON |  |  |  |  | Y
06TPIT0122 | Treaschwig to Westfield ckt.66 | Raised conductors to increase thermal ratings | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-02-06 | 2006-02-15 | 138 | 0 | 7.1 | 0 | 0 | HARRIS | HARRIS |  |  |  | 46550, 46571, 46570 | Y
05TPIT0122 | Magnolia Park | Installed new 138kV 60 MVAR capacitor bank. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-02-15 | 2006-02-14 | 138 | 0.1 | 0 | 0 | 60 | HARRIS | HARRIS |  |  |  | 47700 | Y |  | No transformer capacity added.
06TPIT0186 | Webster | Installed new 138kV 100 MVAR capacitor bank on 138kV ckt.63 to La Marque. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-02-01 | 2006-02-14 | 138 | 0 | 0 | 0 | 100 | HARRIS | HARRIS |  |  |  | 43505 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
06TPIT0204 | Mont Belvieu 138/12kV transformer | Converted part of the 69 kV load at Mont Belvieu to 138kV. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-03-01 | 2006-02-09 | 138 | 0 | 0 | 50 | 0 | CHAMBERS | CHAMBERS |  |  |  | 41112, 41111 | Y |  | No transformer capacity added.
06TPIT0005 | Asherton to Conoco, rebuild 138 kV Line | Rebuild Asherton to Eagle Pass 138 kV line from 4/0 to 795 MCM ACSR |  | AEP GROUP 235 | LCRA TSC / AEP | Brian Johnson 918-599-2653 | 94, LCRA#1003626 | 2006-02-01 | 2006-02-01 | 138 | 0 | 33 | 0 | 0 | DIMMIT | MAVERICK |  |  |  |  | Y
05TPIT0223 | Rio Pecos, add +/-25 MVAR DRCS | Add 259 MVAR of static and 75 MVAR of dynamic reactive support throughout the McCamey area | In-Service | AEP GROUP 250 | AEP/TNC |  | 250 | 2005-10-05 | 2006-01-31 | 69 | 0 | 0 | 0 | 50 | PECOS |  |  |  |  | 6601 | Y
06TPIT0181 | Carbon 69 kV Switching Station | Establish switching station to provide interconnection for a generator. |  |  | Oncor Electric Delivery | Travis Besier, 214-486-4917, travis.besier@oncor.com | R607-WACF | 2006-01-31 | 2006-01-31 | 69 | 0 | 0 | 0 | 0 | HOWARD |  |  |  |  | 1321 | Y
06TPIT0239 | Disconnect and remove Minimax 138KV Substation from CenterPoint Energy's system. | Disconnected and removed customer owned Minimax substation from CNP's ckt.73 White Oak - Wirt. | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2006-01-21 | 2006-01-21 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 46070 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.
05TPIT0188 | Atkins Capacitor Addition | Install 54 MVAR Capacitors at 138 kV |  | 1-274266431 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 418 | 2006-01-06 | 2006-01-06 | 138 | 0 | 0 | 0 | 54 | BRAZOS |  |  |  |  | 32862 | Y |  | There were no new transformers added with this project and/or this project was within an existing substation and there was no new transmission lines installed.
05TPIT0169 | TAMU to Atkins 138 reconductor | Reconductor an existing 138 to 795 ACSR - Currently 636 ACSR |  | 1-308098601 | BTU | Pat Kasper, 979-821-5763, pkasper@btutilities.com | 809 | 2006-06-06 | 2006-01-06 | 138 | 0 | 3.83 | 0 | 0 | BRAZOS | BRAZOS |  |  |  | 2007 32799-32862 2008 and beyond 32799-32006 32006-32862 | Y |  | There were no new transformers added with this project.
05TPIT0184 | Highway 9, replace 138/69 kV autotransformer | Cut-in the Nueces Bay to Morris Street 138 kV line into Highway 9 substation | In-Service | AEP GROUP 041 | AEP/TCC | Michael Glueck 918-599-2653 | 1589 | 2006-01-01 | 2006-01-01 | 138 | 0 | 0 | 187 | 0 | NUECES | [5 empty] | Y
05TPIT0218 | Glenwood - Bertwood ckt.95 | Raised conductors to increase thermal ratings | In-Service |  | CNP | Wayne E. Kemper wayne.kemper@CenterPointEnergy.com 713 207 2192 |  | 2005-12-30 | 2006-01-01 | 138 | 0 | 0 | 0 | 0 | HARRIS | HARRIS |  |  |  | 40620, 40180 | Y |  | No transformer capacity added and no transmission circuits built, rebuilt or reconductored.

## TPITCancelledNoCost08012008
AUGUST BASE FOR TRANSMISSION OWNER SUBMISSION FILE - TRANSMISSION PROJECT INFORMATION TRACKING (TPIT) CANCELLED PROJECTS As Of 08/01/2008
ERCOT Project Number | Project Title (text, please start with location name first) | Project Description (text) | Comments/Reasons for Delays/Changes/Speedup (text) | Associated Projects (project number) | Transmission Owner (text) | TSP/Company Contact | Transmission Owner Project Number (TSP Optional) | Projected In-Service Date (Month/Yr) | Actual In-Service Date (Month/Yr) | Service Level kV | Trans Circuit Miles New | Trans Circuit Miles Rebuilt, Reconductored or Upgraded | Transformer Capacity (MVA) | Reactive Capability Added (Mvar, +Capacitor, -Reactor) | Location County (Start If Line) | End Location If Line County | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers ( CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Requested Additional Information | Other
07TPIT0175 | Up River 138 kV, add 1-28.8 MVAR Cap Bank | Add 360 MVAR of static capacitor support throughout the Laredo, Hamilton, Victoria and Del Rio areas | Cancelled | AEP GROUP 297 | AEP/TCC | Paul Hassink 918-599-2653 | 2037 | 2010-06-30 |  | 138 | 0 | 0 | 0 | 28.8 | Val VERDE | Val VERDE |  |  |  |  | N
10TPIT0060 | CC LNG Retail Cust Connection | Construct a new Corpus Christi LNG Plant Cargo Substation on the White Point to Dupont SS 138 kV transmission line | Cancelled by Customer | AEP GROUP 361 | AEP/TCC | Michael Glueck 918-599-2653 | 2181 | 2010-06-01 | n/a | 138 | 0.9 | 0 | 0 | 0 | NUECES | [5 empty] | N
10TPIT0061 | Dupont SS to Whitepoint 138 kV: Hairpin for Cheniene LNG Ring Bus Station | Construct a new Corpus Christi LNG Plant Cargo Substation on the White Point to Dupont SS 138 kV transmission line | Cancelled by Customer | AEP GROUP 361 | AEP/TCC | Michael Glueck 918-599-2653 | 2184 | 2010-06-01 | n/a | 138 | 0.56 | 0 | 0 | 0 | NUECES | [5 empty] | N
08TPIT0096 | East Munday Station, Replace the existing 69/138 kV auto | Replace 69/138 kV auto at East Munday with an 90 MVA 69/138 kV with LTC | Cancelled | AEP GROUP 289 | AEP/TNC | Brett Madison 918-599-2653 | 2008 | 2009-12-31 |  | 138 | 0 | 0 | 90 | 0 | KNOX | [5 empty] | N
09TPIT0061 | Stephenville Auto Upgrade | Increase auto capacity at Stephenville to at least 100mva | Delayed - no overload - Cancelled |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2011-06-01 |  | 138 | 0 | 0 | 100 | 0 | ERATH |  |  |  |  | 295299 | N |  | There are no circuit breakers, reactive capability or line associated with this project
11TPIT0029 | Hilltop Lakes Auto | Increase 138/69 autotransformer capacity at Hilltop Lakes | Cancelled |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2011-06-01 |  | 138 | 0 | 0 | 60 | 0 | LEON |  |  |  |  | 47,48 | N |  | There is no right of way, circuit miles,conductor type,structure type,or reactive capability associated with this project
10TPIT0059 | Forreston to Reagor Sprongs Rebuild | Rebuild existing Forreston-Reagor Springs line | Cancelled |  | BRAZOS | Dwight Beckmann, 254-750-6373, dbeckman@brazoselectric.com |  | 2010-12-01 |  | 69 | 0 | 12.1 | 0 | 0 | ELLIS | ELLIS |  |  |  |  | N
06TPIT0096 | Wynn Joyce-Ben Davis 138 kV line | Line upgrade | Cancelled |  | GARLAND | Danh Huynh, 972-205-3468,Dhuynh@garlandpower-light.org |  | 2009-06-01 |  | 138 | 0 | 7.37 | 0 | 0 | DALLAS |  |  |  |  | 813, 968 | N |  | This project was removed
08TPIT0150 | Cotton 138 kV Switching Station | Construct new switching station to connect a new wind farm | Cancelled/Per Customer |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R814-E |  |  | 138 | 0 | 0 | 0 | 0 | DAWSON |  |  |  |  | 3326, 3327, 3328 | N
09TPIT0153 | Killeen Switch terminal equipment | Replace terminal equipment | Cancelled |  | Oncor Electric Delivery | Michael Juricek, 214.743.6671, Michael.Juricek@oncor.com | R722-E | 2009-05-01 |  | 138 | 0 | 0 | 0 | 0 | BELL | [5 empty] | N

## TPIT5YearPlanProjects
Project Number | Project Name | Proposed in-service year | Status of Project | Associated TPIT ERCOT Project Number(s) | Notes
2007-R1 | Rothwood 345/138-kV switch station | 2010 | Design Stage | 09TPIT0086 | See the "TPITFuture05012008WithCost" tab for details (CNP) | Planning Stage
2007-R2 | Add a second 345/138-kV autotransformer at Forney | 2012 | Design Stage |  | (ONCOR) | In RPG Process
2007-R3 | Roanoke Switch 345/138-kV autotransformer #1 upgrade | 2010 | Design Stage |  | (ONCOR) | Canceled
2007-R4 | Roanoke Switch-Southlake 138-kV line upgrade | 2009 | Design Stage |  | (ONCOR) | In Construction
2007-R5 | Liggett 345/138-kV autotransformer upgrade | 2012 | Design Stage |  | (ONCOR) | Design Stage
2007-R6 | McCree-Shiloh 138-kV line upgrade | 2009 | Design Stage |  | (GARLAND) | CCN
2007-R7 | Fairdale-Brand 138-kV line upgrade | 2011 | Design Stage |  | This is called Fairdale-Brand 138-kV line upgrade in the 5 year plan (GARLAND)
2007-R8 | Lake Creek-Robinson 138-kV line upgrade | 2012 | Planning Stage |  | (ONCOR)
2007-R9 | Coppell Tap-McKamy Tap 138-kV line upgrade | 2012 | Planning Stage |  | (ONCOR)
2007-R10 | Construct a second McNeil-Summit 138-kV line | 2012 | Planning Stage | 08TPIT0034 | Delayed two years to 2014 due to budget constraint (AUSTIN ENERGY)
2007-R11 | Cross Timbers-Roanoke 138-kV line upgrade | 2011 | Planning Stage |  | (BRAZOS)
2007-R12 | Add a second 345/138-kV autotransformer at Lewisville | 2012 | Planning Stage |  | (BRAZOS)
2007-R13 | Temple North-Temple Elm Creek 138-kV circuit reconfigure | 2009 | Design Stage |  | (ONCOR)
2007-R14 | West Denton-Fort Worth-Teasley 138-kV upgrade | 2012 | Planning Stage |  | (TMPA)
2007-R15 | Anderson-Westover Hills 138-kV line upgrade | 2010 | Planning Stage | 11TPIT0025 | (CPS)
2007-E1 | East Bernard-Orchard-Fort Bend 138-kV line upgrade | 2009 | Design Stage | 09TPIT0088 | See the "TPITFuture05012008WithCost" tab for details (CNP)
2007-E2 | Add a second 345/138-kV autotransformer at Concord | 2009 | Design Stage |  | (BRAZOS)
2007-E3 | Add a second 345/138-kV autotransformer at Whitney | 2010 | Design Stage |  | (BRAZOS)
2007-E4 | Nacogdoches Southeast-Lufkin Switch 345-kV line | 2012 | In RPG Process |  | (ONCOR)
2007-E5 | Moss-Odessa Southwest 138-kV line terminal equipment upgrade | 2009 | Design Stage |  | (ONCOR)
2007-E6 | South McAllen-Las Milpas 138-kV line upgrade | 2012 | Planning Stage | NA | This project may be impacted by potential IPP interconnection (AEP)
2007- E7a | Clear Crossing 345-kV Switch Station | 2009 | Planning Stage | 08TPIT0136 | (AEP)
2007- E7b | Lamesa area upgrades | 2010 | In RPG Process |  | (ONCOR)
2007- E7c | Paint Creek-Murray-Graham 138-kV line upgrade | 2011 |  |  | ONCOR will upgrade terminal equipment at Graham in 2009 (ONCOR)
2007- E7d | Barton-Oran 138-kV line series reactor | 2011 | Planning Stage |  | (ONCOR)
2007- E7e | Oklaunion-Bowman 345-kV line | 2012 | Planning Stage | 11TPIT0020 | (AEP/ONCOR)
2007-E7f | Red Creek-Killeen Switch 345-kV line | 2012 | Planning Stage |  | (ONCOR)

## TransmissionOwnerProjContacts
TRANSMISSION OWNER | TPIT DISTRIBUTION | Primary Contact | Primary Email Address | Primary Phone | Secondary Contacts | Secondary Email Addresses | Secondary PHONE
AEP | Primary & Secondary | Paul Hassink | phassink@aep.com, | Paul Hassink: 918 599 2653 | Glen Reed; David Kidd | gareed@aep.com; dekidd@aep.com; rlbentz@aep.com; emfilat@aep.com; smdsouza@aep.com; ldpuyear@aep.com; | David Kidd: 918 599 2637 Glen Reed: 918 599 2664
AUSTIN ENERGY | Primary & Secondary | Ken Chui | ken.chui@austinenergy.com | Ken: 512 322 6745 | Armke, James; Mathew, Biju; Ebrahimian, Reza; Hunt, Dandy | James.Armke@austinenergy.com; biju.mathew@austinenergy.com; reza.ebrahimian@austinenergy.com; dandy.hunt@austinenergy.com; | James: 512 322 6705 Biju: 512 322 6381 Reza: 512 322 6740 Dandy: 512 322 6748
Bandera Electric | Primary | Brian Bartos | b.bartos@banderaelectric.com | Brian: 830 796 6074 | None | None | None
BEPC (BRAZOS ELECTRIC) | Primary & Secondary | Dwight Beckman | dbeckman@brazoselectric.com | Dwight: 254 750 6373 | David Albers | dalbers@brazoselectric.com; | David: 254 750 6358
BPUB | Primary | Ramon Sanz | rsanz@brownsville-pub.com | Ramon: 956 983 6203 | James McCann | jmccann@brownsville-pub.com; | James: 956 983 6204
BTU | Primary & Secondary | Patrick Kasper | pkasper@btutilities.com | Pat: 979 821 5763 | Randy Trimble | rtrimble@btutilities.com | Randy: 979-821-5728 979-229-3154 (cell)
CNP | Primary & Secondary | Wayne Kemper | wayne.kemper@centerpointenergy.com | Wayne: 713 207 2192 | Wesley Woitt; Rocha Paul; Hanson John; Larisa Loyferman | paul.rocha@centerpointenergy.com; john.hanson@centerpointenergy.com; larisa.loyferman@centerpointenergy.com;wesley.woitt@centerpointenergy.com | Paul: 713 207 2768 John: 713 207 2754 Larisa: 713 207 2499 Wesley: 713 207 2760
COCS | Primary | Tony Michalsky | tmichalsky@cstx.gov | Tony: 979 764 3438 | Aguie Palmisano; Timothy Crabb; David Massey | apalmisano@cstx.gov; tcrabb@cstx.gov; dmassey@cstx.gov | Augie 979 764 3447 Timothy 979 764 3439 David 979 764 3493
CPS | Primary & Secondary | Kenneth Bowen | kbowen@cpsenergy.com | Kenneth: 210-353-4142 | Blake Williams Basileo Rocha | bawilliams@cpsenergy.com; bdrocha@cpsenergy.com | Blake: 210-353-3557 Basileo: 210-353-4933
DENTON | Primary & Secondary | Chuck Sears | Chuck.Sears@cityofdenton.com | Chuck: 940 349 7111 | Brent Heath | brent.heath@cityofdenton.com; | Brent: 940 349 7180
GARLAND | Primary & Secondary | Danh Huynh | Dhuynh@garlandpower-light.org | Danh: 972 205 3826 | Grubbs, David; Fred Sherman; Steve Zaragoza | dlg@gplops.org; FredS@gplops.org; stevez@gplops.org | David: 972 205 3039 Fred: 972 205 3184 Steve: 972-205-3098
Golden Spread EC | Primary & Secondary | Dorothy Pierce | Dorothy.Pierce@chguernsey.com | Dorothy: 405 416 8131 | Shane McMinn, Mike Wise, Archie, Holtan | smcminn@gsec.coop; mwise@gsec.coop; Archie.Holtan@chguernsey.com | Shane: 806 379 7766 Mike: 806 379 7766 Archie: ?
LCRA TSC; PEC; SBEC; GVEC; City of Georgetown; BBEC | Primary & Secondary | Brad Woods | brad.woods@lcra.org | Brad: 512 369 4573 | Sergio Garza, Julius Horvath | sergio.garza@lcra.org; Julius.horvath@lcra.org; | Sergio: 512 369 4149 Julius: 512 369 4104
MVEC | Primary & Secondary | Loretta Gallaga | lgallaga@stec.org | Loretta: 956 514 1289 | Dung Nguyen | dnguyen@stec.org | Dung: 361 485 6142
Oncor | Primary & Secondary | Mike Juricek | Michael.Juricek@oncor.com | Mike: 214 743 6671 | Larry Reiter, Travis Besier | Travis.Besier@oncor.com; Larry.Reiter@oncor.com; | Larry: 214 743 6672 Travis: 214 486 4917
Sharyland Utilities | Primary & Secondary | Mark Caskey | mcaskey@sharylandutilities.com | Mark: 214 978 8243 | Michael Glass, Dwight Yarbrough | mglass@sharylandutilities.com; dyarbrough@sharylandutilities.com | Michael: 956 687 5600, Dwight: 956 687 5600
STEC | Primary & Secondary | Dung Nguyen | dnguyen@stec.org | Dung: 361 485 6142 | Cory Allen | cory@stec.org; | Cory: 866 225 5683 X2531
TMPA | Primary & Secondary | Eric Schroeder | eschroeder@texasmpa.org | Eric: 936 873 1124 | Frank Owens | fowens@texasmpa.org; | Frank: 936 873 1120
TNMP | Primary & Secondary | Mohammed Uddin | Mohammad.Uddin@tnmp.com | Mohammad: 409 948 8451 x232 | Aars, Alton; McDaniel, Rex | Rex.McDaniel@tnmp.com; Alton.Aars@tnmp.com; | Rex: 409 948 8451 X238 Alton: 972 317 5110x105