| NOGRR Number | 022 | NOGRR Title | EECP Media Appeal Change |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Deferred |
| Date of Decision |  | October 22, 2008 |  |  |
| Nodal Operating Guides Sections Requiring Revision |  | 4.5.3, Implementation 4.5.3.1, General Procedures Prior to EECP Operations 4.5.3.3, EECP Steps |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) removes required energy conservation media appeal from Emergency Electric Curtailment Plan (EECP) Step 2 and allows ERCOT management to issue a media appeal for energy conservation at management’s discretion, without requiring ERCOT CEO authorization. |  |  |
| Overall Market Benefit |  | Revision will allow ERCOT to use operational judgment on when an energy conservation media appeal is needed. |  |  |
| Overall Market Impact |  | Energy conservation through media appeal will be more effectively used by not being a firm requirement in EECP, but rather, a tool to be used when needed the most. |  |  |
| Consumer Impact |  | Better use of voluntary energy conservation efforts when Resource capacity is tight. |  |  |
| Procedural History |  | - On 7/22/08, NOGRR022 was posted. - On 8/19/08, the Operating Guides Revision Task Force (OGRTF) comments were posted. - On 8/20/08, the Operations Working Group (OWG) considered NOGRR022. - On 9/5/08, Transition Plan Task Force (TPTF) comments were posted. - On 9/16/08, Luminant comments were posted. - On 10/22/08, ERCOT comments were posted. - On 10/22/08, an Impact Analysis was posted. - On 10/22/08, the OWG considered the OWG Recommendation Report and Impact Analysis for NOGRR022. |  |  |
| OWG Decision |  | On 8/20/08, the OWG was in consensus to recommend approval of NOGRR022 as submitted. On 10/22/08, the OWG was in consensus to defer action on NOGRR022 until the issues with the associated Protocol Revision Request (PRR) 769, EECP Media Appeal Change, are resolved. |  |  |
| Summary of OWG Discussion |  | On 8/20/08, there was no discussion. On 10/22/08, it was noted that the ERCOT Board remanded PRR769 to TAC. |  |  |

ERCOT/Market Segment Impacts and Benefits

| Assumptions | 1 | Nodal Protocol EECP language will also require a change. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Better use of energy conservation through media appeal. If energy conservation through media appeal is needed, ERCOT would have the flexibility to start appeal sooner for more effective system impact. | None. |
|  | 2 | ERCOT might choose not to implement voluntary energy conservation through media appeal if the timeframe for resolving the capacity shortage is short term. The problem might get resolved before the effects of voluntary conservation would take place. | None. |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| OGRTF 081908 | Recommends approval of NOGRR022 as submitted. |
| Luminant 091608 | Proposes revisions so that a media appeal for load reduction would only be made during an EECP event. |
| ERCOT 102208 | Indicates that the development of an Impact Analysis for NOGRR022 will be deferred until the next OWG meeting following the meeting on October 22, 2008. |

| Original Sponsor |  |
| --- | --- |
| Name | John Jonte on behalf of the Operations Working Group (OWG) |
| Company | CenterPoint Energy |
| Market Segment | IOU |

Proposed Guide Language Revision

4.5	Emergency Electric Curtailment Plan (EECP)

[…]

4.5.3	Implementation

(1)	ERCOT shall be responsible for monitoring system conditions, initiating the EECP steps below, notifying all Qualified Scheduling Entities (QSEs) and Transmission Operators (TOs), and coordinating the implementation of the EECP conditions while maintaining transmission security limits.  QSEs and TOs will notify all the Market Participants they represent of each declared EECP step.

(2)	ERCOT has the authority to obtain emergency assistance energy over the Direct Current Tie(s) (DC Tie) for use by ERCOT.  ERCOT is also the coordinating authority for requests for emergency type power into or out of ERCOT.

(3) 	ERCOT, at management’s discretion, may at any time issue an ERCOT-wide appeal through the public news media for voluntary energy conservation.

(4)	There may be insufficient time to implement all steps in sequence.  ERCOT can immediately implement Step 4 of the EECP any time the system frequency is below 59.8 Hz and will immediately implement Step 4 any time the frequency is below 59.5 Hz.

(5)	Percentages for Step 4 Load shedding will be based on the previous year's TSP peak Load, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

(6)	The ERCOT System Operator shall declare the EECP steps to be taken by QSEs and TSPs.  QSEs and TSPs shall implement actions under that Step (and all above if not previously accomplished) and if ordered by the ERCOT Shift Supervisor or his designate, shall report back to the ERCOT System Operator when the requested step has been completed.

4.5.3.1 	General Procedures Prior to EECP Operations

Prior to declaring EECP Step 1 detailed in Section 4.5.3.3, EECP Steps, ERCOT shall:

(1)	Start Reliability Must-Run (RMR) Units available in the time frame of the emergency.  RMR Units should be loaded to full capability;

(2)	Issue Dispatch Instructions to QSEs to suspend any ongoing ERCOT-required generating unit testing;

(3)	Utilize Non-Spinning Reserve (Non-Spin) services that can be deployed to increase Responsive Reserves;

(4)	ERCOT shall use the Reserve Discount Factor (RDF) for the purpose of monitoring Physical Responsive Capability (PRC).  The PRC will be used by ERCOT to determine the appropriate emergency notification and EECP steps; and

[…]

4.5.3.3	EECP Steps

(1)	Step 1 – Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from Load Resources Equal To 2300 Mw

(a)	ERCOT shall:

(i)	Utilize available DC Tie capability that is not already being used by the market;

(ii)	Notify the Southwest Power Pool Security Coordinator;

(iii)	Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency.

(iv)	Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers (BLT).

(b)	QSEs shall notify ERCOT of any resources uncommitted but available in the timeframe of the emergency.

(2)	Step 2 – Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from Load Resources equal to 1750 MW

(a)	In addition to measures associate with Step 1, ERCOT shall:

(i)	Instruct TSPs to reduce Customer Loads by using distribution voltage reduction measures, if deemed beneficial by the TSP;

(ii)	Instruct QSEs to deploy all Responsive Reserve (RRS), which is supplied from Load Resources (controlled by high-set under-frequency relays); and

(iii)	With approval of the affected non-ERCOT control area, may instruct TSPs to implement BLTs, which transfer Load from the ERCOT Control Area to non-ERCOT Control Areas.

(3)	Step 3 – Maintain System frequency at 60 Hz

In addition to measures under Steps 1 and 2, ERCOT shall deploy all available EILS Resources as a single block via a single Verbal Dispatch Instruction to all QSEs providing EILS.

(4)	Step 4 - Maintain System frequency at 59.8 Hz or greater

(a)	In addition to measures under Steps 1, 2, and 3 ERCOT shall direct all TSPs and their agents to shed firm Load, in 100 MW blocks, distributed as agreed and documented in the ERCOT operating procedures in order to maintain a steady state system frequency of 59.8 Hz.  ERCOT may take this action prior to the expiration of the ten minute EILS Resource deployment period if ERCOT, in its sole discretion, believes that shedding firm Load is necessary to maintain the stability of the ERCOT System.  If, due to ERCOT System conditions, EILS Resources are not deployed prior to this action, ERCOT shall deploy EILS Resources as soon as possible following this action.

(b)	In addition to measures under Steps 1 and 2, TSPs shall, keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs shall not manually drop Load connected to under-frequency relays during the implementation of the EECP;