| NPRR Number | 142 | NPRR Title | EECP Media Appeal Change |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | December 4, 2008 |  |  |
| Nodal Protocol Sections Requiring Revision |  | 6.5.9.4, Emergency Electric Curtailment Plan 6.5.9.4.1, General Procedures Prior to EECP Operations 6.5.9.4.2, EECP Steps |  |  |
| Proposed Effective Date |  | Upon the Nodal Protocol Transition Plan’s Texas Nodal Market Implementation Date, as prescribed by zonal Protocol Section 21.12, Process for Transition to Nodal Market Protocol Sections. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This Nodal Protocol Revision Request removes required energy conservation media appeal from Emergency Electric Curtailment Plan (EECP) Step 2 and allows ERCOT management to issue a media appeal for energy conservation at management’s discretion, without requiring ERCOT CEO authorization. |  |  |
| Overall Market Benefit |  | Revision will allow ERCOT to use operational judgment on when an energy conservation media appeal is needed. |  |  |
| Overall Market Impact |  | Energy conservation through media appeal will be more effectively used by not being a firm requirement in EECP, but rather, a tool to be used when needed the most. |  |  |
| Consumer Impact |  | Better use of voluntary energy conservation efforts when Resource capacity is tight. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR142 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 7/22/08, NPRR142 was posted. - On 8/21/08, PRS considered NPRR142. - On 9/5/08, Transition Plan Task Force (TPTF) comments and a TPTF voting ballot were posted. - On 9/16/08, Luminant comments were posted. - On 9/24/08, PRS again considered NPRR142. - On 10/13/08, an Impact Analysis was posted. - On 10/23/08, PRS considered the PRS Recommendation Report and Impact Analysis for NPRR142. - On 11/19/08, ERCOT comments were posted. - On 11/20/08, PRS again considered the PRS Recommendation Report and Impact Analysis for NPRR142. - On 12/4/08, TAC considered NPRR142. |  |  |
| PRS Decision |  | On 8/21/08, PRS unanimously voted to refer NPRR142 to TPTF. All Market Segments were present for the vote. On 9/24/08, PRS unanimously voted to recommend approval of NPRR142 as submitted. All Market Segments were present for the vote. On 10/23/08, PRS unanimously voted to table NPRR142. All Market Segments were present for the vote. On 11/20/08, PRS unanimously voted to endorse and forward the PRS Recommendation Report as revised by ERCOT comments and Impact Analysis for NPRR142 to TAC. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 8/21/08, PRS noted that TPTF had not reviewed NPRR142. On 9/24/08, there was no discussion of NPRR142. During the discussion of the companion Protocol Revision Request (PRR), PRR769, EECP Media Appeal Change, ERCOT Staff expressed support for the revisions as proposed in PRR769 and opposition to the change recommended by Luminant’s comments dated September 16, 2008, which would limit ERCOT’s ability to issue a media appeal for Load reduction to EECP events. ERCOT Staff explained that ERCOT wants the discretion to issue a media appeal not only during EECP events, but also prior to an anticipated EECP event or Alert. One Market Participant expressed its view that there should be some restrictions on ERCOT’s discretion. The possibility of a compromise that would place some limit on ERCOT’s discretion to issue a media appeal, but not only in the case of an EECP event, was also discussed. On 10/23/08, it was noted that the ERCOT Board remanded PRR769 to TAC. On 11/20/08, there was no discussion. |  |  |
| TAC Decision |  | On 12/4/08, TAC unanimously voted to recommend approval of NPRR142 as recommended by PRS. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 12/4/08, there was no discussion. |  |  |

ERCOT/Market Segment Impacts and Benefits

| Assumptions | 1 | The ERCOT Nodal Operating Guides will require a similar revision. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Better use of energy conservation through media appeal. If energy conservation through media appeal is needed, ERCOT would have the flexibility to start appeal sooner for more effective system impact. | None. |
|  | 2 | ERCOT might choose not to implement voluntary energy conservation through media appeal if the timeframe for resolving the capacity shortage is short term. The problem might get resolved before the effects of voluntary conservation would take place. | None. |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| TPTF 090508 | Endorses NPRR142 as submitted and recognized it as “Needed for Go-Live” |
| Luminant 091608 | Proposes revisions to permit ERCOT to issue media appeal for Load reduction only during an EECP event. |
| ERCOT 111908 | Proposes revisions to reflect ERCOT Board approval of PRR769, EECP Media Appeal Change, and NPRR107, Nodal Emergency Interruptible Load Service (EILS). |

| Original Sponsor |  |
| --- | --- |
| Name | John Jonte on behalf of the Operations Working Group (OWG) |
| Company | CenterPoint Energy |
| Market Segment | IOU |

Proposed Protocol Language Revision

6.5.9.4	Emergency Electric Curtailment Plan

(1)	At times it may be necessary to reduce ERCOT System Demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing Demand during such emergencies, ERCOT shall initiate and coordinate the implementation of the Emergency Electric Curtailment Plan (EECP) following the steps set forth below in Section 6.5.9.4.2, EECP Steps.

(2)	The goal of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of cascading Outages.

(3)	ERCOT’s operating procedures must meet the following goals:

(a)	Use of market processes to the fullest extent practicable without jeopardizing the reliability of the ERCOT System;

(b)	Use of RRS services, other Ancillary Services, and Emergency Interruptible Load Service (EILS) to the extent permitted by ERCOT System conditions;

(c)	Maximum use of ERCOT System capability;

(d)	Maintenance of station service for nuclear-powered Generation Resources;

(e)	Securing startup power for Generation Resources;

(f)	Operation of Generation Resources during loss of communication with ERCOT; and

(g)	Restoration of service to Loads in the manner defined in the Operating Guides.

(4)	ERCOT is responsible for coordinating with QSEs, TSPs, and DSPs to monitor ERCOT System conditions, initiating the EECP steps, notifying all QSEs, and coordinating the implementation of the EECP steps while maintaining transmission security limits.

(5)	ERCOT, at management’s discretion, may at any time issue an ERCOT-wide appeal through the public news media for voluntary energy conservation.

(6)	During the EECP, ERCOT has the authority to obtain energy from non-ERCOT Control Areas using the DC Ties or by using Block Load Transfers (BLTs) to move load to non-ERCOT Control Areas.  ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with NERC scheduling guidelines.

(7)	Some of the EECP steps are not applicable if transmission security violations exist.  There may be insufficient time to implement all EECP steps in sequence, however, to the extent practicable, ERCOT shall use Ancillary Services that QSEs have made available in the market to maintain or restore reliability.

(8)	ERCOT may immediately implement Step 4 of the EECP any time the steady-state system frequency is below 59.8 Hz and shall immediately implement Step 4 any time the steady-state frequency is below 59.5 Hz.

(9)	Percentages for Step 4 Load shedding will be based on the previous year’s TSP peak Loads, as reported to ERCOT, and must be reviewed by ERCOT and modified annually as required.

6.5.9.4.1	General Procedures Prior to EECP Operations

- (1)	Prior to declaring EECP Step 1 detailed in Section 6.5.9.4.2, EECP Steps, ERCOT may perform the following operations consistent with Good Utility Practice:

(a)	Provide Dispatch Instructions to QSEs for specific Resources to operate at an Emergency Base Point to maximize Resource deployment so as to increase Responsive Reserve levels on other Resources;

(b)	Commit available Resources as necessary that can respond in the timeframe of the emergency.  Such commitments will be settled using the HRUC process;

(c)	Start RMR units available in the time frame of the emergency.  RMR Units should be loaded to full capability;

(d)	Issue Dispatch Instructions to QSEs to suspend any ongoing ERCOT required generating unit or Resource performance testing;

(e)	Utilize available resources providing Non-Spinning Reserve (Non-Spin) services as required; and

(f)	ERCOT shall use the PRC to determine the appropriate emergency Notification and EECP steps.

6.5.9.4.2	EECP Steps

(1)	Step 1 - Maintain a sum total of 2,300 MW that results from adding the amount of ERCOT PRC MW (Section 6.5.7.5, Ancillary Services Capacity Monitor) and the amount of RRS MW which is supplied from Load Resources.

(a)	ERCOT will:

(i)	Notify the Southwest Power Pool Security Coordinator;

(ii)	Initiate manual HRUC Dispatch Instructions to Generation Resources available and off-line that can perform within the expected timeframe of the emergency; and

- Use available DC Tie import capacity not already being used and inquire about availability of BLTs.

(b)	QSEs will notify ERCOT of any Resources uncommitted but available in the timeframe of the emergency.

(2)	Step 2 - Maintain a sum total of 1,750 MW that results from adding the amount of ERCOT PRC MW (Section 6.5.7.5) and the amount of RRS MW which is supplied from Load Resources.

(a)	In addition to the measures associated with Step 1, ERCOT:

(i)	Will instruct TSPs and DSPs to reduce Customers’ Load by using distribution voltage reduction measures, if deemed beneficial by the TSP or DSP;

(ii)	Will instruct QSEs to deploy Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) in accordance with the following:

(A)	Instruct QSEs to deploy half of the Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 1 Load Resources providing Responsive Reserve.  QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from Group 2 if Load Resource operational considerations require such.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(B)	At the discretion of the ERCOT Operator, instruct QSEs to deploy the remaining Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 2 Load Resources providing Responsive Reserve. ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(C)	The ERCOT Operator may deploy both of the groups of Load Resources providing Responsive Reserves at the same time.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and

(D)	ERCOT shall post a list of Load Resources on the MIS Certified Area immediately following the DRUC for each QSE with a Load Resource obligation which may be deployed to interrupt under paragraph (A), Group 1 and paragraph (B), Group 2.  ERCOT shall develop a process for determining which individual Load Resource to place in Group 1 and which to place in Group 2.  ERCOT procedures shall select Group 1 and Group 2 based on a random sampling of individual Load Resources.  At ERCOT’s discretion, ERCOT may deploy all Load Resources at any given time during EECP Step 2; and

(iii)	With the approval of the affected non-ERCOT Control Area, may instruct TSPs or DSPs to implement BLTs, which transfer Load from the ERCOT Control Area to non-ERCOT Control Areas.  Use of a BLT will be defined in the ERCOT Operating Guides.

(b)	Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

(3)	Step 3 – Maintain system frequency at 60 Hz.  Following deployment of the measures associated with Steps 1 and 2, ERCOT will deploy available contracted EILS Loads, via a single VDI to the all-QSE Hotline; as follows:

(a)	If less than 500 MW of EILS is available for deployment, ERCOT shall deploy all EILS Loads as a single block.

(b)	If the amount of EILS available for deployment equals or exceeds 500 MW, ERCOT may deploy EILS Loads as a single block or may deploy EILS Loads sequentially in two groups of approximately equal size as designated by ERCOT.  For a sequential group deployment, ERCOT shall instruct QSEs to deploy Group 1 immediately and to deploy Group 2 at a specified time in the future.  ERCOT shall develop a random selection methodology for determining which individual EILS Loads to place in Group 1 and which to place in Group 2, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to an EILS Contract Period ERCOT shall notify QSEs representing EILS Loads of their EILS Loads’ Group assignments.

(c)	QSEs shall instruct the EILS Loads to curtail Load consistent with their commitments.

(d)	EILS may be deployed at any time in a Settlement Interval.

(e)	Once ERCOT has deployed EILS, EILS Loads shall remain reduced until ERCOT specifically releases the EILS deployment via a VDI to the all-QSE Hotline.

(f)	Unless scheduled to go Off-Line, due either to an EILS Time Period transition or a previously scheduled period of unavailability, an EILS Load deployed for EILS shall return to its committed operating level as soon as practical following an ERCOT recall.  All EILS Load shall return to normal within ten hours of being recalled.

(g)	Unless a media appeal is already in effect, ERCOT shall issue an appeal through the public news media for voluntary energy conservation.

(4)	Step 4 - Maintain system frequency at 59.8 Hz or greater.

(a)	In addition to measures associated with Steps 1, 2 and 3, ERCOT will direct all TSPs and DSPs or their agents to shed firm load, in 100 MW blocks, as documented in the ERCOT Operating Guides in order to maintain a steady state system frequency of 59.8 Hz.

(b)	In addition to measures associated with Steps 1, 2 and 3, TSPs and DSPs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs and DSPs shall not manually drop load connected to under-frequency relays during the implementation of theEECP.