## Sheet2
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## Sheet1
TRANSMISSION LOSS FACTORS for 2009 as of 11/06/2008
Data from Seasonal SSWG Base Cases Updated with updates received by 9/10/08
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN NOIE INTERNAL TOTAL |  |  |  |  | CPS NOIE INTERNAL TOTAL |  |  |  |  | COG NOIE INTERNAL TOTAL |  |  |  |  | GEUS NOIE INTERNAL TOTAL |  |  |  |  | COD NOIE INTERNAL TOTAL |  |  |  |  | BPUB NOIE INTERNAL TOTAL |  |  |  |  | BTU NOIE INTERNAL TOTAL |  |  |  |  | COCS NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 09SPG1 | 62115.4 | 60708.1 | 1313.99 | 1406.11 | 1225 | 2261.7 | 51.55 | 54.65 | 1091.35 | 2058.8 | 4066.7 | 22.43 | 25.39 | 2033.29 | 90.6 | 293.2 | 2.38 | 2.38 | 204.98 | 23 | 67.5 | 0.15 | 0.15 | 44.65 | 0 | 300.6 | 2.23 | 2.23 | 302.83 | 43 | 236 | 0.26 | 0.26 | 193.26 | 25.6 | 341.7 | 3.02 | 3.13 | 319.23 | 0 | 134.9 | 0.09 | 0.09 | 134.99
Spring Off Peak | 09SPG2 | 38840.9 | 38048.8 | 739.14 | 791.24 | 601 | 1200 | 30.55 | 31.74 | 630.74 | 1740 | 2108.1 | 9.94 | 12.33 | 380.43 | 62.7 | 162.5 | 1.07 | 1.07 | 100.87 | 0 | 42.2 | 0.05 | 0.05 | 42.25 | 0 | 82.7 | 0.51 | 0.51 | 83.21 | 0 | 115 | 0.08 | 0.08 | 115.08 | 25.6 | 165.1 | 0.75 | 0.84 | 140.34 | 0 | 60.6 | 0.03 | 0.03 | 60.63
Summer On Peak | 09SUM1 | 74769.1 | 73073.4 | 1569.32 | 1694.74 | 1237 | 2486 | 59.76 | 63.18 | 1312.18 | 4206.6 | 4647.6 | 32.51 | 39.3 | 480.3 | 387.3 | 497 | 5.68 | 5.68 | 115.38 | 67 | 114.2 | 0.55 | 0.56 | 47.76 | 0 | 334 | 2.85 | 2.85 | 336.85 | 94.4 | 290 | 0.36 | 0.36 | 195.96 | 175.6 | 365.4 | 3.36 | 3.51 | 193.31 | 0 | 195.5 | 0.1 | 0.1 | 195.6
Summer Off Peak | 09SUM2 | 44458 | 43376.9 | 1014.96 | 1079.88 | 630 | 1425 | 31.37 | 32.98 | 827.98 | 1844.4 | 2502.6 | 11.6 | 14.19 | 672.39 | 158.4 | 262.4 | 1.79 | 1.79 | 105.79 | 25 | 69.6 | 0.17 | 0.17 | 44.77 | 0 | 170.5 | 1.22 | 1.22 | 171.72 | 47 | 148 | 0.09 | 0.1 | 101.1 | 34 | 169.9 | 0.91 | 1.05 | 136.95 | 0 | 89.9 | 0.03 | 0.03 | 89.93
Fall On Peak | 09FAL1 | 59414.8 | 58185.8 | 1137.41 | 1228.39 | 1106.8 | 2080 | 54.28 | 56.87 | 1030.07 | 2756 | 3713.6 | 15.94 | 20.27 | 977.87 | 199.9 | 410.6 | 3.05 | 3.05 | 213.75 | 54 | 98.3 | 0.36 | 0.66 | 44.96 | 0 | 269.9 | 1.85 | 1.85 | 271.75 | 47 | 245 | 0.27 | 0.27 | 198.27 | 25.6 | 340.9 | 2.79 | 2.9 | 318.2 | 0 | 164.3 | 0.1 | 0.1 | 164.4
Fall Off Peak | 09FAL2 | 36921.6 | 36101.5 | 766.01 | 819.4 | 399.4 | 1115 | 31.19 | 32.14 | 747.74 | 1951.8 | 1849.6 | 8.26 | 10.87 | -91.33 | 104.3 | 208.9 | 1 | 1 | 105.6 | 16 | 61.6 | 0.11 | 0.38 | 45.98 | 0 | 113.3 | 0.77 | 0.77 | 114.07 | 0 | 130 | 0.11 | 0.11 | 130.11 | 0 | 169.6 | 1.07 | 1.08 | 170.68 | 0 | 76.3 | 0.04 | 0.04 | 76.34
Winter On Peak | 10WIN1 | 58426 | 57136.8 | 1198.18 | 1287.88 | 596.4 | 1848 | 38.85 | 40.06 | 1291.66 | 1776 | 3067.6 | 13.06 | 16.01 | 1307.61 | 160.3 | 371.4 | 3.02 | 3.03 | 214.13 | 36 | 89.7 | 0.27 | 0.42 | 54.12 | 0 | 190.8 | 1.66 | 1.66 | 192.46 | 44 | 236 | 0.27 | 0.27 | 192.27 | 25.6 | 321 | 3.02 | 3.13 | 298.53 | 0 | 156.4 | 0.11 | 0.11 | 156.51
Winter Off Peak | 10WIN2 | 41124.9 | 40206.2 | 851.57 | 917.63 | 297.8 | 980 | 20.69 | 21.53 | 703.73 | 1661.2 | 2112.6 | 8.9 | 11.42 | 462.82 | 142.9 | 251.6 | 1.63 | 1.64 | 110.34 | 0 | 53 | 0.08 | 0.08 | 53.08 | 0 | 97.4 | 0.95 | 0.95 | 98.35 | 0 | 154.9 | 0.14 | 0.14 | 155.04 | 32 | 183.3 | 1.54 | 1.67 | 152.97 | 0 | 139.1 | 0.06 | 0.06 | 139.16
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 09SPG1 | 2907 | 1314.1 | 523.7 | 25.6 | 148.4 | 0 | 4918.8 |  | 7702.3 | 4324.58 | 3377.72 | 82.11 | 09SPG1
Spring Off Peak | 09SPG2 | 2907 | 1314.1 | 523.7 | 25.6 | 148.4 | 0 | 4918.8 |  | 3936.2 | 1553.55 | 2382.65 | 42.98 | 09SPG2
Summer On Peak | 09SUM1 | 2907 | 1295.32 | 523.7 | 32 | 148.4 | 0 | 4906.42 |  | 8929.7 | 2877.34 | 6052.36 | 105.17 | 09SUM1
Summer Off Peak | 09SUM2 | 2907 | 1302.02 | 523.7 | 32 | 148.4 | 0 | 4913.12 |  | 4837.9 | 2150.63 | 2687.27 | 47.18 | 09SUM2
Fall On Peak | 09FAL1 | 2907 | 1300.1 | 523.7 | 25.6 | 148.4 | 0 | 4904.8 |  | 7322.6 | 3219.27 | 4103.33 | 78.64 | 09FAL1
Fall Off Peak | 09FAL2 | 2907 | 1300.1 | 523.7 | 0 | 148.4 | 0 | 4879.2 |  | 3724.3 | 1299.19 | 2425.11 | 42.55 | 09FAL2
Winter On Peak | 10WIN1 | 2907 | 1314 | 523.7 | 25.6 | 148.4 | 0 | 4918.7 |  | 6280.9 | 3707.29 | 2573.61 | 60.26 | 10WIN1
Winter Off Peak | 10WIN2 | 2907 | 1298.21 | 523.7 | 32 | 148.4 | 0 | 4909.31 |  | 3971.9 | 1875.49 | 2096.41 | 33.99 | 10WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 57196.6 | 33922.1 | 2.297% | 2.179% |  | 2261.7 | 1200 | 2.228% | 2.483% |  | 4066.7 | 2108.1 | 0.5485% | 0.4693% |  | 293.2 | 162.5 | 0.8052% | 0.6542% |  | 67.5 | 42.2 | 0.2217% | 0.1183% |  | 300.6 | 82.7 | 0.7364% | 0.6129% |  | 236 | 115 | 0.11% | 0.06952% |  | 341.7 | 165.1 | 0.8761% | 0.4522% |  | 134.9 | 60.6 | 0.06667% | 0.04948%
SUMMER | 69862.68 | 39544.88 | 2.246% | 2.567% |  | 2486 | 1425 | 2.347% | 2.154% |  | 4647.6 | 2502.6 | 0.6946% | 0.4614% |  | 497 | 262.4 | 1.13% | 0.6775% |  | 114.2 | 69.6 | 0.4793% | 0.2437% |  | 334 | 170.5 | 0.8461% | 0.7105% |  | 290 | 148 | 0.124% | 0.06077% |  | 365.4 | 169.9 | 0.9112% | 0.5328% |  | 195.5 | 89.9 | 0.05112% | 0.03336%
FALL | 54510 | 32042.4 | 2.087% | 2.391% |  | 2080 | 1115 | 2.543% | 2.721% |  | 3713.6 | 1849.6 | 0.4274% | 0.4446% |  | 410.6 | 208.9 | 0.7373% | 0.4764% |  | 98.3 | 61.6 | 0.3649% | 0.1783% |  | 269.9 | 113.3 | 0.6808% | 0.675% |  | 245 | 130 | 0.1101% | 0.08454% |  | 340.9 | 169.6 | 0.8118% | 0.6269% |  | 164.3 | 76.3 | 0.06083% | 0.0524%
WINTER | 53507.3 | 36215.59 | 2.239% | 2.351% |  | 1848 | 980 | 2.059% | 2.068% |  | 3067.6 | 2112.6 | 0.4239% | 0.4195% |  | 371.4 | 251.6 | 0.8066% | 0.6437% |  | 89.7 | 53 | 0.3001% | 0.1507% |  | 190.8 | 97.4 | 0.8625% | 0.9659% |  | 236 | 154.9 | 0.1143% | 0.0903% |  | 321 | 183.3 | 0.932% | 0.8332% |  | 156.4 | 139.1 | 0.07028% | 0.04312%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  | For Testing Only |  |  | AEN NOIE INTERNAL |  | For Testing Only |  |  | CPS NOIE INTERNAL |  | For Testing Only |  |  | COG NOIE INTERNAL |  | For Testing Only |  |  | GEUS NOIE INTERNAL |  | For Testing Only |  |  | COD NOIE INTERNAL |  | For Testing Only |  |  | BPUB NOIE INTERNAL |  | For Testing Only |  |  | BTU NOIE INTERNAL |  | For Testing Only |  |  | COCS NOIE INTERNAL |  | For Testing Only
| SSC | SIC | 42555.9 |  |  | SSC | SIC | 2022.1 |  |  | SSC | SIC | 2920.1 |  |  | SSC | SIC | 381.1 |  |  | SSC | SIC | 77.1 |  |  | SSC | SIC | 252 |  |  | SSC | SIC | 204 |  |  | SSC | SIC | 279 |  |  | SSC | SIC | 108
SPRING | 5.0866e-06 | 2.0064 | 2.2229 |  |  | -0.00023939 | 2.7699 | 2.2858 |  |  | 4.045e-05 | 0.38403 | 0.50215 |  |  | 0.0011556 | 0.46636 | 0.90678 |  |  | 0.0040864 | -0.054104 | 0.26096 |  |  | 0.00056668 | 0.56604 | 0.70885 |  |  | 0.00033497 | 0.030995 | 0.099329 |  |  | 0.0024001 | 0.05596 | 0.72559 |  |  | 0.00023137 | 0.035459 | 0.060448
SUMMER | -1.0565e-05 | 2.9844 | 2.5348 |  |  | 0.00018233 | 1.8942 | 2.2629 |  |  | 0.00010875 | 0.18923 | 0.50678 |  |  | 0.0019284 | 0.17153 | 0.90644 |  |  | 0.0052835 | -0.12408 | 0.28328 |  |  | 0.00082945 | 0.56904 | 0.77806 |  |  | 0.00044514 | -0.0051072 | 0.085702 |  |  | 0.0019356 | 0.2039 | 0.74393 |  |  | 0.00016823 | 0.018235 | 0.036404
FALL | -1.3531e-05 | 2.8242 | 2.2484 |  |  | -0.0001844 | 2.9268 | 2.5539 |  |  | -9.2269e-06 | 0.46166 | 0.43472 |  |  | 0.0012936 | 0.20618 | 0.69918 |  |  | 0.0050855 | -0.13501 | 0.25708 |  |  | 3.6709e-05 | 0.67086 | 0.68012 |  |  | 0.00022208 | 0.055674 | 0.10098 |  |  | 0.001079 | 0.44394 | 0.74499 |  |  | 9.5796e-05 | 0.045088 | 0.055434
WINTER | -6.4833e-06 | 2.5862 | 2.3103 |  |  | -9.8919e-06 | 2.0773 | 2.0573 |  |  | 4.6289e-06 | 0.40974 | 0.42325 |  |  | 0.0013597 | 0.30157 | 0.81977 |  |  | 0.0040704 | -0.065016 | 0.24881 |  |  | -0.0011073 | 1.0738 | 0.79475 |  |  | 0.00029564 | 0.044504 | 0.10482 |  |  | 0.00071814 | 0.70152 | 0.90188 |  |  | 0.0015704 | -0.17532 | -0.0057223