ERCOT Operations Report

November 2008 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 11/1/2008 0:32 | 59.842 | 10 | Unit trip with 790 MW online |
| 11/6/2008 12:20 | 59.776 | 111 | Unit trip with 760 MW online |
| 11/6/2008 13:50 | 60.118 | 158 | Out of DRS due to SCE +800 in 10 min, then at 13:45 non-spin deployed to cover unit trip from 12:20. Steel mill load drop of 100 MW in 1 min |
| 11/10/2008 18:03 | 60.101 | 4 | SCE +330 in 3 min, steel mill load drop of 130 MW in 1 min |
| 11/10/2008 18:28 | 59.898 | 4 | Unit trip with 250 MW online |
| 11/12/2008 0:01 | 60.102 | 780 | 800 MW of balancing energy cleared to recover URS, then OOMEs expired and units slow to respond |
| 11/14/2008 14:59 | 60.101 | 148 | SCE +1050 in 13 min |
| 11/17/2008 9:01 | 59.836 | 85 | Unit trip with 750 MW online |
| 11/20/2008 20:32 | 59.875 | 4 | Unit trip with 750 MW online |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 11/01 00:32:12 | 11/01 00:49:00 | 0:16:48 | 666.64 |  |
| 11/01 22:05:10 | 11/01 22:11:24 | 0:06:14 | 317.69 | SCE change -1530 MW in 10 min |
| 11/03 17:30:34 | 11/03 17:46:32 | 0:15:58 | 322.90 | SCE change -360 MW in 2 min |
| 11/04 12:01:08 | 11/04 12:12:20 | 0:11:12 | 338.53 | SCE change -1000 MW in 10 min |
| 11/06 12:20:56 | 11/06 13:18:00 | 0:57:04 | 1010.40 |  |
| 11/09 17:53:54 | 11/09 18:16:18 | 0:22:24 | 343.74 | Out of URS, SCE change -290 MW in 8 min |
| 11/10 18:28:52 | 11/10 18:39:24 | 0:10:32 | 374.99 |  |
| 11/10 20:18:52 | 11/10 20:27:48 | 0:08:56 | 338.53 | SCE change -200 MW in 2 min, Steel Mill Load change pick up 180 MW in 1 min |
| 11/10 20:49:10 | 11/10 21:05:24 | 0:16:14 | 333.33 | Out of URS, Steel Mill Load pick up 120 MW in 3 min, STLF was 600 MW lower |
| 11/11 22:04:58 | 11/11 22:19:20 | 0:14:22 | 328.10 | Input error in offset calculation |
| 11/17 09:01:46 | 11/17 09:29:12 | 0:27:26 | 968.69 | Unit Trip |
| 11/20 20:32:22 | 11/20 20:44:08 | 0:11:46 | 494.77 |  |
| 11/20 22:16:48 | 11/20 22:25:40 | 0:08:52 | 359.35 | SCE change -460 MW in 5 min |
| 11/25 05:08:40 | 11/25 05:16:16 | 0:07:36 | 317.69 | Unit Trip, SCE change -230 MW in 5 min |
| 11/26 22:04:38 | 11/26 22:12:42 | 0:08:04 | 322.9 | SCE change -600 MW in 9 min |

Day-Ahead OOMC and RMR Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | Total |
| --- | --- | --- | --- | --- |
| W RIO | 53 | 12 | 0 | 65 |
| DFW | 0 | 0 | 15 | 15 |
| Western | 6 | 0 | 8 | 14 |
| Austin | 0 | 4 | 7 | 11 |
| San Antonio | 0 | 2 | 8 | 10 |
| E RIO | 1 | 7 | 0 | 8 |
| South | 0 | 6 | 0 | 6 |
| Houston | 1 | 2 | 1 | 4 |
| Laredo | 0 | 3 | 0 | 3 |
| Northeast | 2 | 0 | 0 | 2 |
| North | 0 | 1 | 1 | 2 |
| Bryan Area | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 0 |
|  | 63 | 37 | 40 | 140 |

| Historical Totals | Nov-07 | Oct-08 | Nov-08 |
| --- | --- | --- | --- |
| Austin | 19 | 6 | 11 |
| Bryan Area | 0 | 0 | 0 |
| Corpus | 2 | 19 | 0 |
| DFW | 8 | 3 | 15 |
| E RIO | 9 | 5 | 8 |
| Houston | 29 | 0 | 4 |
| Laredo | 57 | 2 | 3 |
| North | 11 | 2 | 2 |
| Northeast | 0 | 0 | 2 |
| San Antonio | 16 | 5 | 10 |
| South | 0 | 2 | 6 |
| W RIO | 31 | 95 | 65 |
| Western | 64 | 7 | 14 |
| Total | 246 | 146 | 140 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Sandow - Austrop 345KV | Sandow Switch - Elgin 138KV | 17 |
| Aspermont or Scurry Switch - Spur 138KV | Girard Tap - DKEC Jayton 69KV | 17 |
| Menard - Gillespie/San Angelo 138KV | Menard 138/69KV Transformer 1 | 15 |
| Oasis – PH Robinson | Midtown – Garrott 138 kV | 9 |
| Golden Switch - Bluff Creek 138KV | Sun Switch - Sacroc/Golden Switch 138KV | 8 |
| King - Kuykendahl - Roans Switch & Jewett - Tomball 345KV | Garrott - Midtown 138KV | 6 |
| PH Robinson 345/138KV Transformer 3 or 4 | Garrott - Midtown 138KV | 5 |
| Austrop - Lost Pines 345KV | Fayetteville - Winchester 138KV | 4 |
| Dilley Switch - San Miguel 138KV | Pearsall - Derby 69KV | 3 |
| Aspermont - Spur 138KV | Spur 138/69KV | 3 |
| Comanche Peak - Venus Switch 345KV | Comanche Peak - Decordova 345KV | 3 |
| Eagle Mountain - Parker Switch - Roanoke Switch 345KV | West Denton - Airport or Roanoke Switch 138KV | 3 |
| Jewett - Tomball 345KV | Garrott - Midtown 138KV | 2 |
| Lon Hill - North Edinburg 345KV | Lon Hill - Kingsville 138KV | 2 |
| Moss Switch - Holt Switch 138KV | Odessa North 138/69KV transformer 1 | 2 |
| STP - Elm Creek 345KV | Blessing - Lolita 138KV | 2 |
| Odessa EHV - Morgan Creek and Quail Switch 345KV | Stanton East Switching Station - Midland East 138KV | 2 |
| Odessa EHV - Morgan Creek and Quail Switch 345KV | Big Springs Switch - Big Spring West | 2 |
| Elm Creek - San Miguel 345KV | San Miguel Switchyard 345/138KV autotransformer A | 2 |
| Scurry Switch - Spur 138KV | Matador - Paducah Tap 69KV | 2 |
| Dilley Switch - North Laredo 138KV | Asherton - North Laredo Switch 138KV | 2 |
| Temple Creek -Tradinghouse and Temple Switch - Lake Creek 345KV | Menard - San Angelo 138KV | 1 |
| Comanche Peak #1 & #2 | Weatherford - Agnes 138KV | 1 |
| Dyann - East Bernard 138KV | Lane City - Blessing 138KV | 1 |
| LaPalma - Loma Alta 138KV | Military Highway 138/69KV transformer 2 | 1 |
| Loop 337 - Comal 138KV | Seguin - Seguin West 138KV | 1 |
| Comal - Loop 337 138KV | Structural Metals - McQueeny 138KV | 1 |
| Roanoke - West Denton 345KV | West Denton - Teasley 138KV | 1 |
| STP - Hillje and Whitepoint 345KV | Blessing - Lolita 138KV | 1 |
| North Edinburg - Rio Hondo 345KV | Stewart Road - Weslaco 138KV | 1 |
| Austrop T2 autotransformer 345/138KV | Austrop T1 autotransformer 345/138KV | 1 |
| Elm Mott - Whitney TU 138KV | Lake Whitney - Whitney TU 138KV | 1 |
| Paris Switch - Valley SES 345KV | Paris Switch 345/138KV autotransformer 1 | 1 |
| Lon Hill - Coleto Creek 345KV | Victoria - Warburton 138KV | 1 |
| Grant - HO Clark 138KV | Garrott - Midtown 138KV | 1 |
| Odessa EHV - Morgan SES Quail Switch 345KV | Lamesa 138/69KV autotransformer | 1 |
| Morgan Creek - Eskota Switch 138KV | Trent - Merkel 69KV | 1 |
| South Channel - Jefferson 138KV | Crown - Galena Park 138KV | 1 |
| Garfield - Onion & Hicross 138KV | Lytton Springs - Pilot Knob 138KV | 1 |
| Holt Switch 138/69KV transformer | Odessa North 138/69KV transformer #1 | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North-Houston | 1 |
| West-North | 17 |
| North-West | 1 |

New RAP (Date indicates last update of RAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 11/25/2008 | Frequency Control Desk V 3 Rev 71 | 392 |
| 11/25/2008 | Transmission & Security Desk V 3 Rev 97 | 391 |
| 11/25/2008 | Shift Supervisor Desk, V3, Rev 52 | 390 |
| 11/04/2008 | Day Ahead Desk, V3R37 | 389 |

## Blackout/Load Shed Incidences

None

EECP

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

11/10   18:58	ERCOT held the deployments for IE 18:45 and resumed with the deployments for IE 20:00 There were a total of 4 held intervals.

Communication

None

## ERCOT peak (Unofficial)

11/05 	   16:00 38,284 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2005 | 2006 | 2007 | 2008 |
| January | 5.02 | 4.79 | 4.55 | 3.30 |
| February | 3.47 | 4.81 | 3.75 | 3.59 |
| March | 3.41 | 4.95 | 2.70 | 3.29 |
| April | 3.37 | 5.59 | 3.00 | 2.45 |
| May | 4.21 | 3.59 | 3.22 | 3.01 |
| June | 3.91 | 2.65 | 4.46 | 2.81 |
| July | 5.22 | 2.62 | 4.29 | 2.55 |
| August | 4.86 | 2.09 | 3.11 | 3.66 |
| September | 6.24 | 4.03 | 3.78 | 4.99 |
| October | 4.51 | 3.63 | 3.08 | 2.79 |
| November | 4.53 | 3.28 | 2.95 | 2.60 |
| Annual Average | 4.56 | 3.79 | 3.55 | 3.18 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 11/1/08 | 15:28 | 23:15 | Advisory ARR below 3000 MW. |
| 11/3/08 | 4:26 | 8:00 | OCN issued for projected capacity shortage for HE 1800 - 1900. |
| 11/5/08 | 13:12 | 20:49 | Advisory ARR below 3000 MW. |
| 11/6/08 | 12:40 | 19:56 | Advisory ARR below 3000 MW. |
| 11/6/08 | 13:22 | 16:00 | Deployed NSRS in all zones due to depleted Up Balancing Energy bids. |
| 11/7/08 | 6:30 | 10:00 | Advisory ARR below 3000 MW. |
| 11/8/08 | 8:45 | 13:10 | Advisory ARR below 3000 MW. |
| 11/9/08 | 18:25 | 20:42 | Advisory ARR below 3000 MW. |
| 11/10/08 | 11:15 | 22:52 | Advisory ARR below 3000 MW. |
| 11/10/08 | 11:15 | 15:10 | OCN issued for projected capacity shortage for HE 1900 - 2000. |
| 11/10/08 | 17:00 | 20:30 | Deployed NSRS in all zones due to projected depletion of Up Balancing Energy bids. |
| 11/11/08 | 0:45 | 10:25 | OCN issued for projected capacity shortage for HE 1300 - 2400. |
| 11/11/08 | 10:25 | 12:00 | Advisory ARR below 3000 MW. |
| 11/11/08 | 18:15 | 20:00 | Advisory ARR below 3000 MW. |
| 11/12/08 | 17:58 | 20:00 | Advisory ARR below 3000 MW. |
| 11/15/08 | 15:40 | 21:00 | OCN issued for projected capacity shortage for HE 1900 - 2000. |
| 11/15/08 | 17:40 | 0:00 | Advisory ARR below 3000 MW. |
| 11/15/08 | 17:53 | 21:00 | Deployed NSRS in all zones due to a projected depletion of up balancing energy bids. |
| 11/16/08 | 0:15 | 1:00 | Advisory ARR below 3000 MW. |
| 11/18/08 | 17:45 | 19:40 | Advisory ARR below 3000 MW. |
| 11/22/08 | 13:50 | 14:54 | OCN issued for projected capacity shortage for hour ending 18:00 - 20:00. |
| 11/22/08 | 14:55 | 15:40 | Alert issued for projected capacity shortage for HE 1800 - 2000. |
| 11/25/08 | 5:05 | 9:50 | Advisory ARR below 3000 MW. |
| 11/26/08 | 5:15 | 15:10 | Advisory ARR below 3000 MW. |
| 11/26/08 | 22:15 | 0:00 | Advisory ARR below 3000 MW. |
| 11/26/08 | 23:06 | 0:00 | OCN issued for a projected capacity shortage on 11/27/08 for HE 0900 - 1200. |
| 11/27/08 | 0:00 | 0:15 | Advisory ARR below 3000 MW. |
| 11/27/08 | 0:00 | 0:20 | OCN issued for projected capacity shortage for HE 0900 - 1200. |
| 11/27/08 | 0:21 | 0:55 | Alert issued for a projected capacity shortage for HE 0900 - 1200. |
| 11/27/08 | 10:00 | 14:40 | Advisory ARR below 3000 MW. |
| 11/28/08 | 9:40 | 20:00 | Advisory ARR below 3000 MW. |
| 11/29/08 | 17:35 | 21:35 | Advisory ARR below 3000 MW. |
| 11/30/08 | 17:30 | 22:00 | Advisory ARR below 3000 MW. |
| 11/30/08 | 18:42 | 21:00 | Alert ARR below 2500 MW. |
| 11/30/08 | 18:48 | 21:00 | Deployed NSRS in North zone due to Alert for Adjusted Responsive Reserve below 2500 MW. |

Emergency Notice

11/17   18:10	Emergency Notice issued for Replacement Reserve Service Market failed to solve correctly for Tuesday 11/18/08 not meeting the 18:00 required timeline.

11/11   18:05   Emergency Notice issued for Replacement Reserve Service Market failed to solve correctly not meeting the 18:00 required timeline.

11/27   11:27   Emergency Notice issued so that an emergency DC Tie schedule could be started on the Railroad South DC Tie.

Texas RE Event Analysis

11/14  00:03	SPS at Stanton Wind Energy Center SPS Activated: ERCOT determination operated as intended.

11/21  23:01	SPS at Stanton Wind Energy Center SPS Activated.

11/24  01:26	SPS at Stanton Wind Energy Center SPS Activated.

Other

11/11   17:52	Held Real-time Balancing Market IE 18:00 for IE 18:15 due to short term load forecast error, resumed with IE 18:30.

11/20   11:00	Held IE 11:00 real-time balancing deployments for IE 11:15, resumed with IE 11:30 deployments.