| PRR Number | 788 | PRR Title | Ramp Rate Limits for Existing WGRs |
| --- | --- | --- | --- |
| Date |  | December 15, 2008 |  |
| Submitter’s Information |  |  |  |
| Name |  | Henry Durrwachter |  |
| E-mail Address |  | hdurrwachter@luminant.com |  |
| Company |  | Luminant Energy Company LLC |  |
| Phone Number |  | 214-875-9285 |  |
| Cell Number |  | 214-437-4622 |  |
| Market Segment |  | Investor-Owned Utility (IOU) |  |

Comments

| Overall Market Benefit |  |
| --- | --- |
| Overall Market Impact |  |
| Consumer Impact |  |

Luminant Energy believes that ramp rate performance by a Wind-powered Generation Resource (WGR) is solely the responsibility of the WGR, not the Qualified Scheduling Entity (QSE) as the proposed Section 6.5.13, paragraph (9) of this Protocol Revision Request (PRR) envisions.  Ramp rate performance can only be controlled by the WGR, since the QSE does not control individual generating units at a WGR site.  Thus, Luminant Energy’s comments below delete the reference to QSEs in Section 6.5.13, paragraph (9).  Furthermore, Luminant Energy believes that it is important that the events that would exempt WGRs from the requirements of Section 6.5.13, paragraph (1) or paragraph (3) should be clearly delineated so we offer those changes as well.

Revised Proposed Protocol Language

6.5.13 	WGR Ramp Rate Limitations

- Each Wind-powered Generating Resource (WGR) which is part of an Interconnection Agreement signed on or after January 1, 2009 shall limit its ramp rate to ten percent (10%) per minute of its nameplate rating (MWs) as registered with ERCOT when responding to or released from an ERCOT deployment.

- The requirement of paragraph (1) above does not apply during a Force Majeure Event or during intervals in which a decremental deployment instruction coincides with a demonstrated decrease in the available wind resource.

- Each WGR which is part of an Interconnection Agreement signed on or before December 31, 2008 and which controls power output by means other than turbine stoppage shall limit its ramp rate to ten percent (10%) per minute of its nameplate rating (MWs) as registered with ERCOT when responding to or released from an ERCOT deployment.

- The requirement of paragraph (3) above does not apply during a Force Majeure Event, during intervals in which a decremental deployment instruction coincides with a demonstrated decrease in the available wind resource, or during unit start up and shut down mode.

- WGRs which meet the technical specifications of paragraph (3) above and which do not comply with its ramp rate requirement shall submit a compliance plan to ERCOT on or before June 1, 2009 which details the technical limitations leading to non-compliance, a work plan to achieve compliance by a reasonable date, and a ramp rate mitigation plan describing the WGR’s best efforts to adhere to the WGR ramp rate limitation during the applicable compliance transition period.

- WGRs which do not meet the technical specifications of paragraph (3) above must submit an operations plan to ERCOT on or before June 1, 2009 describing the WGR’s best efforts to adhere to the WGR ramp rate limitation.

- WGRs subject to the ramp rate limitations of paragraphs (1) and (3) above are exempt from the requirements of the applicable section upon receipt of a valid dispatch instruction from ERCOT to exceed the applicable ramp rate limitation when necessary to protect system reliability.

- WGRs which operate under a Special Protection Scheme (SPS) are exempt from the ramp rate limitations of paragraphs (1) and (3) above when decreasing unit output to avoid SPS activation.

- WGRs which meet the requirements of paragraphs (1) and (3) above shall be deemed non-compliant with ramp rate limitation requirements when the number of 10-minute averages of eligible intervals meeting ten percent (10%) of nameplate capacity per minute ramp rate limit is less than ninety percent (90%) of eligible intervals per month.  Intervals where paragraphs (2), (4), (7) or (8) above apply shall be excluded as eligible intervals for this performance metric.