## Slide 1: 2008 ERCOT LaaRs CAPABILITY STUDY
Conducted by ERCOT DWG

## Slide 2: STUDY DURATION
Long study duration. Required engineering people-hours >>> Available engineering people-hours.
  Time intensive study. Massive amount of work involved with preparing model data, planning simulations, running simulations, interpreting results, planning and running follow-up simulations.
  DWG engineering people-hours became scarce in 2008. DWG composed of volunteers from TSPs within ERCOT. DWG members experienced a significant shift in workloads within their companies during 2008. In addition to normal transmission planning duties:
    Surge in generation interconnect studies
    Surge in industrial load facility interconnect studies
    Special reliability studies
  Lost some DWG expertise in 2008 due to promotion/reassignment of duties.

## Slide 3: STUDY RESULTS
For making a decision on the maximum amount of LaaRs that can be reliably deployed via underfrequency relaying:
The driver is how the LaaR relays are, or will be set in terms of frequency trip setting. In general:
  Lowest allowable LaaR amounts correspond to scenarios where all LaaRs trip at the same frequency.
  Higher LaaR amounts are allowable to varying degrees as LaaRs are spread out over a range of trip frequencies.
The secondary consideration is how the LaaRs are, or will be geographically distributed.
Section 6.10.3.2 of the ERCOT Protocols allow a LaaR to be deployed at up to 150% of the amount requested by ERCOT at the time of testing the LaaR. This potential variance between contracted and actual LaaR amount should be considered when establishing LaaR limits.

## Slide 4: NEXT STEPS
At this point, the DWG seeks the following answers from ROS/TAC:
Are the study conclusions pertaining to the 59.7 Hz tier sufficient for ROS/TAC decision making?
Lacking quantitative conclusions for the 59.8 Hz tier…
  Is there still a need for higher tier LaaRs?
  If so, we need to specify the following 59.7 Hz tier parameters for such analysis:
    LaaR relay trip frequencies.
    LaaR locations.