## Report
| Report No. | ERCOT20000101 |  |  | Date : | 2000-01-01 01:12 |  |  | Time (HHMMSS): |  | 36526.0497
| 1 |  |  |  | Time Standard |  |  |  | BA BIAS | -660 | MW/0.1 Hz
| Scan Rate | 2 | 2 seconds |  | CDT |  |  |  | 55147 | Load @ A
| Freq. (before) |  | Freq. (after) |  | Freq. Chg. |  | Sch. Freq. | FR % of Bias | 54979 | Load @ B
| 59.9848 |  | 59.8592 |  | -0.12557 |  | 60 | 90.49% | -597.2558 | BA MW/0.1 Hz
| Average Before |  | Average After |  |  |  |  | 22.4% | -133.7853 | BA Load MW/0.1 Hz
| Comments File: | [6 empty] | Load FR % of | -660 | Interconnection Total Bias
| Interconnection Minimum Freq Response Target. |  |  |  | -420 | MW/0.1 Hz |  | Total FR | 65340.22 | Interconnection Peak Forecast Load
| BA Performance based on Peak Load Ratio |  |  |  | 142.2% |  |  |  | 65340.22 | BA Peak Forecast Load
| BA Performance based on Bias Ratio |  |  |  | 142.2%
|  |  |  | Frequency Response data report for BA: |  |  |  | ERCOT
T = Time of Disturbance
| Time | F |  | Resource Lost | ACE | Index | [5 empty] | Resource Lost
T-60 sec | 36526.049 | 59.982 |  | 750 | -117.1901 | 1 | [5 empty] | 750
T-58 sec | 36526.049 | 59.979 |  | 750 | -136.7094 | 2 | [5 empty] | 750
T-56 sec | 36526.049 | 59.979 |  | 750 | -136.7094 | 3 | [5 empty] | 750
T-54 sec | 36526.0491 | 59.978 |  | 750 | -143.2158 | 4 | [5 empty] | 750
T-52 sec | 36526.0491 | 59.978 |  | 750 | -143.2158 | 5 | [5 empty] | 750
T-50 sec | 36526.0491 | 59.978 |  | 750 | -143.2158 | 6 | [5 empty] | 750
T-48 sec | 36526.0491 | 59.978 |  | 750 | -143.2158 | 7 | [5 empty] | 750
T-46 sec | 36526.0491 | 59.981 |  | 750 | -123.6966 | 8 | [5 empty] | 750
T-44 sec | 36526.0492 | 59.981 |  | 750 | -123.6966 | 9 | [5 empty] | 750
T-42 sec | 36526.0492 | 59.981 |  | 750 | -123.6966 | 10 | [5 empty] | 750
T-40 sec | 36526.0492 | 59.982 |  | 750 | -117.1901 | 11 | [5 empty] | 750
T-38 sec | 36526.0492 | 59.982 |  | 750 | -117.1901 | 12 | [5 empty] | 750
T-36 sec | 36526.0493 | 59.982 |  | 750 | -117.1901 | 13 | [5 empty] | 750
T-34 sec | 36526.0493 | 59.985 |  | 750 | -97.646 | 14 | [5 empty] | 750
T-32 sec | 36526.0493 | 59.985 |  | 750 | -97.646 | 15 | [5 empty] | 750
T-30 sec | 36526.0493 | 59.984 |  | 750 | -104.1525 | 16 | [5 empty] | 750
T-28 sec | 36526.0494 | 59.984 |  | 750 | -104.1525 | 17 | [5 empty] | 750
T-26 sec | 36526.0494 | 59.981 |  | 750 | -123.6966 | 18 | [5 empty] | 750
T-24 sec | 36526.0494 | 59.981 |  | 750 | -123.6966 | 19 | [5 empty] | 750
T-22 sec | 36526.0494 | 59.981 |  | 750 | -123.6966 | 20 | [5 empty] | 750
T-20 sec | 36526.0494 | 59.981 |  | 750 | -123.6966 | 21 | [5 empty] | 750
T-18 sec | 36526.0495 | 59.983 |  | 750 | -110.6589 | 22 | [5 empty] | 750
T-16 sec | 36526.0495 | 59.983 |  | 750 | -110.6589 | 23 | 59.9848 | 750 |  |  |  | 750
T-14 sec | 36526.0495 | 59.985 |  | 750 | -97.646 | 24 | 59.9848 | 750 |  |  |  | 750
T-12 sec | 36526.0495 | 59.985 |  | 750 | -97.646 | 25 | 59.9848 | 750 |  |  |  | 750
T-10 sec | 36526.0496 | 59.985 |  | 750 | -97.646 | 26 | 59.9848 | 750 |  |  |  | 750
T-08 sec | 36526.0496 | 59.985 |  | 750 | -97.646 | 27 | 59.9848 | 750 |  |  |  | 750
T-06 sec | 36526.0496 | 59.985 |  | 750 | -97.646 | 28 | 59.9848 | 750 |  |  |  | 750
T-04 sec | 36526.0496 | 59.985 |  | 750 | -97.646 | 29 | 59.9848 | 750 |  |  |  | 750
T-02 sec | 36526.0497 | 59.985 |  | 750 | -97.646 | 30 | 59.9848 | 750 |  |  |  | 750
T+0 sec | 36526.0497 | 59.831 |  | 750 | -1100.1817 | 31 | [5 empty] | 750
T+02 sec | 36526.0497 | 59.842 |  | 750 | -1028.5862 | 32 | [5 empty] | 750
T+04 sec | 36526.0497 | 59.842 |  | 0 | -1028.5862 | 33 | [5 empty] | 0
T+06 sec | 36526.0497 | 59.867 |  | 0 | -865.8262 | 34 | [5 empty] | 0
T+08 sec | 36526.0498 | 59.867 |  | 0 | -865.8262 | 35 | [5 empty] | 0
T+10 sec | 36526.0498 | 59.874 |  | 0 | -820.2564 | 36 | [5 empty] | 0
T+12 sec | 36526.0498 | 59.874 |  | 0 | -820.2564 | 37 | [5 empty] | 0
T+14 sec | 36526.0498 | 59.87 |  | 0 | -846.307 | 38 | [5 empty] | 0
T+16 sec | 36526.0499 | 59.87 |  | 0 | -846.307 | 39 | [5 empty] | 0
T+18 sec | 36526.0499 | 59.87 |  | 0 | -846.307 | 40 | [5 empty] | 0
T+20 sec | 36526.0499 | 59.87 |  | 0 | -846.307 | 41 | 59.8592 | 0 |  |  |  | 0
T+22 sec | 36526.0499 | 59.867 |  | 0 | -865.8262 | 42 | 59.8592 | 0 |  |  |  | 0
T+24 sec | 36526.05 | 59.867 |  | 0 | -865.8262 | 43 | 59.8592 | 0 |  |  |  | 0
T+26 sec | 36526.05 | 59.866 |  | 0 | -872.3326 | 44 | 59.8592 | 0 |  |  |  | 0
T+28 sec | 36526.05 | 59.866 |  | 0 | -872.3326 | 45 | 59.8592 | 0 |  |  |  | 0
T+30 sec | 36526.05 | 59.861 |  | 0 | -904.8896 | 46 | 59.8592 | 0 |  |  |  | 0
T+32 sec | 36526.05 | 59.861 |  | 0 | -904.8896 | 47 | 59.8592 | 0 |  |  |  | 0
T+34 sec | 36526.0501 | 59.857 |  | 0 | -930.9401 | 48 | 59.8592 | 0 |  |  |  | 0
T+36 sec | 36526.0501 | 59.857 |  | 0 | -930.9401 | 49 | 59.8592 | 0 |  |  |  | 0
T+38 sec | 36526.0501 | 59.857 |  | 0 | -930.9401 | 50 | 59.8592 | 0 |  |  |  | 0
T+40 sec | 36526.0501 | 59.857 |  | 0 | -930.9401 | 51 | 59.8592 | 0 |  |  |  | 0
T+42 sec | 36526.0502 | 59.854 |  | 0 | -950.4594 | 52 | 59.8592 | 0 |  |  |  | 0
T+44 sec | 36526.0502 | 59.854 |  | 0 | -950.4594 | 53 | 59.8592 | 0 |  |  |  | 0
T+46 sec | 36526.0502 | 59.853 |  | 0 | -956.9658 | 54 | 59.8592 | 0 |  |  |  | 0
T+48 sec | 36526.0502 | 59.853 |  | 0 | -956.9658 | 55 | 59.8592 | 0 |  |  |  | 0
T+50 sec | 36526.0503 | 59.853 |  | 0 | -956.9658 | 56 | 59.8592 | 0 |  |  |  | 0
T+52 sec | 36526.0503 | 59.853 |  | 0 | -956.9658 | 57 | 59.8592 | 0 |  |  |  | 0
T+54 sec | 36526.0503 | 59.853 |  | 0 | -956.9658 | 58 | [5 empty] | 0
T+56 sec | 36526.0503 | 59.853 |  | 0 | -956.9658 | 59 | [5 empty] | 0
T+58 sec | 36526.0503 | 59.854 |  | 0 | -950.4594 | 60 | [5 empty] | 0
T+60 sec | 36526.0504 | 59.854 |  | 0 | -950.4594 | 61 | [5 empty] | 0
36526.0504
Collect scan rate data on Data sheet that includes 60 seconds before and after event. Sheet is set up for 20 Minutes of data.
Data entered once annually
Edit formula in this cell. Change the row number in the formula to the row number on the "Data" sheet where t+0 occurs.
For example, this event t+0 occurs in row 348 so the formula is "=Data!B348"
Enter data for each event.

## Data
Data Start | 2000-01-01 01:00
Data End | 2000-01-01 01:22
|  |  |  | Resource |  |  |  | Resource
|  | Hz | Sch Hz | Lost | ACE | Bias | Load | or Load Lost
| 36526.0417 | 60.015 | 60 | 750 | 97.646 | -651 | 55002.6133
| 36526.0417 | 60.015 | 60 | 750 | 97.646 | -651 | 55008.0859
| 36526.0417 | 60.015 | 60 | 750 | 97.646 | -651 | 55008.0859
| 36526.0417 | 60.014 | 60 | 750 | 91.1396 | -651 | 54987.8086
| 36526.0418 | 60.014 | 60 | 750 | 91.1396 | -651 | 54987.8086
| 36526.0418 | 60.014 | 60 | 750 | 91.1396 | -651 | 54987.8086
| 36526.0418 | 60.014 | 60 | 750 | 91.1396 | -651 | 54987.8086
| 36526.0418 | 60.014 | 60 | 750 | 91.1396 | -651 | 54987.8086
| 36526.0419 | 60.013 | 60 | 750 | 84.6332 | -651 | 54997.5156
| 36526.0419 | 60.013 | 60 | 750 | 84.6332 | -651 | 54997.668
| 36526.0419 | 60.013 | 60 | 750 | 84.6332 | -651 | 54997.668
| 36526.0419 | 60.011 | 60 | 750 | 71.6203 | -651 | 55001.1523
| 36526.0419 | 60.011 | 60 | 750 | 71.6203 | -651 | 55001.1523
| 36526.042 | 60.012 | 60 | 750 | 78.1268 | -651 | 55008.3281
| 36526.042 | 60.012 | 60 | 750 | 78.1268 | -651 | 55008.3281
| 36526.042 | 60.014 | 60 | 750 | 91.1396 | -651 | 55008.0117
| 36526.042 | 60.014 | 60 | 750 | 91.1396 | -651 | 55008.0117
| 36526.0421 | 60.015 | 60 | 750 | 97.646 | -651 | 55003.4258
| 36526.0421 | 60.015 | 60 | 750 | 97.646 | -651 | 55003.4258
| 36526.0421 | 60.016 | 60 | 750 | 104.1525 | -651 | 55002.0938
| 36526.0421 | 60.016 | 60 | 750 | 104.1525 | -651 | 55002.0938
| 36526.0422 | 60.012 | 60 | 750 | 78.1268 | -651 | 54995.6367
| 36526.0422 | 60.012 | 60 | 750 | 78.1268 | -651 | 54995.6367
| 36526.0422 | 60.011 | 60 | 750 | 71.6203 | -651 | 55007.1367
| 36526.0422 | 60.011 | 60 | 750 | 71.6203 | -651 | 55007.1367
| 36526.0422 | 60.01 | 60 | 750 | 65.0891 | -651 | 55006.8398
| 36526.0423 | 60.01 | 60 | 750 | 65.0891 | -651 | 55006.8398
| 36526.0423 | 60.01 | 60 | 750 | 65.0891 | -651 | 55010.9766
| 36526.0423 | 60.01 | 60 | 750 | 65.0891 | -651 | 55010.9766
| 36526.0423 | 60.013 | 60 | 750 | 84.6332 | -651 | 55000.3516
| 36526.0424 | 60.013 | 60 | 750 | 84.6332 | -651 | 55000.3516
| 36526.0424 | 60.014 | 60 | 750 | 91.1396 | -651 | 54996.9258
| 36526.0424 | 60.014 | 60 | 750 | 91.1396 | -651 | 54996.9258
| 36526.0424 | 60.011 | 60 | 750 | 71.6203 | -651 | 55004.5117
| 36526.0425 | 60.011 | 60 | 750 | 71.6203 | -651 | 55004.5117
| 36526.0425 | 60.011 | 60 | 750 | 71.6203 | -651 | 55004.5117
| 36526.0425 | 60.005 | 60 | 750 | 32.557 | -651 | 54998.5391
| 36526.0425 | 60.003 | 60 | 750 | 19.5193 | -651 | 55007.6914
| 36526.0425 | 60.003 | 60 | 750 | 19.5193 | -651 | 55007.6914
| 36526.0426 | 60.003 | 60 | 750 | 19.5193 | -651 | 55007.6914
| 36526.0426 | 60.006 | 60 | 750 | 39.0634 | -651 | 54999.1328
| 36526.0426 | 60.008 | 60 | 750 | 52.0762 | -651 | 54992.6094
| 36526.0426 | 60.008 | 60 | 750 | 52.0762 | -651 | 54992.6094
| 36526.0427 | 60.005 | 60 | 750 | 32.557 | -651 | 55000.4453
| 36526.0427 | 60.005 | 60 | 750 | 32.557 | -651 | 55000.4453
| 36526.0427 | 59.995 | 60 | 750 | -32.557 | -651 | 54998.9844
| 36526.0427 | 59.995 | 60 | 750 | -32.557 | -651 | 54998.9844
| 36526.0428 | 59.992 | 60 | 750 | -52.0762 | -651 | 55002.1914
| 36526.0428 | 59.992 | 60 | 750 | -52.0762 | -651 | 55002.1914
| 36526.0428 | 59.991 | 60 | 750 | -58.5826 | -651 | 55004.5469
| 36526.0428 | 59.991 | 60 | 750 | -58.5826 | -651 | 55004.5469
| 36526.0428 | 59.991 | 60 | 750 | -58.5826 | -651 | 55004.5469
| 36526.0429 | 59.99 | 60 | 750 | -65.0891 | -651 | 54987.5781
| 36526.0429 | 59.99 | 60 | 750 | -65.0891 | -651 | 54978.4648
| 36526.0429 | 59.99 | 60 | 750 | -65.0891 | -651 | 54978.4648
| 36526.0429 | 60.002 | 60 | 750 | 13.0128 | -651 | 54976.1602
| 36526.043 | 60.002 | 60 | 750 | 13.0128 | -651 | 54976.1602
| 36526.043 | 60.003 | 60 | 750 | 19.5193 | -651 | 54947.5039
| 36526.043 | 60.003 | 60 | 750 | 19.5193 | -651 | 54947.5039
| 36526.043 | 60.003 | 60 | 750 | 19.5193 | -651 | 54938.8633
| 36526.0431 | 60.003 | 60 | 750 | 19.5193 | -651 | 54938.8633
| 36526.0431 | 60.004 | 60 | 750 | 26.0505 | -651 | 54929.4805
| 36526.0431 | 60.004 | 60 | 750 | 26.0505 | -651 | 54929.4805
| 36526.0431 | 60.005 | 60 | 750 | 32.557 | -651 | 54933.5938
| 36526.0431 | 60.005 | 60 | 750 | 32.557 | -651 | 54933.5938
| 36526.0432 | 60.005 | 60 | 750 | 32.557 | -651 | 54933.5938
| 36526.0432 | 60.005 | 60 | 750 | 32.557 | -651 | 54938.2266
| 36526.0432 | 60.006 | 60 | 750 | 39.0634 | -651 | 54938.3516
| 36526.0432 | 60.006 | 60 | 750 | 39.0634 | -651 | 54938.3516
| 36526.0433 | 60.006 | 60 | 750 | 39.0634 | -651 | 54938.3516
| 36526.0433 | 60.004 | 60 | 750 | 26.0505 | -651 | 54933.8438
| 36526.0433 | 60.001 | 60 | 750 | 6.5064 | -651 | 54934.2109
| 36526.0433 | 60.001 | 60 | 750 | 6.5064 | -651 | 54934.2109
| 36526.0434 | 59.993 | 60 | 750 | -45.5698 | -651 | 54939.6367
| 36526.0434 | 59.993 | 60 | 750 | -45.5698 | -651 | 54939.6367
| 36526.0434 | 59.99 | 60 | 750 | -65.0891 | -651 | 54936.125
| 36526.0434 | 59.99 | 60 | 750 | -65.0891 | -651 | 54936.125
| 36526.0434 | 59.987 | 60 | 750 | -84.6332 | -651 | 54943.4102
| 36526.0435 | 59.987 | 60 | 750 | -84.6332 | -651 | 54943.4102
| 36526.0435 | 59.984 | 60 | 750 | -104.1525 | -651 | 54941.3477
| 36526.0435 | 59.984 | 60 | 750 | -104.1525 | -651 | 54941.3477
| 36526.0435 | 59.984 | 60 | 750 | -104.1525 | -651 | 54941.3477
| 36526.0436 | 59.989 | 60 | 750 | -71.6203 | -651 | 54925.75
| 36526.0436 | 59.99 | 60 | 750 | -65.0891 | -651 | 54920.3555
| 36526.0436 | 59.99 | 60 | 750 | -65.0891 | -651 | 54920.3555
| 36526.0436 | 59.983 | 60 | 750 | -110.6589 | -651 | 54917.8164
| 36526.0437 | 59.983 | 60 | 750 | -110.6589 | -651 | 54917.8164
| 36526.0437 | 59.98 | 60 | 750 | -130.203 | -651 | 54912.9102
| 36526.0437 | 59.98 | 60 | 750 | -130.203 | -651 | 54912.9102
| 36526.0437 | 59.979 | 60 | 750 | -136.7094 | -651 | 54908.668
| 36526.0437 | 59.979 | 60 | 750 | -136.7094 | -651 | 54908.668
| 36526.0438 | 59.977 | 60 | 750 | -149.7223 | -651 | 54896.9258
| 36526.0438 | 59.977 | 60 | 750 | -149.7223 | -651 | 54896.9258
| 36526.0438 | 59.97 | 60 | 750 | -195.2921 | -651 | 54896.5781
| 36526.0438 | 59.97 | 60 | 750 | -195.2921 | -651 | 54896.5781
| 36526.0439 | 59.967 | 60 | 750 | -214.8362 | -651 | 54908.5352
| 36526.0439 | 59.967 | 60 | 750 | -214.8362 | -651 | 54908.5352
| 36526.0439 | 59.967 | 60 | 750 | -214.8362 | -651 | 54908.5352
| 36526.0439 | 59.966 | 60 | 750 | -221.3426 | -651 | 54906.3516
| 36526.044 | 59.966 | 60 | 750 | -221.3426 | -651 | 54906.3516
| 36526.044 | 59.966 | 60 | 750 | -221.3426 | -651 | 54912.7969
| 36526.044 | 59.971 | 60 | 750 | -188.7856 | -651 | 54912.4648
| 36526.044 | 59.971 | 60 | 750 | -188.7856 | -651 | 54912.4648
| 36526.0441 | 59.969 | 60 | 750 | -201.7985 | -651 | 54907.8242
| 36526.0441 | 59.969 | 60 | 750 | -201.7985 | -651 | 54907.8242
| 36526.0441 | 59.967 | 60 | 750 | -214.8362 | -651 | 54913.6523
| 36526.0441 | 59.967 | 60 | 750 | -214.8362 | -651 | 54913.6523
| 36526.0441 | 59.968 | 60 | 750 | -208.3297 | -651 | 54917.0469
| 36526.0442 | 59.968 | 60 | 750 | -208.3297 | -651 | 54917.0469
| 36526.0442 | 59.971 | 60 | 750 | -188.7856 | -651 | 54906.6367
| 36526.0442 | 59.971 | 60 | 750 | -188.7856 | -651 | 54906.6367
| 36526.0442 | 59.971 | 60 | 750 | -188.7856 | -651 | 54906.6367
| 36526.0443 | 59.969 | 60 | 750 | -201.7985 | -651 | 54911.375
| 36526.0443 | 59.968 | 60 | 750 | -208.3297 | -651 | 54913.4492
| 36526.0443 | 59.968 | 60 | 750 | -208.3297 | -651 | 54913.4492
| 36526.0443 | 59.969 | 60 | 750 | -201.7985 | -651 | 54919.9258
| 36526.0444 | 59.969 | 60 | 750 | -201.7985 | -651 | 54919.9258
| 36526.0444 | 59.97 | 60 | 750 | -195.2921 | -651 | 54933.1289
| 36526.0444 | 59.97 | 60 | 750 | -195.2921 | -651 | 54933.1289
| 36526.0444 | 59.97 | 60 | 750 | -195.2921 | -651 | 54927.3203
| 36526.0444 | 59.97 | 60 | 750 | -195.2921 | -651 | 54927.3203
| 36526.0445 | 59.968 | 60 | 750 | -208.3297 | -651 | 54933.1875
| 36526.0445 | 59.968 | 60 | 750 | -208.3297 | -651 | 54933.1875
| 36526.0445 | 59.973 | 60 | 750 | -175.7728 | -651 | 54927.8438
| 36526.0445 | 59.973 | 60 | 750 | -175.7728 | -651 | 54927.8438
| 36526.0446 | 59.975 | 60 | 750 | -162.7599 | -651 | 54922.4766
| 36526.0446 | 59.975 | 60 | 750 | -162.7599 | -651 | 54922.4766
| 36526.0446 | 59.975 | 60 | 750 | -162.7599 | -651 | 54922.4766
| 36526.0446 | 59.974 | 60 | 750 | -169.2664 | -651 | 54913.4297
| 36526.0447 | 59.974 | 60 | 750 | -169.2664 | -651 | 54913.4297
| 36526.0447 | 59.974 | 60 | 750 | -169.2664 | -651 | 54913.1328
| 36526.0447 | 59.97 | 60 | 750 | -195.2921 | -651 | 54922.707
| 36526.0447 | 59.97 | 60 | 750 | -195.2921 | -651 | 54922.707
| 36526.0447 | 59.973 | 60 | 750 | -175.7728 | -651 | 54928.2578
| 36526.0448 | 59.973 | 60 | 750 | -175.7728 | -651 | 54928.2578
| 36526.0448 | 59.975 | 60 | 750 | -162.7599 | -651 | 54942.2188
| 36526.0448 | 59.975 | 60 | 750 | -162.7599 | -651 | 54942.2188
| 36526.0448 | 59.977 | 60 | 750 | -149.7223 | -651 | 54948.7422
| 36526.0449 | 59.977 | 60 | 750 | -149.7223 | -651 | 54948.7422
| 36526.0449 | 59.978 | 60 | 750 | -143.2158 | -651 | 54953.4805
| 36526.0449 | 59.978 | 60 | 750 | -143.2158 | -651 | 54953.4805
| 36526.0449 | 59.979 | 60 | 750 | -136.7094 | -651 | 54954.3242
| 36526.045 | 59.979 | 60 | 750 | -136.7094 | -651 | 54954.3242
| 36526.045 | 59.979 | 60 | 750 | -136.7094 | -651 | 54954.3242
| 36526.045 | 59.979 | 60 | 750 | -136.7094 | -651 | 54954.3242
| 36526.045 | 59.979 | 60 | 750 | -136.7094 | -651 | 54961.8359
| 36526.045 | 59.979 | 60 | 750 | -136.7094 | -651 | 54961.8359
| 36526.0451 | 59.984 | 60 | 750 | -104.1525 | -651 | 54970.4297
| 36526.0451 | 59.984 | 60 | 750 | -104.1525 | -651 | 54970.4297
| 36526.0451 | 59.982 | 60 | 750 | -117.1901 | -651 | 54972.2734
| 36526.0451 | 59.982 | 60 | 750 | -117.1901 | -651 | 54972.2734
| 36526.0452 | 59.984 | 60 | 750 | -104.1525 | -651 | 54971.9688
| 36526.0452 | 59.984 | 60 | 750 | -104.1525 | -651 | 54971.9688
| 36526.0452 | 59.987 | 60 | 750 | -84.6332 | -651 | 54955.2383
| 36526.0452 | 59.987 | 60 | 750 | -84.6332 | -651 | 54955.2383
| 36526.0453 | 59.986 | 60 | 750 | -91.1396 | -651 | 54950.8945
| 36526.0453 | 59.986 | 60 | 750 | -91.1396 | -651 | 54950.8945
| 36526.0453 | 59.986 | 60 | 750 | -91.1396 | -651 | 54950.8945
| 36526.0453 | 59.986 | 60 | 750 | -91.1396 | -651 | 54968.8359
| 36526.0453 | 59.986 | 60 | 750 | -91.1396 | -651 | 54968.8359
| 36526.0454 | 59.986 | 60 | 750 | -91.1396 | -651 | 54968.9883
| 36526.0454 | 59.991 | 60 | 750 | -58.5826 | -651 | 54993.7383
| 36526.0454 | 59.991 | 60 | 750 | -58.5826 | -651 | 54993.7383
| 36526.0454 | 59.993 | 60 | 750 | -45.5698 | -651 | 55006.6914
| 36526.0455 | 59.993 | 60 | 750 | -45.5698 | -651 | 55006.6914
| 36526.0455 | 59.988 | 60 | 750 | -78.1268 | -651 | 55014.5625
| 36526.0455 | 59.988 | 60 | 750 | -78.1268 | -651 | 55014.5625
| 36526.0455 | 59.991 | 60 | 750 | -58.5826 | -651 | 54999.6289
| 36526.0456 | 59.991 | 60 | 750 | -58.5826 | -651 | 54999.6289
| 36526.0456 | 59.992 | 60 | 750 | -52.0762 | -651 | 55010.6914
| 36526.0456 | 59.992 | 60 | 750 | -52.0762 | -651 | 55010.6914
| 36526.0456 | 59.987 | 60 | 750 | -84.6332 | -651 | 55012.3594
| 36526.0456 | 59.987 | 60 | 750 | -84.6332 | -651 | 55012.3594
| 36526.0457 | 59.988 | 60 | 750 | -78.1268 | -651 | 55012.3594
| 36526.0457 | 59.988 | 60 | 750 | -78.1268 | -651 | 55023.332
| 36526.0457 | 59.984 | 60 | 750 | -104.1525 | -651 | 55012.4375
| 36526.0457 | 59.984 | 60 | 750 | -104.1525 | -651 | 55012.4375
| 36526.0458 | 59.984 | 60 | 750 | -104.1525 | -651 | 55009.8398
| 36526.0458 | 59.984 | 60 | 750 | -104.1525 | -651 | 55009.8398
| 36526.0458 | 59.986 | 60 | 750 | -91.1396 | -651 | 55018.3711
| 36526.0458 | 59.986 | 60 | 750 | -91.1396 | -651 | 55018.3711
| 36526.0459 | 59.987 | 60 | 750 | -84.6332 | -651 | 55017.4492
| 36526.0459 | 59.987 | 60 | 750 | -84.6332 | -651 | 55017.4492
| 36526.0459 | 59.987 | 60 | 750 | -84.6332 | -651 | 55017.4492
| 36526.0459 | 59.987 | 60 | 750 | -84.6332 | -651 | 55017.4492
| 36526.0459 | 59.99 | 60 | 750 | -65.0891 | -651 | 55022.9766
| 36526.046 | 59.99 | 60 | 750 | -65.0891 | -651 | 55024.5938
| 36526.046 | 59.99 | 60 | 750 | -65.0891 | -651 | 55024.5938
| 36526.046 | 59.99 | 60 | 750 | -65.0891 | -651 | 55034.1133
| 36526.046 | 59.99 | 60 | 750 | -65.0891 | -651 | 55034.1133
| 36526.0461 | 59.985 | 60 | 750 | -97.646 | -651 | 55032.8594
| 36526.0461 | 59.985 | 60 | 750 | -97.646 | -651 | 55043.7344
| 36526.0461 | 59.985 | 60 | 750 | -97.646 | -651 | 55043.7344
| 36526.0461 | 59.991 | 60 | 750 | -58.5826 | -651 | 55034.4453
| 36526.0462 | 59.991 | 60 | 750 | -58.5826 | -651 | 55034.4453
| 36526.0462 | 59.99 | 60 | 750 | -65.0891 | -651 | 55031
| 36526.0462 | 59.99 | 60 | 750 | -65.0891 | -651 | 55031
| 36526.0462 | 59.986 | 60 | 750 | -91.1396 | -651 | 55046.5664
| 36526.0462 | 59.986 | 60 | 750 | -91.1396 | -651 | 55046.5664
| 36526.0463 | 59.986 | 60 | 750 | -91.1396 | -651 | 55046.9336
| 36526.0463 | 59.986 | 60 | 750 | -91.1396 | -651 | 55046.9336
| 36526.0463 | 59.988 | 60 | 750 | -78.1268 | -651 | 55048.4844
| 36526.0463 | 59.988 | 60 | 750 | -78.1268 | -651 | 55048.4844
| 36526.0464 | 59.989 | 60 | 750 | -71.6203 | -651 | 55045.0664
| 36526.0464 | 59.989 | 60 | 750 | -71.6203 | -651 | 55045.0664
| 36526.0464 | 59.989 | 60 | 750 | -71.6203 | -651 | 55035.8984
| 36526.0464 | 59.989 | 60 | 750 | -71.6203 | -651 | 55035.8984
| 36526.0465 | 59.985 | 60 | 750 | -97.646 | -651 | 55042.3711
| 36526.0465 | 59.985 | 60 | 750 | -97.646 | -651 | 55042.3711
| 36526.0465 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0465 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0466 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0466 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0466 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0466 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0466 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0467 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0467 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0467 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0467 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0468 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0468 | 59.986 | 60 | 750 | -91.1396 | -651 | 55044.9297
| 36526.0468 | 59.988 | 60 | 750 | -78.1268 | -651 | 55045.2031
| 36526.0468 | 59.987 | 60 | 750 | -84.6332 | -651 | 55045.2031
| 36526.0469 | 59.987 | 60 | 750 | -84.6332 | -651 | 55049.1172
| 36526.0469 | 59.991 | 60 | 750 | -58.5826 | -651 | 55047.8242
| 36526.0469 | 59.991 | 60 | 750 | -58.5826 | -651 | 55047.8242
| 36526.0469 | 59.992 | 60 | 750 | -52.0762 | -651 | 55062.3672
| 36526.0469 | 59.992 | 60 | 750 | -52.0762 | -651 | 55062.3672
| 36526.047 | 59.993 | 60 | 750 | -45.5698 | -651 | 55059.5469
| 36526.047 | 59.993 | 60 | 750 | -45.5698 | -651 | 55059.5469
| 36526.047 | 59.994 | 60 | 750 | -39.0634 | -651 | 55066.6875
| 36526.047 | 59.994 | 60 | 750 | -39.0634 | -651 | 55066.6875
| 36526.0471 | 59.994 | 60 | 750 | -39.0634 | -651 | 55066.6875
| 36526.0471 | 59.994 | 60 | 750 | -39.0634 | -651 | 55066.6875
| 36526.0471 | 59.989 | 60 | 750 | -71.6203 | -651 | 55066.6875
| 36526.0471 | 59.989 | 60 | 750 | -71.6203 | -651 | 55070.9648
| 36526.0472 | 59.989 | 60 | 750 | -71.6203 | -651 | 55074.3398
| 36526.0472 | 59.989 | 60 | 750 | -71.6203 | -651 | 55074.3398
| 36526.0472 | 59.989 | 60 | 750 | -71.6203 | -651 | 55074.5625
| 36526.0472 | 59.989 | 60 | 750 | -71.6203 | -651 | 55074.5625
| 36526.0472 | 59.988 | 60 | 750 | -78.1268 | -651 | 55072.8281
| 36526.0473 | 59.988 | 60 | 750 | -78.1268 | -651 | 55072.8281
| 36526.0473 | 59.993 | 60 | 750 | -45.5698 | -651 | 55090.0859
| 36526.0473 | 59.993 | 60 | 750 | -45.5698 | -651 | 55090.0859
| 36526.0473 | 60.001 | 60 | 750 | 6.5064 | -651 | 55083.4805
| 36526.0474 | 60.001 | 60 | 750 | 6.5064 | -651 | 55083.4805
| 36526.0474 | 60.003 | 60 | 750 | 19.5193 | -651 | 55071.5117
| 36526.0474 | 60.003 | 60 | 750 | 19.5193 | -651 | 55071.5117
| 36526.0474 | 60.003 | 60 | 750 | 19.5193 | -651 | 55071.5117
| 36526.0475 | 60.003 | 60 | 750 | 19.5193 | -651 | 55065.6094
| 36526.0475 | 60.003 | 60 | 750 | 19.5193 | -651 | 55065.6094
| 36526.0475 | 60.003 | 60 | 750 | 19.5193 | -651 | 55065.6094
| 36526.0475 | 60.003 | 60 | 750 | 19.5193 | -651 | 55065.6094
| 36526.0475 | 60.005 | 60 | 750 | 32.557 | -651 | 55064.875
| 36526.0476 | 60.005 | 60 | 750 | 32.557 | -651 | 55055.0742
| 36526.0476 | 60.005 | 60 | 750 | 32.557 | -651 | 55055.0742
| 36526.0476 | 60.007 | 60 | 750 | 45.5698 | -651 | 55053.0078
| 36526.0476 | 60.007 | 60 | 750 | 45.5698 | -651 | 55053.0078
| 36526.0477 | 60.008 | 60 | 750 | 52.0762 | -651 | 55044.125
| 36526.0477 | 60.008 | 60 | 750 | 52.0762 | -651 | 55044.125
| 36526.0477 | 60.006 | 60 | 750 | 39.0634 | -651 | 55059.5156
| 36526.0477 | 60.006 | 60 | 750 | 39.0634 | -651 | 55059.5156
| 36526.0478 | 60.006 | 60 | 750 | 39.0634 | -651 | 55059.5156
| 36526.0478 | 60.006 | 60 | 750 | 39.0634 | -651 | 55064.3203
| 36526.0478 | 60.007 | 60 | 750 | 45.5698 | -651 | 55064.75
| 36526.0478 | 60.007 | 60 | 750 | 45.5698 | -651 | 55064.75
| 36526.0478 | 59.995 | 60 | 750 | -32.557 | -651 | 55064.8789
| 36526.0479 | 59.995 | 60 | 750 | -32.557 | -651 | 55064.8789
| 36526.0479 | 59.985 | 60 | 750 | -97.646 | -651 | 55066.3086
| 36526.0479 | 59.985 | 60 | 750 | -97.646 | -651 | 55066.3086
| 36526.0479 | 59.986 | 60 | 750 | -91.1396 | -651 | 55093.6875
| 36526.048 | 59.986 | 60 | 750 | -91.1396 | -651 | 55093.6875
| 36526.048 | 59.987 | 60 | 750 | -84.6332 | -651 | 55098.5234
| 36526.048 | 59.987 | 60 | 750 | -84.6332 | -651 | 55098.5234
| 36526.048 | 59.984 | 60 | 750 | -104.1525 | -651 | 55089.0781
| 36526.0481 | 59.984 | 60 | 750 | -104.1525 | -651 | 55089.0781
| 36526.0481 | 59.978 | 60 | 750 | -143.2158 | -651 | 55087.2109
| 36526.0481 | 59.978 | 60 | 750 | -143.2158 | -651 | 55087.2109
| 36526.0481 | 59.978 | 60 | 750 | -143.2158 | -651 | 55114.9102
| 36526.0481 | 59.978 | 60 | 750 | -143.2158 | -651 | 55114.9102
| 36526.0482 | 59.982 | 60 | 750 | -117.1901 | -651 | 55120.7305
| 36526.0482 | 59.982 | 60 | 750 | -117.1901 | -651 | 55120.7305
| 36526.0482 | 59.982 | 60 | 750 | -117.1901 | -651 | 55120.7305
| 36526.0482 | 59.984 | 60 | 750 | -104.1525 | -651 | 55092.625
| 36526.0483 | 59.983 | 60 | 750 | -110.6589 | -651 | 55095
| 36526.0483 | 59.983 | 60 | 750 | -110.6589 | -651 | 55095
| 36526.0483 | 59.98 | 60 | 750 | -130.203 | -651 | 55090.4883
| 36526.0483 | 59.98 | 60 | 750 | -130.203 | -651 | 55090.4883
| 36526.0484 | 59.98 | 60 | 750 | -130.203 | -651 | 55088.082
| 36526.0484 | 59.98 | 60 | 750 | -130.203 | -651 | 55088.082
| 36526.0484 | 59.977 | 60 | 750 | -149.7223 | -651 | 55100.1602
| 36526.0484 | 59.977 | 60 | 750 | -149.7223 | -651 | 55100.1602
| 36526.0484 | 59.977 | 60 | 750 | -149.7223 | -651 | 55100.1602
| 36526.0485 | 59.979 | 60 | 750 | -136.7094 | -651 | 55100.1602
| 36526.0485 | 59.979 | 60 | 750 | -136.7094 | -651 | 55100.1602
| 36526.0485 | 59.979 | 60 | 750 | -136.7094 | -651 | 55092.7656
| 36526.0485 | 59.979 | 60 | 750 | -136.7094 | -651 | 55099.5312
| 36526.0486 | 59.979 | 60 | 750 | -136.7094 | -651 | 55099.5312
| 36526.0486 | 59.972 | 60 | 750 | -182.2792 | -651 | 55098.2578
| 36526.0486 | 59.972 | 60 | 750 | -182.2792 | -651 | 55098.2578
| 36526.0486 | 59.977 | 60 | 750 | -149.7223 | -651 | 55106.6211
| 36526.0487 | 59.977 | 60 | 750 | -149.7223 | -651 | 55106.6211
| 36526.0487 | 59.976 | 60 | 750 | -156.2287 | -651 | 55119.6016
| 36526.0487 | 59.976 | 60 | 750 | -156.2287 | -651 | 55119.6016
| 36526.0487 | 59.973 | 60 | 750 | -175.7728 | -651 | 55121.9258
| 36526.0487 | 59.973 | 60 | 750 | -175.7728 | -651 | 55121.9258
| 36526.0488 | 59.972 | 60 | 750 | -182.2792 | -651 | 55099.6211
| 36526.0488 | 59.972 | 60 | 750 | -182.2792 | -651 | 55099.6211
| 36526.0488 | 59.972 | 60 | 750 | -182.2792 | -651 | 55099.6211
| 36526.0488 | 59.972 | 60 | 750 | -182.2792 | -651 | 55099.6211
| 36526.0489 | 59.972 | 60 | 750 | -182.2792 | -651 | 55099.6211
| 36526.0489 | 59.972 | 60 | 750 | -182.2792 | -651 | 55099.6211
| 36526.0489 | 59.973 | 60 | 750 | -175.7728 | -651 | 55112.4453
| 36526.0489 | 59.973 | 60 | 750 | -175.7728 | -651 | 55102.8867
| 36526.049 | 59.982 | 60 | 750 | -117.1901 | -651 | 55127.8516
| 36526.049 | 59.982 | 60 | 750 | -117.1901 | -651 | 55127.8516
| 36526.049 | 59.979 | 60 | 750 | -136.7094 | -651 | 55111.6445
| 36526.049 | 59.979 | 60 | 750 | -136.7094 | -651 | 55111.6445
| 36526.0491 | 59.978 | 60 | 750 | -143.2158 | -651 | 55126.6289
| 36526.0491 | 59.978 | 60 | 750 | -143.2158 | -651 | 55126.6289
| 36526.0491 | 59.978 | 60 | 750 | -143.2158 | -651 | 55128.0977
| 36526.0491 | 59.978 | 60 | 750 | -143.2158 | -651 | 55128.0977
| 36526.0491 | 59.981 | 60 | 750 | -123.6966 | -651 | 55129.7305
| 36526.0492 | 59.981 | 60 | 750 | -123.6966 | -651 | 55129.7305
| 36526.0492 | 59.981 | 60 | 750 | -123.6966 | -651 | 55129.7305
| 36526.0492 | 59.982 | 60 | 750 | -117.1901 | -651 | 55129.7305
| 36526.0492 | 59.982 | 60 | 750 | -117.1901 | -651 | 55137.2383
| 36526.0493 | 59.982 | 60 | 750 | -117.1901 | -651 | 55137.2383
| 36526.0493 | 59.985 | 60 | 750 | -97.646 | -651 | 55127.4258
| 36526.0493 | 59.985 | 60 | 750 | -97.646 | -651 | 55127.4258
| 36526.0493 | 59.984 | 60 | 750 | -104.1525 | -651 | 55123.7031
| 36526.0494 | 59.984 | 60 | 750 | -104.1525 | -651 | 55123.7031
| 36526.0494 | 59.981 | 60 | 750 | -123.6966 | -651 | 55135.6992
| 36526.0494 | 59.981 | 60 | 750 | -123.6966 | -651 | 55135.6992
| 36526.0494 | 59.981 | 60 | 750 | -123.6966 | -651 | 55136.5586
| 36526.0494 | 59.981 | 60 | 750 | -123.6966 | -651 | 55136.5586
| 36526.0495 | 59.983 | 60 | 750 | -110.6589 | -651 | 55141.8242
| 36526.0495 | 59.983 | 60 | 750 | -110.6589 | -651 | 55141.8242
| 36526.0495 | 59.985 | 60 | 750 | -97.646 | -651 | 55157.4297
| 36526.0495 | 59.985 | 60 | 750 | -97.646 | -651 | 55157.4297
| 36526.0496 | 59.985 | 60 | 750 | -97.646 | -651 | 55157.4297
| 36526.0496 | 59.985 | 60 | 750 | -97.646 | -651 | 55152.8047
| 36526.0496 | 59.985 | 60 | 750 | -97.646 | -651 | 55152.8047
| 36526.0496 | 59.985 | 60 | 750 | -97.646 | -651 | 55153.8125
| 36526.0497 | 59.985 | 60 | 750 | -97.646 | -651 | 55153.8125
| 36526.0497 | 59.831 | 60 | 750 | -1100.1817 | -651 | 55158.375
| 36526.0497 | 59.842 | 60 | 750 | -1028.5862 | -651 | 55230.2656
| 36526.0497 | 59.842 | 60 | 0 | -1028.5862 | -651 | 55230.2656
| 36526.0497 | 59.867 | 60 | 0 | -865.8262 | -651 | 55418.207
| 36526.0498 | 59.867 | 60 | 0 | -865.8262 | -651 | 55418.207
| 36526.0498 | 59.874 | 60 | 0 | -820.2564 | -651 | 54802.8711
| 36526.0498 | 59.874 | 60 | 0 | -820.2564 | -651 | 54802.8711
| 36526.0498 | 59.87 | 60 | 0 | -846.307 | -651 | 54952.6602
| 36526.0499 | 59.87 | 60 | 0 | -846.307 | -651 | 54952.6602
| 36526.0499 | 59.87 | 60 | 0 | -846.307 | -651 | 54952.6602
| 36526.0499 | 59.87 | 60 | 0 | -846.307 | -651 | 54952.6602
| 36526.0499 | 59.867 | 60 | 0 | -865.8262 | -651 | 54990.7031
| 36526.05 | 59.867 | 60 | 0 | -865.8262 | -651 | 54990.7031
| 36526.05 | 59.866 | 60 | 0 | -872.3326 | -651 | 54982.918
| 36526.05 | 59.866 | 60 | 0 | -872.3326 | -651 | 54982.918
| 36526.05 | 59.861 | 60 | 0 | -904.8896 | -651 | 55004.2969
| 36526.05 | 59.861 | 60 | 0 | -904.8896 | -651 | 55004.2969
| 36526.0501 | 59.857 | 60 | 0 | -930.9401 | -651 | 54995.5078
| 36526.0501 | 59.857 | 60 | 0 | -930.9401 | -651 | 54995.5078
| 36526.0501 | 59.857 | 60 | 0 | -930.9401 | -651 | 55004.9727
| 36526.0501 | 59.857 | 60 | 0 | -930.9401 | -651 | 55004.9727
| 36526.0502 | 59.854 | 60 | 0 | -950.4594 | -651 | 55010.4531
| 36526.0502 | 59.854 | 60 | 0 | -950.4594 | -651 | 55010.4531
| 36526.0502 | 59.853 | 60 | 0 | -956.9658 | -651 | 55031.9922
| 36526.0502 | 59.853 | 60 | 0 | -956.9658 | -651 | 55031.9922
| 36526.0503 | 59.853 | 60 | 0 | -956.9658 | -651 | 55031.9922
| 36526.0503 | 59.853 | 60 | 0 | -956.9658 | -651 | 55031.9922
| 36526.0503 | 59.853 | 60 | 0 | -956.9658 | -651 | 55031.9922
| 36526.0503 | 59.853 | 60 | 0 | -956.9658 | -651 | 55031.9922
| 36526.0503 | 59.854 | 60 | 0 | -950.4594 | -651 | 55059.3359
| 36526.0504 | 59.854 | 60 | 0 | -950.4594 | -651 | 55059.3359
| 36526.0504 | 59.868 | 60 | 0 | -859.3198 | -651 | 55085.1953
| 36526.0504 | 59.868 | 60 | 0 | -859.3198 | -651 | 55085.1953
| 36526.0504 | 59.875 | 60 | 0 | -813.75 | -651 | 55109.5234
| 36526.0505 | 59.875 | 60 | 0 | -813.75 | -651 | 55109.5234
| 36526.0505 | 59.881 | 60 | 0 | -774.6866 | -651 | 55127.8984
| 36526.0505 | 59.881 | 60 | 0 | -774.6866 | -651 | 55127.8984
| 36526.0505 | 59.886 | 60 | 0 | -742.1297 | -651 | 55127.1055
| 36526.0506 | 59.886 | 60 | 0 | -742.1297 | -651 | 55127.1055
| 36526.0506 | 59.887 | 60 | 0 | -735.6232 | -651 | 55141.5508
| 36526.0506 | 59.887 | 60 | 0 | -735.6232 | -651 | 55141.5508
| 36526.0506 | 59.886 | 60 | 0 | -742.1297 | -651 | 55141.6445
| 36526.0506 | 59.886 | 60 | 0 | -742.1297 | -651 | 55141.6445
| 36526.0507 | 59.894 | 60 | 0 | -690.0534 | -651 | 55148.4805
| 36526.0507 | 59.894 | 60 | 0 | -690.0534 | -651 | 55148.4805
| 36526.0507 | 59.895 | 60 | 0 | -683.547 | -651 | 55146.3438
| 36526.0507 | 59.895 | 60 | 0 | -683.547 | -651 | 55146.3438
| 36526.0508 | 59.896 | 60 | 0 | -677.0406 | -651 | 55169.207
| 36526.0508 | 59.896 | 60 | 0 | -677.0406 | -651 | 55169.207
| 36526.0508 | 59.901 | 60 | 0 | -644.4836 | -651 | 55169.6797
| 36526.0508 | 59.901 | 60 | 0 | -644.4836 | -651 | 55169.6797
| 36526.0509 | 59.908 | 60 | 0 | -598.9138 | -651 | 55184.0156
| 36526.0509 | 59.908 | 60 | 0 | -598.9138 | -651 | 55184.0156
| 36526.0509 | 59.91 | 60 | 0 | -585.901 | -651 | 55177.1797
| 36526.0509 | 59.91 | 60 | 0 | -585.901 | -651 | 55177.1797
| 36526.0509 | 59.91 | 60 | 0 | -585.901 | -651 | 55177.1797
| 36526.051 | 59.91 | 60 | 0 | -585.901 | -651 | 55177.1797
| 36526.051 | 59.91 | 60 | 0 | -585.901 | -651 | 55177.1797
| 36526.051 | 59.913 | 60 | 0 | -566.3817 | -651 | 55188.1484
| 36526.051 | 59.913 | 60 | 0 | -566.3817 | -651 | 55188.7227
| 36526.0511 | 59.913 | 60 | 0 | -566.3817 | -651 | 55188.7227
| 36526.0511 | 59.924 | 60 | 0 | -494.7614 | -651 | 55209.5703
| 36526.0511 | 59.924 | 60 | 0 | -494.7614 | -651 | 55209.5703
| 36526.0511 | 59.931 | 60 | 0 | -449.1916 | -651 | 55215.1875
| 36526.0512 | 59.931 | 60 | 0 | -449.1916 | -651 | 55215.1875
| 36526.0512 | 59.931 | 60 | 0 | -449.1916 | -651 | 55218.3008
| 36526.0512 | 59.931 | 60 | 0 | -449.1916 | -651 | 55218.3008
| 36526.0512 | 59.929 | 60 | 0 | -462.2044 | -651 | 55209.2852
| 36526.0512 | 59.929 | 60 | 0 | -462.2044 | -651 | 55209.2852
| 36526.0513 | 59.933 | 60 | 0 | -436.1787 | -651 | 55228.7773
| 36526.0513 | 59.933 | 60 | 0 | -436.1787 | -651 | 55228.7773
| 36526.0513 | 59.933 | 60 | 0 | -436.1787 | -651 | 55228.7773
| 36526.0513 | 59.933 | 60 | 0 | -436.1787 | -651 | 55228.7773
| 36526.0514 | 59.942 | 60 | 0 | -377.5713 | -651 | 55237.9805
| 36526.0514 | 59.942 | 60 | 0 | -377.5713 | -651 | 55237.9805
| 36526.0514 | 59.946 | 60 | 0 | -351.5456 | -651 | 55258.3008
| 36526.0514 | 59.946 | 60 | 0 | -351.5456 | -651 | 55258.3008
| 36526.0515 | 59.945 | 60 | 0 | -358.052 | -651 | 55255.8047
| 36526.0515 | 59.945 | 60 | 0 | -358.052 | -651 | 55255.8047
| 36526.0515 | 59.944 | 60 | 0 | -364.5584 | -651 | 55279.8125
| 36526.0515 | 59.944 | 60 | 0 | -364.5584 | -651 | 55279.8125
| 36526.0516 | 59.948 | 60 | 0 | -338.5079 | -651 | 55282.7109
| 36526.0516 | 59.948 | 60 | 0 | -338.5079 | -651 | 55282.7109
| 36526.0516 | 59.955 | 60 | 0 | -292.9381 | -651 | 55283.5352
| 36526.0516 | 59.955 | 60 | 0 | -292.9381 | -651 | 55283.5352
| 36526.0516 | 59.963 | 60 | 0 | -240.8619 | -651 | 55293.4219
| 36526.0517 | 59.963 | 60 | 0 | -240.8619 | -651 | 55293.4219
| 36526.0517 | 59.963 | 60 | 0 | -240.8619 | -651 | 55293.4219
| 36526.0517 | 59.963 | 60 | 0 | -240.8619 | -651 | 55293.4219
| 36526.0517 | 59.965 | 60 | 0 | -227.849 | -651 | 55293.4219
| 36526.0518 | 59.965 | 60 | 0 | -227.849 | -651 | 55295.9141
| 36526.0518 | 59.972 | 60 | 0 | -182.2792 | -651 | 55305.5938
| 36526.0518 | 59.972 | 60 | 0 | -182.2792 | -651 | 55305.5938
| 36526.0518 | 59.974 | 60 | 0 | -169.2664 | -651 | 55308.2539
| 36526.0519 | 59.974 | 60 | 0 | -169.2664 | -651 | 55308.2539
| 36526.0519 | 59.977 | 60 | 0 | -149.7223 | -651 | 55307.5391
| 36526.0519 | 59.977 | 60 | 0 | -149.7223 | -651 | 55307.5391
| 36526.0519 | 59.979 | 60 | 0 | -136.7094 | -651 | 55316.1914
| 36526.0519 | 59.979 | 60 | 0 | -136.7094 | -651 | 55316.1914
| 36526.052 | 59.996 | 60 | 0 | -26.0505 | -651 | 55314.25
| 36526.052 | 59.996 | 60 | 0 | -26.0505 | -651 | 55314.25
| 36526.052 | 59.996 | 60 | 0 | -26.0505 | -651 | 55314.25
| 36526.052 | 59.996 | 60 | 0 | -26.0505 | -651 | 55314.25
| 36526.0521 | 60.007 | 60 | 0 | 45.5698 | -651 | 55313.6367
| 36526.0521 | 60.007 | 60 | 0 | 45.5698 | -651 | 55313.6367
| 36526.0521 | 60.007 | 60 | 0 | 45.5698 | -651 | 55281.5078
| 36526.0521 | 60.007 | 60 | 0 | 45.5698 | -651 | 55281.5078
| 36526.0522 | 60.017 | 60 | 0 | 110.6589 | -651 | 55287.3438
| 36526.0522 | 60.017 | 60 | 0 | 110.6589 | -651 | 55287.3438
| 36526.0522 | 60.026 | 60 | 0 | 169.2664 | -651 | 55276.3164
| 36526.0522 | 60.026 | 60 | 0 | 169.2664 | -651 | 55276.3164
| 36526.0522 | 60.029 | 60 | 0 | 188.7856 | -651 | 55265.6992
| 36526.0523 | 60.029 | 60 | 0 | 188.7856 | -651 | 55265.6992
| 36526.0523 | 60.036 | 60 | 0 | 234.3554 | -651 | 55272.6562
| 36526.0523 | 60.036 | 60 | 0 | 234.3554 | -651 | 55272.6562
| 36526.0523 | 60.041 | 60 | 0 | 266.9124 | -651 | 55264.2422
| 36526.0524 | 60.041 | 60 | 0 | 266.9124 | -651 | 55264.2422
| 36526.0524 | 60.041 | 60 | 0 | 266.9124 | -651 | 55264.2422
| 36526.0524 | 60.041 | 60 | 0 | 266.9124 | -651 | 55264.2422
| 36526.0524 | 60.041 | 60 | 0 | 266.9124 | -651 | 55264.2422
| 36526.0525 | 60.038 | 60 | 0 | 247.3683 | -651 | 55274.9922
| 36526.0525 | 60.033 | 60 | 0 | 214.8362 | -651 | 55274.9922
| 36526.0525 | 60.033 | 60 | 0 | 214.8362 | -651 | 55274.9922
| 36526.0525 | 60.04 | 60 | 0 | 260.406 | -651 | 55287.5898
| 36526.0525 | 60.04 | 60 | 0 | 260.406 | -651 | 55287.5898
| 36526.0526 | 60.043 | 60 | 0 | 279.9252 | -651 | 55290.5664
| 36526.0526 | 60.043 | 60 | 0 | 279.9252 | -651 | 55290.5664
| 36526.0526 | 60.038 | 60 | 0 | 247.3683 | -651 | 55291.0195
| 36526.0526 | 60.038 | 60 | 0 | 247.3683 | -651 | 55291.0195
| 36526.0527 | 60.039 | 60 | 0 | 253.8995 | -651 | 55292.0898
| 36526.0527 | 60.039 | 60 | 0 | 253.8995 | -651 | 55292.0898
| 36526.0527 | 60.039 | 60 | 0 | 253.8995 | -651 | 55279.6641
| 36526.0527 | 60.039 | 60 | 0 | 253.8995 | -651 | 55279.6641
| 36526.0528 | 60.039 | 60 | 0 | 253.8995 | -651 | 55279.6641
| 36526.0528 | 60.039 | 60 | 0 | 253.8995 | -651 | 55279.6641
| 36526.0528 | 60.039 | 60 | 0 | 253.8995 | -651 | 55290.2891
| 36526.0528 | 60.039 | 60 | 0 | 253.8995 | -651 | 55290.2891
| 36526.0528 | 60.04 | 60 | 0 | 260.406 | -651 | 55288.3828
| 36526.0529 | 60.04 | 60 | 0 | 260.406 | -651 | 55288.3828
| 36526.0529 | 60.038 | 60 | 0 | 247.3683 | -651 | 55286.4062
| 36526.0529 | 60.038 | 60 | 0 | 247.3683 | -651 | 55286.4062
| 36526.0529 | 60.039 | 60 | 0 | 253.8995 | -651 | 55296.7383
| 36526.053 | 60.039 | 60 | 0 | 253.8995 | -651 | 55296.7383
| 36526.053 | 60.037 | 60 | 0 | 240.8619 | -651 | 55276.2891
| 36526.053 | 60.037 | 60 | 0 | 240.8619 | -651 | 55276.2891
| 36526.053 | 60.04 | 60 | 0 | 260.406 | -651 | 55287.0469
| 36526.0531 | 60.04 | 60 | 0 | 260.406 | -651 | 55287.0469
| 36526.0531 | 60.04 | 60 | 0 | 260.406 | -651 | 55287.0469
| 36526.0531 | 60.04 | 60 | 0 | 260.406 | -651 | 55298.1758
| 36526.0531 | 60.04 | 60 | 0 | 260.406 | -651 | 55298.1758
| 36526.0531 | 60.033 | 60 | 0 | 214.8362 | -651 | 55289.2695
| 36526.0532 | 60.031 | 60 | 0 | 201.7985 | -651 | 55296.8555
| 36526.0532 | 60.031 | 60 | 0 | 201.7985 | -651 | 55296.8555
| 36526.0532 | 60.033 | 60 | 0 | 214.8362 | -651 | 55300.6445
| 36526.0532 | 60.033 | 60 | 0 | 214.8362 | -651 | 55300.6445
| 36526.0533 | 60.032 | 60 | 0 | 208.3297 | -651 | 55300.6172
| 36526.0533 | 60.032 | 60 | 0 | 208.3297 | -651 | 55300.6172
| 36526.0533 | 60.032 | 60 | 0 | 208.3297 | -651 | 55331.7031
| 36526.0533 | 60.032 | 60 | 0 | 208.3297 | -651 | 55331.7031
| 36526.0534 | 60.029 | 60 | 0 | 188.7856 | -651 | 55315.0625
| 36526.0534 | 60.029 | 60 | 0 | 188.7856 | -651 | 55315.0625
| 36526.0534 | 60.029 | 60 | 0 | 188.7856 | -651 | 55318.6797
| 36526.0534 | 60.029 | 60 | 0 | 188.7856 | -651 | 55318.6797
| 36526.0534 | 60.029 | 60 | 0 | 188.7856 | -651 | 55318.6797
| 36526.0535 | 60.029 | 60 | 0 | 188.7856 | -651 | 55318.6797
| 36526.0535 | 60.029 | 60 | 0 | 188.7856 | -651 | 55318.6797
| 36526.0535 | 60.031 | 60 | 0 | 201.7985 | -651 | 55308.5078
| 36526.0535 | 60.03 | 60 | 0 | 195.2921 | -651 | 55328.6953
| 36526.0536 | 60.03 | 60 | 0 | 195.2921 | -651 | 55328.6953
| 36526.0536 | 60.027 | 60 | 0 | 175.7728 | -651 | 55332.4414
| 36526.0536 | 60.027 | 60 | 0 | 175.7728 | -651 | 55332.4414
| 36526.0536 | 60.027 | 60 | 0 | 175.7728 | -651 | 55330.1523
| 36526.0537 | 60.027 | 60 | 0 | 175.7728 | -651 | 55330.1523
| 36526.0537 | 60.024 | 60 | 0 | 156.2287 | -651 | 55320.957
| 36526.0537 | 60.024 | 60 | 0 | 156.2287 | -651 | 55320.957
| 36526.0537 | 60.019 | 60 | 0 | 123.6966 | -651 | 55332.8672
| 36526.0537 | 60.019 | 60 | 0 | 123.6966 | -651 | 55332.8672
| 36526.0538 | 60.018 | 60 | 0 | 117.1901 | -651 | 55332.8672
| 36526.0538 | 60.018 | 60 | 0 | 117.1901 | -651 | 55332.8672
| 36526.0538 | 60.018 | 60 | 0 | 117.1901 | -651 | 55336.2109
| 36526.0538 | 60.018 | 60 | 0 | 117.1901 | -651 | 55336.2109
| 36526.0539 | 60.02 | 60 | 0 | 130.203 | -651 | 55311.4102
| 36526.0539 | 60.02 | 60 | 0 | 130.203 | -651 | 55311.4102
| 36526.0539 | 60.026 | 60 | 0 | 169.2664 | -651 | 55335.7305
| 36526.0539 | 60.026 | 60 | 0 | 169.2664 | -651 | 55335.7305
| 36526.054 | 60.025 | 60 | 0 | 162.7599 | -651 | 55327.9453
| 36526.054 | 60.025 | 60 | 0 | 162.7599 | -651 | 55327.9453
| 36526.054 | 60.023 | 60 | 0 | 149.7223 | -651 | 55321.9141
| 36526.054 | 60.023 | 60 | 0 | 149.7223 | -651 | 55321.9141
| 36526.0541 | 60.025 | 60 | 0 | 162.7599 | -651 | 55347.9062
| 36526.0541 | 60.025 | 60 | 0 | 162.7599 | -651 | 55347.9062
| 36526.0541 | 60.025 | 60 | 0 | 162.7599 | -651 | 55347.2891
| 36526.0541 | 60.025 | 60 | 0 | 162.7599 | -651 | 55347.2891
| 36526.0541 | 60.025 | 60 | 0 | 162.7599 | -651 | 55347.2891
| 36526.0542 | 60.025 | 60 | 0 | 162.7599 | -651 | 55347.2891
| 36526.0542 | 60.025 | 60 | 0 | 162.7599 | -651 | 55347.2891
| 36526.0542 | 60.025 | 60 | 0 | 162.7599 | -651 | 55347.2891
| 36526.0542 | 60.024 | 60 | 0 | 156.2287 | -651 | 55339.1992
| 36526.0543 | 60.024 | 60 | 0 | 156.2287 | -651 | 55337.4844
| 36526.0543 | 60.023 | 60 | 0 | 149.7223 | -651 | 55334.0273
| 36526.0543 | 60.023 | 60 | 0 | 149.7223 | -651 | 55334.0273
| 36526.0543 | 60.022 | 60 | 0 | 143.2158 | -651 | 55325.2305
| 36526.0544 | 60.022 | 60 | 0 | 143.2158 | -651 | 55325.2305
| 36526.0544 | 60.02 | 60 | 0 | 130.203 | -651 | 55325.293
| 36526.0544 | 60.02 | 60 | 0 | 130.203 | -651 | 55325.293
| 36526.0544 | 60.017 | 60 | 0 | 110.6589 | -651 | 55325.8711
| 36526.0544 | 60.017 | 60 | 0 | 110.6589 | -651 | 55325.8711
| 36526.0545 | 60.016 | 60 | 0 | 104.1525 | -651 | 55343.2734
| 36526.0545 | 60.016 | 60 | 0 | 104.1525 | -651 | 55343.2734
| 36526.0545 | 60.016 | 60 | 0 | 104.1525 | -651 | 55343.2734
| 36526.0545 | 60.016 | 60 | 0 | 104.1525 | -651 | 55343.2734
| 36526.0546 | 60.017 | 60 | 0 | 110.6589 | -651 | 55339.4297
| 36526.0546 | 60.017 | 60 | 0 | 110.6589 | -651 | 55339.4297
| 36526.0546 | 60.022 | 60 | 0 | 143.2158 | -651 | 55352.2578
| 36526.0546 | 60.022 | 60 | 0 | 143.2158 | -651 | 55352.2578
| 36526.0547 | 60.02 | 60 | 0 | 130.203 | -651 | 55336.8828
| 36526.0547 | 60.02 | 60 | 0 | 130.203 | -651 | 55336.8828
| 36526.0547 | 60.014 | 60 | 0 | 91.1396 | -651 | 55345.9883
| 36526.0547 | 60.014 | 60 | 0 | 91.1396 | -651 | 55345.9883
| 36526.0547 | 60.007 | 60 | 0 | 45.5698 | -651 | 55364.625
| 36526.0548 | 60.007 | 60 | 0 | 45.5698 | -651 | 55364.625
| 36526.0548 | 60.002 | 60 | 0 | 13.0128 | -651 | 55369.5117
| 36526.0548 | 60.002 | 60 | 0 | 13.0128 | -651 | 55369.5117
| 36526.0548 | 60.002 | 60 | 0 | 13.0128 | -651 | 55369.5117
| 36526.0549 | 60.005 | 60 | 0 | 32.557 | -651 | 55358.8594
| 36526.0549 | 60.008 | 60 | 0 | 52.0762 | -651 | 55356.9609
| 36526.0549 | 60.008 | 60 | 0 | 52.0762 | -651 | 55356.9609
| 36526.0549 | 60.002 | 60 | 0 | 13.0128 | -651 | 55341.1758
| 36526.055 | 60.002 | 60 | 0 | 13.0128 | -651 | 55341.1758
| 36526.055 | 59.991 | 60 | 0 | -58.5826 | -651 | 55343.4922
| 36526.055 | 59.991 | 60 | 0 | -58.5826 | -651 | 55343.4922
| 36526.055 | 59.989 | 60 | 0 | -71.6203 | -651 | 55350.2891
| 36526.055 | 59.989 | 60 | 0 | -71.6203 | -651 | 55350.2891
| 36526.0551 | 59.991 | 60 | 0 | -58.5826 | -651 | 55330.418
| 36526.0551 | 59.991 | 60 | 0 | -58.5826 | -651 | 55330.418
| 36526.0551 | 59.992 | 60 | 0 | -52.0762 | -651 | 55350.3672
| 36526.0551 | 59.992 | 60 | 0 | -52.0762 | -651 | 55350.3672
| 36526.0552 | 59.99 | 60 | 0 | -65.0891 | -651 | 55335.7344
| 36526.0552 | 59.99 | 60 | 0 | -65.0891 | -651 | 55335.7344
| 36526.0552 | 59.988 | 60 | 0 | -78.1268 | -651 | 55331.6953
| 36526.0552 | 59.988 | 60 | 0 | -78.1268 | -651 | 55331.6953
| 36526.0553 | 59.988 | 60 | 0 | -78.1268 | -651 | 55331.6953
| 36526.0553 | 59.988 | 60 | 0 | -78.1268 | -651 | 55331.6953
| 36526.0553 | 59.988 | 60 | 0 | -78.1268 | -651 | 55331.6953
| 36526.0553 | 59.97 | 60 | 0 | -195.2921 | -651 | 55335.5586
| 36526.0553 | 59.97 | 60 | 0 | -195.2921 | -651 | 55330.2891
| 36526.0554 | 59.97 | 60 | 0 | -195.2921 | -651 | 55330.2891
| 36526.0554 | 59.966 | 60 | 0 | -221.3426 | -651 | 55334.0195
| 36526.0554 | 59.966 | 60 | 0 | -221.3426 | -651 | 55334.0195
| 36526.0554 | 59.964 | 60 | 0 | -234.3554 | -651 | 55337.1602
| 36526.0555 | 59.964 | 60 | 0 | -234.3554 | -651 | 55337.1602
| 36526.0555 | 59.968 | 60 | 0 | -208.3297 | -651 | 55335.2383
| 36526.0555 | 59.968 | 60 | 0 | -208.3297 | -651 | 55335.2383
| 36526.0555 | 59.967 | 60 | 0 | -214.8362 | -651 | 55338.5508
| 36526.0556 | 59.967 | 60 | 0 | -214.8362 | -651 | 55338.5508
| 36526.0556 | 59.966 | 60 | 0 | -221.3426 | -651 | 55340.3906
| 36526.0556 | 59.966 | 60 | 0 | -221.3426 | -651 | 55340.3906
| 36526.0556 | 59.965 | 60 | 0 | -227.849 | -651 | 55322.8008
| 36526.0556 | 59.965 | 60 | 0 | -227.849 | -651 | 55322.8008
| 36526.0557 | 59.962 | 60 | 0 | -247.3683 | -651 | 55329.9531
| 36526.0557 | 59.962 | 60 | 0 | -247.3683 | -651 | 55329.9531
| 36526.0557 | 59.964 | 60 | 0 | -234.3554 | -651 | 55357.0273
| 36526.0557 | 59.964 | 60 | 0 | -234.3554 | -651 | 55357.0273
| 36526.0558 | 59.973 | 60 | 0 | -175.7728 | -651 | 55348.4609
| 36526.0558 | 59.973 | 60 | 0 | -175.7728 | -651 | 55348.4609
| 36526.0558 | 59.981 | 60 | 0 | -123.6966 | -651 | 55341.6172
| 36526.0558 | 59.981 | 60 | 0 | -123.6966 | -651 | 55341.6172
| 36526.0559 | 59.984 | 60 | 0 | -104.1525 | -651 | 55340.2734
| 36526.0559 | 59.984 | 60 | 0 | -104.1525 | -651 | 55340.2734
| 36526.0559 | 59.984 | 60 | 0 | -104.1525 | -651 | 55340.2734
| 36526.0559 | 59.984 | 60 | 0 | -104.1525 | -651 | 55340.2734
| 36526.0559 | 59.984 | 60 | 0 | -104.1525 | -651 | 55340.2734
| 36526.056 | 59.987 | 60 | 0 | -84.6332 | -651 | 55300.4297
| 36526.056 | 59.985 | 60 | 0 | -97.646 | -651 | 55299.8398
| 36526.056 | 59.985 | 60 | 0 | -97.646 | -651 | 55299.8398
| 36526.056 | 59.984 | 60 | 0 | -104.1525 | -651 | 55304.3125
| 36526.0561 | 59.984 | 60 | 0 | -104.1525 | -651 | 55304.3125
| 36526.0561 | 59.983 | 60 | 0 | -110.6589 | -651 | 55280.7266
| 36526.0561 | 59.983 | 60 | 0 | -110.6589 | -651 | 55280.7266
| 36526.0561 | 59.976 | 60 | 0 | -156.2287 | -651 | 55286.3516
| 36526.0562 | 59.976 | 60 | 0 | -156.2287 | -651 | 55286.3516
| 36526.0562 | 59.966 | 60 | 0 | -221.3426 | -651 | 55297.7852
| 36526.0562 | 59.966 | 60 | 0 | -221.3426 | -651 | 55297.7852
| 36526.0562 | 59.966 | 60 | 0 | -221.3426 | -651 | 55291.7734
| 36526.0562 | 59.966 | 60 | 0 | -221.3426 | -651 | 55291.7734
| 36526.0563 | 59.972 | 60 | 0 | -182.2792 | -651 | 55308.4062
| 36526.0563 | 59.972 | 60 | 0 | -182.2792 | -651 | 55308.4062
| 36526.0563 | 59.978 | 60 | 0 | -143.2158 | -651 | 55321.7305
| 36526.0563 | 59.978 | 60 | 0 | -143.2158 | -651 | 55321.7305
| 36526.0564 | 59.978 | 60 | 0 | -143.2158 | -651 | 55322.1719
| 36526.0564 | 59.978 | 60 | 0 | -143.2158 | -651 | 55322.1719
| 36526.0564 | 59.974 | 60 | 0 | -169.2664 | -651 | 55313.3906
| 36526.0564 | 59.974 | 60 | 0 | -169.2664 | -651 | 55313.3906
| 36526.0565 | 59.972 | 60 | 0 | -182.2792 | -651 | 55314.3633
| 36526.0565 | 59.972 | 60 | 0 | -182.2792 | -651 | 55314.3633
| 36526.0565 | 59.97 | 60 | 0 | -195.2921 | -651 | 55311.5586
| 36526.0565 | 59.97 | 60 | 0 | -195.2921 | -651 | 55311.5586
| 36526.0566 | 59.97 | 60 | 0 | -195.2921 | -651 | 55307.0898
| 36526.0566 | 59.97 | 60 | 0 | -195.2921 | -651 | 55307.0898
| 36526.0566 | 59.97 | 60 | 0 | -195.2921 | -651 | 55307.0898
| 36526.0566 | 59.97 | 60 | 0 | -195.2921 | -651 | 55307.0898
| 36526.0566 | 59.971 | 60 | 0 | -188.7856 | -651 | 55326.0078
| 36526.0567 | 59.972 | 60 | 0 | -182.2792 | -651 | 55327.0742
| 36526.0567 | 59.97 | 60 | 0 | -195.2921 | -651 | 55318.0664
| 36526.0567 | 59.97 | 60 | 0 | -195.2921 | -651 | 55318.0664
| 36526.0567 | 59.966 | 60 | 0 | -221.3426 | -651 | 55310.168
| 36526.0568 | 59.966 | 60 | 0 | -221.3426 | -651 | 55310.168
| 36526.0568 | 59.965 | 60 | 0 | -227.849 | -651 | 55301.2188
| 36526.0568 | 59.965 | 60 | 0 | -227.849 | -651 | 55301.2188
| 36526.0568 | 59.968 | 60 | 0 | -208.3297 | -651 | 55307.2695
| 36526.0569 | 59.968 | 60 | 0 | -208.3297 | -651 | 55307.2695
| 36526.0569 | 59.968 | 60 | 0 | -208.3297 | -651 | 55319.5781
| 36526.0569 | 59.968 | 60 | 0 | -208.3297 | -651 | 55319.5781
| 36526.0569 | 59.963 | 60 | 0 | -240.8619 | -651 | 55326.8789
| 36526.0569 | 59.963 | 60 | 0 | -240.8619 | -651 | 55326.8789
| 36526.057 | 59.964 | 60 | 0 | -234.3554 | -651 | 55326.8789
| 36526.057 | 59.964 | 60 | 0 | -234.3554 | -651 | 55335.7539
| 36526.057 | 59.965 | 60 | 0 | -227.849 | -651 | 55321.4453
| 36526.057 | 59.965 | 60 | 0 | -227.849 | -651 | 55321.4453
| 36526.0571 | 59.968 | 60 | 0 | -208.3297 | -651 | 55333.8672
| 36526.0571 | 59.968 | 60 | 0 | -208.3297 | -651 | 55333.8672