ERCOT Operations Report

January 2009 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 1/10/2009 0:01 | 60.136 | 303 | Out of Down Regulation, SCE change +200 in 2 mins |
| 1/16/2009 6:13 | 59.811 | 86 | Unit trip with 793 MW |
| 1/20/2009 21:29 | 60.156 | 410 | Ramping out of 1227MW of Non-Spin slower than Balancing Energy Schedule increase. |
| 1/23/2009 20:59 | 59.898 | 4 | Balancing Energy Schedule change -1700 MW |
| 1/25/2009 8:19 | 59.837 | 97 | Unit trip with 545 MW |
| 1/28/2009 4:54 | 59.859 | 43 | Unit trip with 775 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 1/06 22:04:48 | 1/06 22:16:10 | 0:11:22 | 359.04 | Projected Load is lower than actual load. |
| 1/08 03:18:32 | 1/08 03:30:16 | 0:11:44 | 422.41 | Unit Trip. |
| 1/09 20:01:38 | 1/09 20:24:40 | 0:23:02 | 327.36 | SCE change -770 MW in 6 min. |
| 1/16 06:13:56 | 1/16 06:27:48 | 0:13:52 | 826.55 |  |
| 1/16 21:17:02 | 1/16 21:36:04 | 0:19:02 | 322.08 | Out of URS. |
| 1/17 07:13:08 | 1/17 07:30:03 | 0:16:55 | 327.47 | Out of URS, SCE change -80 MW in 2 min, Steel Mill Load pick up 50 MW in 4 min. |
| 1/18 18:06:36 | 1/18 18:19:08 | 0:12:32 | 327.24 | Out of URS, SCE change -170 MW in 5 min, Steel Mill Load pick up 50 MW in 1 min. |
| 1/19 18:16:50 | 1/19 18:31:06 | 0:14:16 | 322.08 | SCE change -420 MW in 10 min caused depletion of URS. |
| 1/20 19:07:01 | 1/20 19:16:45 | 0:09:44 | 353.77 | Out of Up Reg at 19:04. Steel Mill Load pick up 180 MW in 5 min. |
| 1/20 19:29:59 | 1/20 19:44:07 | 0:14:08 | 327.36 | Projected Load is lower than actual load. |
| 1/20 22:01:47 | 1/20 22:28:51 | 0:27:04 | 359.04 | SCE change -520 MW in 5m and Slow Unit Response |
| 1/23 20:59:13 | 1/23 21:30:41 | 0:31:28 | 374.90 | SCE change -1000 MW in 7 min. |
| 1/25 08:19:42 | 1/25 08:38:37 | 0:18:55 | 702.24 |  |
| 1/26 06:10:42 | 1/26 06:28:25 | 00:17:43 | 337.94 | Out of Up Reg at 6:10. |
| 1/28 04:54:51 | 1/28 05:14:34 | 0:19:43 | 586.08 |  |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC |  | RPRS S1 |  | RPRS S2 |  | RPRS S1+S2 |  | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| W RIO | 124 |  | 13 |  | 0 |  | 13 |  | 137 |
| DFW | 26 |  | 2 |  | 23 |  | 25 |  | 51 |
| North | 2 |  | 6 |  | 25 |  | 31 |  | 33 |
| Austin | 19 |  | 0 |  | 12 |  | 12 |  | 31 |
| E RIO | 18 |  | 4 |  | 0 |  | 4 |  | 22 |
| Laredo | 0 |  | 16 |  | 2 |  | 18 |  | 18 |
| Western | 0 |  | 3 |  | 11 |  | 14 |  | 14 |
| Houston | 1 |  | 0 |  | 11 |  | 11 |  | 12 |
| San Antonio | 0 |  | 0 |  | 10 |  | 10 |  | 10 |
| South | 0 |  | 7 |  | 0 |  | 7 |  | 7 |
| Northeast | 0 |  | 0 |  | 6 |  | 6 |  | 6 |
| Corpus | 0 |  | 2 |  | 0 |  | 2 |  | 2 |
| Bryan Area | 0 |  | 0 |  | 0 |  | 0 |  | 0 |
| Total | 190 |  | 53 |  | 100 |  | 153 |  | 343 |
| Historical Totals |  | Jan-09 |  | Jan-08 |  | Dec-08 |  |  |  |
| Austin |  | 19 |  | 1 |  | 9 |  |  |  |
| Bryan Area |  | 0 |  | 7 |  | 0 |  |  |  |
| Corpus |  | 2 |  | 0 |  | 1 |  |  |  |
| DFW |  | 28 |  | 0 |  | 24 |  |  |  |
| E RIO |  | 22 |  | 0 |  | 8 |  |  |  |
| Houston |  | 1 |  | 0 |  | 1 |  |  |  |
| Laredo |  | 16 |  | 51 |  | 14 |  |  |  |
| North |  | 8 |  | 0 |  | 17 |  |  |  |
| Northeast |  | 0 |  | 2 |  | 0 |  |  |  |
| San Antonio |  | 0 |  | 1 |  | 0 |  |  |  |
| South |  | 0 |  | 0 |  | 10 |  |  |  |
| W RIO |  | 137 |  | 0 |  | 107 |  |  |  |
| Western |  | 3 |  | 4 |  | 7 |  |  |  |
| Total |  | 243 |  | 66 |  | 198 |  |  |  |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Aspermont - Spur 138KV | Jayton - Spur 69 kV | 19 |
| Sandow Switch - Austrop 345KV | Sandow Switch - Elgin Switch 138 kV | 10 |
| Victoria - Victoria DuPont 138KV | Formosa - Lolita 138KV | 8 |
| Garfield 345/138KV Transformer T1 | Garfield 345/138KV Transformer T2 | 8 |
| Bosque Switch - Whitney TU 138KV | Lake Whitney - Bosque Switch 138 kV | 7 |
| Menard - Gillespie 138KV | Menard autotransformer 138/69KV | 6 |
| Aspermont - Spur 138KV | Spur autotransformer 69/138KV | 5 |
| Elgin Switch - Gilleland Creek 138KV | Elgin Switch - Taylor 138 kV | 5 |
| Sandow Switch - Austrop Switch 345KV | Austrop 345/138KV Autotransformer T1 | 5 |
| Sun Switch - Morgan SES 138KV | Sun Switch - Sacroc 138 kV | 5 |
| Dilley Switch - San Miguel 138KV | Derby - Pearsall 69KV | 4 |
| Garfield - Onion - Hicross 138KV | Austrop 138KV T2 | 3 |
| San Angelo - Live Oak 138KV | San Angelo Concho - San Angelo Lake Nasworthy 69KV | 3 |
| Abilene South - Eskota Switch 138KV | Merkel - Trent 69KV | 2 |
| Abilene South - Eskota Switch 138KV | Eskota Switch 138/69KV autotransformer | 2 |
| Austrop - Daffin and Decker 138KV | Elgin - Taylor 138KV | 2 |
| Crane LCRA - Spudder Flats 138KV | Crane LCRA - Rio Pecos 138KV | 2 |
| Golden Switch - Bluff Creek 138KV | Sun Switch - Sacroc 138KV | 2 |
| Graham - Benbrook and Parker Switch 345KV | Flat Creek - Leon Switch 138KV | 2 |
| Jack County - Reno 138 KV | Bowie 138/69KV transformer | 2 |
| Lamesa 138/69KV autotransformer | Bluff Creek Switch - Sharon Ridge 138KV | 2 |
| Oasis - PH Robinson 345KV | Garrott - Midtown 138KV | 2 |
| Temple Pecan Creek - Tradinghouse and Temple Switch - Lake Creek 345KV | Menard - San Angelo Power Station 138KV | 2 |
| Royse Switch - Farmersville 345KV | Farmersville - Royse Switch 345KV | 1 |
| Asherton - West Batesville 138KV | Asherton 138/69KV autotransformer | 1 |
| Austrop - Lost Pines 345KV | Fayetteville 345/138KV Auto | 1 |
| Calavers - Skyline and Walzem Road 138KV | Westside - Five Points 138KV | 1 |
| Dilley Switch - Asherton 138KV | Camp Woods - Leakey 69KV | 1 |
| Graham - Long Creek 345KV | Menard - San Angelo Power Station 138KV | 1 |
| Jewett - Tomball 345KV | Garrott - Midtown 138KV | 1 |
| Joslin - North Carbide 138KV | Victoria DuPont Switch - Joslin 138KV | 1 |
| Lon Hill - Whitepoint 345KV | Nueces Bay - Whitepoint 138KV | 1 |
| Moore - Uvalde 138KV | Camp Woods – Leakey 69 kV | 1 |
| Morgan Creek – Sun Switch 138KV | Menard – San Angelo Power Station 138KV | 1 |
| Odessa EHV autotransformer #2 345/138KV | Odessa EHV autotransformer #1 345/138KV | 1 |
| Odessa EHV – Morgan SES and Quail Switch 345kV | Big Spring Switch – Big Spring West 138kV | 1 |
| Sandow Switch - Austrop 345KV | Menard – San Angelo Power Station 138 kV | 1 |
| Sandow Switch - Austrop Switch 345KV | Elgin Switch - Butler 345/138KV | 1 |
| South Channel - Jefferson 138KV | Jefferson - Crown 138KV | 1 |
| South Channel - Jefferson 138KV | Crown - Galena Park 138KV | 1 |
| West Columbia - Sweeny 138KV | Sweeny Sub - Old Ocean 69KV | 1 |
| West Levee - 800/900 NWK 138KV | West Levee - Dealey Street 138KV | 1 |
| Zorn - Marion - Clearsprings 345KV | Clearsprings 345/138KV Auto #1 | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West-North | 18 |
| North – South | 2 |

New RAP (Date indicates last update of RAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 01/30/2009 | Frequency Control Desk V 3 Rev 73 | 402 |
| 01/30/2009 | Transmission & Security Desk V 3 Rev 99 | 401 |
| 01/30/2009 | Shift Supervisor Desk V 3 Rev 54 | 400 |
| 01/30/2009 | Operating Period Desk V 2 Rev 25 | 399 |
| 01/30/2009 | Day-Ahead Desk V 3 Rev 39 | 398 |

## Blackout/Load Shed Incidences

None

EECP

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

None

Communication

None

## ERCOT peak (Unofficial)

1/29 	   08:00 45,442 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2006 | 2007 | 2008 | 2009 |
| January | 4.79 | 4.55 | 3.30 | 4.11 |
| February | 4.81 | 3.75 | 3.59 | NA |
| March | 4.95 | 2.70 | 3.29 | NA |
| April | 5.59 | 3.00 | 2.45 | NA |
| May | 3.59 | 3.22 | 3.01 | NA |
| June | 2.65 | 4.46 | 2.81 | NA |
| July | 2.62 | 4.29 | 2.55 | NA |
| August | 2.09 | 3.11 | 3.66 | NA |
| September | 4.03 | 3.78 | 4.99 | NA |
| October | 3.63 | 3.08 | 2.79 | NA |
| November | 3.28 | 2.95 | 2.60 | NA |
| December | 3.44 | 3.74 | 4.54 | NA |
| Annual Average | 3.79 | 3.55 | 3.18 | 4.11 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 1/3/09 | 9:11 | 14:15 | OCN potential capacity shortage for operating hour 19:00. |
| 1/4/09 | 8:30 | 10:30 | OCN potential capacity shortage for operating hours 19:00 - 23:00. |
| 1/4/09 | 10:30 | 12:15 | Alert potential capacity shortage for hours 19:00 to 23:00. |
| 1/4/09 | 17:35 | 21:20 | Advisory ARR below 3000 MW. |
| 1/7/09 | 6:10 | 8:15 | Deployed NSRS in Houston, North and South zones due to depletion of Up Balancing Energy bids. |
| 1/7/09 | 6:54 | 8:25 | Advisory ARR below 3000 MW. |
| 1/8/09 | 7:05 | 9:00 | Advisory ARR below 3000 MW. |
| 1/20/09 | 17:56 | 23:00 | Advisory ARR below 3000 MW. |
| 1/20/09 | 18:36 | 21:30 | Deployed NSRS in all zones for IE 19:15 due to depletion of UBES. |
| 1/21/09 | 7:00 | 10:00 | Advisory ARR below 3000 MW |
| 1/24/09 | 3:45 | 14:45 | OCN projected capacity shortage for HE12:00 - 13:00 & 18:00. |
| 1/24/09 | 10:13 | 14:45 | Advisory ARR below 3000 MW. |
| 1/26/09 | 7:03 | 9:00 | Advisory ARR below 3000 MW |
| 1/26/09 | 19:00 | 0:00 | OCN anticipated freezing precipitation in the ERCOT region. |
| 1/27/09 | 18:38 | 0:00 | Advisory freezing precipitation across the ERCOT Region. |
| 1/27/09 | 0:15 | 18:38 | OCN anticipated freezing precipitation in the ERCOT region. |
| 1/28/09 | 0:15 | 11:21 | Advisory freezing precipitation across the ERCOT Region. |

Transmission

01/27   08:52	Transmission Alert issued for post-contingency overload of San Angelo - Big Lake 69 kV due to forced outage.

Emergency Notice

01/16   18:10	Emergency Notice issued due to Replacement Reserve Service (RPRS) did not meet Market time line.

Texas RE Event Analysis

01/04  01:08	SPS at Whirlwind Energy Center activated.

01/04   02:00   SPS at Stanton Wind Energy Center activated.

01/09   08:42	SPS at Ocotillo Wind Farm activated.

01/16   18:10   Emergency Notice issued due to the Replacement Reserve Service did not meet Market time line.

01/23   02:00   Austin EMMS Servers were unavailable

Other

01/07   06:25	Held IE 06:30 real-time balancing deployments for IE 06:45 due to an incorrect off-set calculation, resumed with IE 07:00 deployments.