Standard Development Roadmap

This section is maintained by the drafting team during the development of the standard and will be removed when the standard becomes effective.

Development Steps Completed

SAR submitted April 15, 2008.

RSC Accepted May 27, 2008.

Drafting Team was Nominated and Selected in June 2008.

Drafting Team Met July 10, 2008.

Drafting Team Met August 14, 2008.

Drafting Team Met September 2, 2008.

Drafting Team Met September 9-10, 2008, with PDCWG.

Drafting Team Met September 16, 2008.

Drafting Team Met October 3, 2008.

Drafting Team Met October 23, 2008.

Drafting Team Met November 21, 2008.

Drafting Team Met December 5, 2008.

Drafting Team presented initial draft to RSC at December 16, 2008 meeting.

Drafting Team Met February 5, 2008.

Description of Current Draft

This drafting team has completed an initial draft including all requirements, measures, and levels of compliance per the FERC Order associated with this variance.  This initial draft still needs revisions by the team.

Future Development Plan:

Anticipated Actions							Anticipated Date

Revise									September 5, 2008

Consider at PDCWG							September 9-10, 2008

Revise									September 16, 2008

Revise									October 3, 2008

Report and update RSC						October 7, 2008

Revise									October 23, 2008

Revise									November 21, 2008

Revise/finalize initial draft						December 5, 2008

Present initial draft to RSC						December 16, 2008

Revise									February 5, 2009

Revise									February 26, 2009

Present final draft to RSC						March 4, 2009

Post for Comment							March 2009

Respond to Comments/Revise					April 2009

Present revised draft to RSC						May 2009

Form ballot pool and vote						May/June 2009

TRE Board Adopt (Tentative)					July 2009

NERC Submit	(Tentative)						August 2009

FERC Approval (Tentative)						October 2009

Definitions of Terms Used in Standard

This section includes all newly defined or revised terms used in the proposed standard.  Terms already defined in the Reliability Standards Glossary of Terms are not repeated here.  New or revised definitions listed below become approved when the proposed standard is approved.  When the standard becomes effective, these defined terms will be removed from the individual standard and added to the Glossary.

Measurable Event:  A sudden change in interconnection frequency that will be evaluated for interconnection frequency response performance and will meet one of the following:

- a change in interconnection frequency that has a pre-perturbation average frequency to post-perturbation average frequency absolute deviation greater than 100 mHz (the 100 mHz value may be adjusted by the BA to capture 30 to 40 events per year).  See Attachment 3 for detailed criteria for this measurement.

or

- a change in a Generation Resource, DC tie or firm load pre-perturbation average MW output to post-perturbation average MW output absolute deviation greater than 550 MW (the 550 MW value may be adjusted by the BA to capture 30 to 40 events per year).  See Attachment 3 for detailed criteria for this measurement.

Interconnection Minimum Frequency Response:    The minimum frequency response limit for the Interconnection that is initially set at 420 MW/0.1 Hz.  See Attachment 1 for measurement detail.

Perturbation:  Any disturbance of motion, course, arrangement, or state of equilibrium that causes a sudden change in frequency on the Bulk Electric System.

t (0):  It is the time of the first observable change in Interconnection frequency at the beginning of a perturbation.

Pre-perturbation:  The 16-second period of time before t(0).

Post–perturbation:  The 34-second period of time starting 20 seconds after t(0).

Generation Resource:  A generator that is capable of providing energy or Ancillary Service to the ERCOT System and is registered with ERCOT as a Generation Resource.

- Introduction

- Title:		Real Power Balancing Control Performance

- Number:		BAL-001-TRE-1 (Regional Variance)

- Purpose:		To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time.  This regional variance replaces the CPS2 Waiver that was approved for ERCOT by NERC on November 21, 2002.  Specifically, this variance replaces requirement 2 of BAL-001-0a per FERC Order 693.

- Applicability:	Balancing Authorities (BA), Generator Owners (GO), Generator Operators (GOP)

- Effective Date:	Within an appropriate time after final regulatory approval and with a three-year implementation plan to allow Generation Resources time to meet the requirements.  See outline of implementation plan in Attachment 4.

- Requirements

- The Balancing Authority for the ERCOT Interconnection shall identify Measurable Events (as defined in this regional standard) for primary governing frequency response measurement of Generation Resources and load.

- Within 30 days of a Measurable Event, the Balancing Authority for the ERCOT Interconnection shall submit to the Compliance Enforcement Authority scan rate data necessary to analyze each Measurable Event identified in R1.  This data shall include:

- Interconnection Frequency;

- Interconnection scheduled frequency used in the ACE equation;

- Regulation Service deployed;

- Responsive Reserve Service deployed;

- Available Responsive Reserve Service (Nodal only);

- Generation Resource MW value;

- Control Error (Schedule CE in Zonal, Generation Resource CE in Nodal);

- Generation Resource Expected Frequency Response;

- Resource Regulation Service Allocation (Nodal only);

- Resource Economic Base Point (Nodal only);

- Resource High Operating Limit;

- Resource Low Operating Limit;

- Load Acting As Resource MW;

- Load Acting As Resource deployed;

- Resource Responsive Reserve Service Responsibility (Nodal only);

- ERCOT Load;

- MW value for loss of individual Generation Resource(s) or load that triggered the Measurable Event;

- Emergency Interruptible Load Service deployed;

- Time (synchronous time stamp to the nearest second for the data above).

- The BA shall analyze frequency and frequency movements and calculate the Interconnection Minimum Frequency Response (IMFR) (MW/0.1Hz) by January 1 of each year.

- The BA shall attain a twelve-month rolling average Interconnection Frequency Response, as measured in Attachment 1, greater than or equal to the Interconnection Minimum Frequency Response.

- For each Measurable Event, the frequency response performance of each interconnected Generation Resource shall be compiled by the BA as measured in Attachment 2.

- The BA shall calculate the twelve-month rolling average frequency response performance of each Generation Resource and report it to the Compliance Enforcement Authority.  Generation Resources less than 10 MW each, who at a single point of interconnection sum to an aggregate greater than 10 MW, shall be treated as a single Generation Resource.

- The GO shall report to ERCOT the operating range, performance level, and any parameter limiting the frequency response of each Generation Resource.  See Attachment 2 for reporting process.

- The GO shall ensure that combustion turbines have a governor droop characteristic of 4%, steam turbines have a governor droop characteristic of 5%, and that all other Generation Resources have a governor droop characteristic of 5% or less.  See Attachment 2 for these characteristics.

- Each GO shall limit governor dead bands, intentional and unintentional, of turbine governors to those stated in Attachment 2.

- Except for protection of equipment or safety, the GO and GOP will sustain its governor response to all frequency deviations that exceed the dead bands stated in Attachment 2.

- Each Generation Resource will meet a minimum twelve-month rolling average frequency response performance as stated in Attachment 2.  See chart of Figure 4: Measured Droop Performance and Minimum Performance and associated spreadsheet.

- Measures

- The BA shall have a procedure in place for identifying Measurable Events.

- The BA shall make available for inspection evidence that the data as specified in R2 was submitted to the Compliance Enforcement Authority for evaluation.

- The BA shall have available for inspection evidence that the analysis of the IMFR was performed as specified in R3.

- The BA shall have evidence it calculated the twelve-month rolling average frequency response performance of the Interconnection of all Measurable Events.

- For each Measurable Event, the BA shall have evidence it reported the performance of each interconnected Generation Resource to the Compliance Enforcement Authority.

- For each Measurable Event, the BA shall have evidence it reported the twelve- month rolling average performance of each Generation Resource to the Compliance Enforcement Authority.

- The GOP shall have evidence it reported to the BA, each Generation Resource’s governor operating range and expected frequency response performance for the full output range of each Generation Resource.

- The GO will complete the governor test form as shown in Attachment 3.

- The GO shall have evidence its frequency response Generation Resource’s governors are set in accordance to the limits in Attachment 2.

- Within the Measurable Event report, evidence of premature frequency response withdrawal by the Generation Resource was not visually observed.

- Within the Measurable Event report, the twelve-month rolling average frequency response performance of each Generation Resource met the minimum performance as stated in Attachment 2.  See spreadsheet of Figure 4: Measured Droop Performance and Minimum Performance.

- Compliance

- Compliance Monitoring Process

  - Compliance Enforcement Authority

Texas Regional Entity

  - Compliance Monitoring Period and Reset Time Frame

    - If a Generation Resource fails any requirement or measure of this standard, the GO and GOP will submit mitigation plans for the failing Generation Resource with a timeline not to exceed 90 days from the notification of failing performance.

    - Each Generation Resource will have a rolling event average performance as stated in Attachment 2 of this Standard.  If a Generation Resource completes a mitigation plan and implements corrective action that corrects past failing performance as measured by this standard, the rolling event average will be reset on the next successful performance during a measurable event and the Generation Resource will begin a new rolling event average performance.  If the Generation Resource fails the next measurable event performance, the GO and GOP will submit a follow-up mitigation plan with a timeline not to exceed 30 days from the notification of failing performance.

  - Data Retention

- The Balancing Authority, Generator Operator, and GOP shall keep data or evidence to show compliance, as identified below, unless directed by its Compliance Enforcement Authority to retain specific evidence for a longer period of time as part of an investigation:

- Each BA shall retain a list of identified Measurable Events since the last compliance audit for Requirement 1, Measure 1.

- Each BA shall retain all archived data since the last compliance audit for Requirement 2, Measure 2.

- Each BA shall retain all analysis and calculations since its last compliance audit for Requirement 3, Measure 3.

- Each BA shall retain all comparative calculations since its last compliance audit for Requirement 4, Measure 4.

- Each BA shall retain all calculations and compilations since its last compliance audit for Requirement 5, Measure 5.

- Each BA shall retain all calculations since its last compliance audit for Requirement 6, Measure 6.

- Each GOP shall retain evidence since its last compliance audit for Requirement 7, Measure 7.

- Each GO shall retain evidence since its last compliance audit for Requirement 8, Measure 8.

- Each GO shall retain evidence since its last compliance audit for Requirement 9, Measure 9.

- Each GO and GOP shall retain evidence since its last compliance audit for Requirement 10, Measure 10.

- Each GO shall retain evidence since its last compliance audit for Requirement 11, Measure 11.

The Compliance Enforcement Authority shall keep the last audit records and all requested and submitted subsequent records.

  - Compliance Monitoring and Assessment Processes

Compliance Audits

Self-Certifications

Spot Checking

Compliance Violation Investigations

Self-Reporting

Complaints

Periodic Data Submittals (if periodic reporting is listed, the reporting interval must be specified)

Exception Reporting (if exception reporting is listed, the conditions for the report must be specified)

- Violation Severity Levels

| - R # | - Lower VSL | - Moderate VSL | - High VSL | - Severe VSL |
| --- | --- | --- | --- | --- |
| - R1 |  |  |  | Did not have a procedure in place to identify MEs. |
| - R2 | Submitted Data to Compliance Enforcement Authority 45 days after the event. | Submitted Data to Compliance Enforcement Authority 60 days after the event. | Submitted Data 120 days after the event. | No submission was made to Compliance Enforcement Authority on the identified event. |
| - R3 |  |  | All changes in Generation Resources greater than ten MW, either individually or as aggregated behind a single meter, were not included in the IMFR analysis. | No analysis was performed to determine IMFR or there was no record of doing so. |
| - R4 | The twelve-month rolling average frequency response is less than 100% but greater than or equal to 90% of the IMFR. | The twelve-month rolling average frequency response is less than 90% but greater than or equal to 80% of the IMFR. | The twelve-month rolling average frequency response is less than 80% but greater than or equal to 70% of the IMFR. | The twelve-month rolling average frequency response is less than 70% of the IMFR. |
| - R5 |  |  |  | - No evidence of reporting to Compliance Enforcement Authority. |
| - R6 |  |  |  | - No evidence of reporting to Compliance Enforcement Authority. |
| - R7 |  |  | - The GOP does not have evidence that it reported to the BA most of its Generation Resource’s expected frequency response for its normal operating range. | - The GOP does not have evidence that it reported to the BA any of its Generation Resource’s expected frequency response for its normal operating range. |
| - R8 | - Completed governor droop test form dated longer than two years. | - Completed governor droop test form dated longer than three years. | - Completed governor droop test form dated longer than four years. | - The GOP does not have evidence that the governor droop characteristics were set per Attachment 2. |
| - R9 |  |  |  | - The GOP does not have evidence that the governor dead band limits were set per Attachment 2. |
| - R10 |  |  |  | - The GO or GOP applied control action to reduce or withdraw frequency response of a Generation Resource that exceeded the allowable dead bands as stated in Attachment 2. |
| - R11 | - The twelve month rolling average frequency response performance of a Generation Resource is greater than or equal to 0.45 P.U. and less than 0.55 P.U. as measured in Attachment 2. | - The twelve-month rolling average frequency response performance of a Generation Resource is greater than or equal to 0.35 P.U. and less than 0.45 P.U. as measured in Attachment 2. | - The twelve-month rolling average frequency response performance of a Generation Resource is greater than or equal to 0.25 P.U. and less than 0.35 P.U. as measured in Attachment 2. | - The twelve-month rolling average frequency response performance of a Generation Resource is less than 0.25 P.U. as measured in Attachment 2. |

- Regional Variances

- This is a regional variance to NERC Standard BAL-001-0a, specifically replacing R2.  Instead of complying with R2 in BAL-001-0a (CPS2), the BA, GO, and GOP in the ERCOT Interconnection maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time by the methods, requirements, and measures described in this regional standard and associated attachments and documents.

- Associated Documents

Waiver Request – Control Performance Standard 2

Organization

ERCOT

Operating Policy

ERCOT requests a waiver from Policy 1, “Generation Control and Performance,” Section E,

“Performance Standard” as follows:

Standards

1.2.	Control Performance Standard (CPS2). The average ACE for each of the six ten-minute periods during the hour (i.e., for the ten-minute periods ending at 10, 20, 30, 40, 50, and 60 minutes past the hour) must be within specific limits, referred to as L10. See the “Performance Standard Training Document,” Section B.1.1.2 for the methods for calculating L10.

Requirements

2.	Control Performance Standard (CPS) Compliance. Each CONTROL AREA shall achieve CPS1 compliance of 100% and achieve CPS2 compliance of 90% (see the “Performance Standard Training Document,” Section C).

Explanation

ERCOT requests a waiver from the CPS2 Standards and Requirements listed above for the following reasons:

- On July 31, 2001, the ERCOT Interconnection began operating as a single CONTROL AREA, asynchronously connected via two DC ties to the Eastern Interconnection. At that time, ERCOT changed from the traditional tie-line bias generation control algorithms in which ten CONTROL AREAS participated, to a single 15-minute interval competitive balancing energy market and a frequency control system that regulates around the balancing energy schedule on two-to-four second intervals. ERCOT requests that the Operating Committee reconsider CPS2 to ensure it is feasible under this new type of market-based control.

If the Operating Committee believes that the CPS2 is feasible, then ERCOT would suggest that Policy 1 (or the appropriate Compliance document) provide for a “test period” of six months to allow CONTROL AREAS making such a transition the opportunity to test new control algorithms provided they can show that reliability is not degraded during that period. ERCOT also believes that its L10 may not be appropriate as it is less than half of the L10 of another NERC CONTROL AREA of similar load size.

- The ERCOT Interconnection is now a single CONTROL AREA asynchronously connected to the Eastern Interconnection, and cannot create inadvertent power flows or frequency errors in other CONTROL AREAS. Therefore, the ISO questions whether the CPS2 Standard is necessary or even beneficial for such asynchronous operation. ERCOT is currently performing a study that compares its single CONTROL AREA performance against that of the former ten CONTROL AREA operations. Initial results of that study show that while the ten CONTROL AREAS individually met CPS2 standards, the aggregate CPS2 performance of the ten CONTROL AREAS did not, and was actually below that of the current single CONTROL AREA.

Current Operating Reliability

ERCOT does not believe that Frequency control within its new single CONTROL AREA INTERCONNECTION is less reliable as a result of non-compliance with the CPS2 Standard following its conversion. ERCOT Interconnection frequency control has been, and continues to be, very reliable since that conversion.

The table below shows ERCOT’s CPS2 performance for August through December 2000 as an INTERCONNECTION with ten Control Areas. The average CPS2 compliance was 74.82%. CPS2 compliance for ERCOT as a single control area for August 2001 was 83.88%, an improvement of approximately nine percentage points.

|  |  |  | Single Control Area |  | Average of | Average of |
| --- | --- | --- | --- | --- | --- | --- |
|  | % of Frequency Data | Supplier Of Frequency Data | CPS1 % | CPS2 % | Absolute1 min Averages Freq | Absolute10 min Averages Freq |
|  | Available |  |  |  | Deviation | Deviation |
| August-00 | 79 | ERCOT | 140.99 | 76.50 | 0.011978483 | 0.008299971 |
| September-00 | 100 | ERCOT | 134.89 | 76.02 | 0.012366 | 0.009495 |
| September-00 | 100 | REIT HLP | 135.91 | 77.01 | 0.012221795 | 0.008443165 |
| October-00 | 23 | ERCOT | 199.68 | 76.90 | 0.013910426 | 0.00857111 |
| October-00 | 100 | REIT HLP | 114.01 | 78.58 | 0.014621429 | 0.008120248 |
| November-00 | 65 | ERCOT | 105.19 | 67.20 | 0.015061531 | 0.010523159 |
| December-00 | 60 | ERCOT | 192.59 | 72.60 | 0.013428052 | 0.009330552 |
| Average | (See Note 1) |  | 134.71 | 74.82 | 0.013439915 | 0.009062032 |
| August-01 | None (See Note 2) | None (See Note 2) | 127.30 | 83.88 |  |  |

Note 1: Weighted Average Based on ERCOT for August, September November and December and REIT for October.

Note 2: From ERCOT CPS report. ERCOT is working on providing frequency data for August 2001.

FERC ORDER 693

FROM FERC ORDER 693, March 16, 2007, Paragraphs 309-315

Regional Difference to BAL-001-0: ERCOT Control Performance Standard 2

309. NERC approved a regional difference for ERCOT by allowing it to be exempt from Requirement R2 in BAL-001-0, which requires that the average area control error (ACE) for each of the six ten-minute periods during the hour must be within specific limits, and that a balancing authority achieves 90 percent compliance. This Requirement is referred to as Control Performance Standard 2 (CPS2).

310. NERC explains that ERCOT requested a waiver of CPS2 because: (1) ERCOT, as a single control area asynchronously connected to the Eastern Interconnection, cannot create inadvertent flows or time errors in other control areas and (2) CPS2 may not be feasible under ERCOT’s competitive balancing energy market. In support of this argument, ERCOT cites to a study that it performed showing that, under the new market structure, the ten control areas in its region individually were able to meet CPS2 standards while the aggregate performance of the ten control areas was not in compliance. Since requesting the waiver from CPS2, ERCOT has adopted section 5 of the ERCOT protocols which identify the necessary frequency controls needed for reliable operation in ERCOT.

311. In the NOPR, the Commission proposed to approve the ERCOT regional difference and have the ERO submit a modification of the ERCOT regional difference to include the requirements concerning frequency response contained in section five of the ERCOT protocols.

312. No comments were filed on this regional difference.

313. The Commission approves the ERCOT regional difference as mandatory and enforceable. Order No. 672 explains that “uniformity of Reliability Standards should be the goal and the practice, the rule rather than the exception.” However, the Commission has stated that, as a general matter, regional differences are permissible if they are either more stringent than the continent-wide Reliability Standard, or if they are necessitated by a physical difference in the Bulk-Power System. Regional differences must still be just, reasonable, not unduly discriminatory or preferential and in the public interest.

314. The Commission finds that ERCOT’s approach under section 5 of the ERCOT protocols appears to be a more stringent practice than Requirement R2 in BAL-001-0 and therefore approves the regional difference.

315. As proposed in the NOPR, the Commission directs the ERO to file a modification of the ERCOT regional difference to include the requirements concerning frequency response contained in section 5 of the ERCOT protocols. As with other new regional differences, the Commission expects that the ERCOT regional difference will include Requirements, Measures and Levels of Non-Compliance sections.

ERCOT Protocol 5.9

5.9	Frequency Response Requirements and Monitoring

5.9.1	Generation Resource and QSE Participation

5.9.1.1	Governor in Service

At all times a Generation Resource is on line, its turbine governor shall remain in service and be allowed to respond to all changes in system frequency.  Generation Entities shall not reduce governor response on individual Resources during abnormal conditions without ERCOT’s consent (conveyed by way of the Generation Entity’s QSE) unless equipment damage is imminent.

5.9.1.2	Reporting

Generation Entities shall conduct applicable generating governor speed regulation tests on Resources as specified in the Operating Guides.  Test results and/or other relevant information shall be reported to ERCOT and ERCOT shall forward results to the appropriate TSPs.

Resource governor modeling information required in the ERCOT Planning Criteria shall be determined from actual Resource testing described in the Operating Guides.  Within thirty (30) days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the connected TSP.

When the governor of a Generation Resource is blocked while the Resource is operating, the QSE shall promptly inform ERCOT.  The QSE shall also supply governor status logs to ERCOT upon request.

Any short-term inability of a Generation Resource to supply governor response shall be immediately reported to ERCOT.

If a Generation Resource trips Off-line due to governor response problems, the Generation Entity shall immediately report the change in the status of the Resource to ERCOT and the QSE.

5.9.2	Primary Frequency Control Measurements

For the purposes of this section, the A Point is the last stable frequency value prior to a frequency disturbance.  For a decreasing frequency event with the last stable frequency value of 60.000 Hz or below, the actual frequency is used.  For a decreasing frequency event with the last stable frequency value between 60.000 and 60.036 Hz, 60.000 Hz will be used.  For a decreasing frequency event with the last stable frequency value above 60.036 Hz, actual frequency will be used.  For an increasing frequency event with the last stable frequency value of 60.000 or above, the actual frequency is used.  For an increasing frequency event with the last stable frequency between 59.964 and 60.000 Hz, 60.000 Hz will be used.  For an increasing frequency event with the last stable frequency value of 59.964 or below, the actual frequency is used.  ERCOT shall determine the A Point frequency for each event.

For the purposes of this section, the C Point is the lowest frequency value during the first five seconds of the event.

For the purposes of this section, the B Point is the “recovery” frequency value after the C Point.   The B Point should occur after full governor response of the turbines has occurred, usually between ten (10) and thirty (30) seconds after the A Point, but not greater than sixty (60) seconds after the A Point.  ERCOT shall determine the B Point for each event.

B Point Plus Thirty Seconds: At thirty seconds following the B Point, an analysis will be performed by ERCOT with the assistance of the appropriate ERCOT subcommittee to determine if primary frequency control response is sustained.

For the purposes of this section, a “Measurable Event” is the sudden change in interconnection frequency that will be evaluated for performance compliance will have i) a frequency B Point between 59.700 Hz and 59.900 Hz or between 60.100 Hz and 60.300 Hz, and ii) a difference between the B Point and the A Point greater than or equal to +/- 0.100 Hz.

5.9.2.1	ERCOT Required Primary Frequency Control Response

The combined response of all Generation Resources interconnected in ERCOT to a Measurable Event shall be at least 420 MW / 0.1 Hz. This value should be reviewed on an annual basis by ERCOT and the appropriate ERCOT subcommittee for system interconnect reliability needs.

ERCOT will evaluate, with the assistance of the appropriate ERCOT subcommittee, primary frequency control response during Measurable Events.  The actual Generation Resource response will be compiled to determine if adequate primary frequency control participation was available.

ERCOT and the appropriate ERCOT subcommittee will review each Measurable Event, verifying the reasonableness of data.  Data that is in question may be requested from the QSE for comparison and/or individual Resource data may be retrieved from ERCOT’s database.

ERCOT’s performance will be averaged using the most recent six (6) Measurable Events to determine its rolling average contribution.

5.9.3	ERCOT Data Collection

5.9.3.1	Data Collection

ERCOT will collect all data necessary to analyze each Measurable Event.  This will include the following real-time data:

(1)	Interconnection Frequency;

(2)	Regulation Service deployed;

(3)	Responsive Reserve Service deployed;

(4)	QSE available  Responsive Reserve Service;

(5)	QSE total Generation;

(6)	QSE SCE;

(7)	QSE Bias;

(8)	QSE LaaR MW;

(9)	LaaR deployed;

(10)QSE Responsive Reserve Service;

(11)ERCOT Load and individual Resource(s) that contributed to the frequency deviation; and

(12)EILS deployed.

#### Version History

| Version | Date | Action | Change Tracking |
| --- | --- | --- | --- |

Part 1:  Measuring ERCOT Interconnection Frequency Response

The process for measuring Interconnection Frequency Response requires scan rate data of Interconnection frequency and scan rate data of the Generation Resource(s) or Load(s) causing the perturbation.  This data must be aligned to eliminate time skew.  The steps in the frequency response calculation are: 1) Determine the scan data for t (0), which is the first scan of frequency that frequency deviates from normal.  This scan value identifies the beginning of the perturbation; 2) Calculate the average of the Pre and Post perturbation of the Interconnection frequency and megawatt of the Generation Resource(s) or Load(s) causing the perturbation; 3) Take the mathematical differences of each parameter, divide the difference in megawatt change by the difference in frequency change and 4) Divide this quotient by 10 for the standard form in MW per tenth Hz (MW/0.1Hz).  An Excel spreadsheet named “Frequency Response data report for Single BA Interconnection 2 second scan.xls” is included in this attachment and performs the frequency response calculation.  See Figure 1 below.

Figure 1:  Interconnection frequency response measurement.

Attachment 2

Part 1:  Governor dead band and droop settings

Governor Dead Bands:

Mechanical governors of steam turbine Generation Resources:  Due to gear lash and movement of mechanical parts of a mechanical fly-ball governor on a steam turbine, it is common to observe frequency response dead band for small changes in frequency.  This dead band, or range of no frequency response, shall be limited to less than +/- 0.036 Hz (36 mHz).

Electronic and digital governors of Generation Resources:  Intentional governor dead bands on electronic and digital governors should be avoided.  If intentional frequency response dead band of electronic or digital governors is necessary for Generation Resource stability, it shall be limited to a maximum of +/- 0.01667 Hz (16.67 mHz or one rpm on a two pole generator) as measured from 60.000 Hz.  Once frequency deviation has exceeded the governor dead band from 60.000 Hz, the frequency response characteristic shall not “step-into” the 5% droop curve or the 4% droop curve.  The droop curve shall linearly add frequency response and attain the 5% droop curve characteristic when frequency deviation reaches +/-3.0 Hz or attain the 4% droop curve characteristic when frequency deviation reaches +/-2.4 Hz.

Governor Droop Setting:

Steam Turbine:

Droop settings of steam turbines shall be 5% or lower.  The 5% droop curve shall linearly add frequency response and attain the 5% droop curve characteristic when frequency deviation reaches +/-3.0 Hz.

Combustion turbines operating in Combined Cycle mode, single or multiple shafts:

Combustion turbines, operating in a “combined cycle mode”, governor shall be set at 4% droop or lower.  The 4% droop curve shall linearly add frequency response and attain the 4% droop curve characteristic when frequency deviation reaches +/-2.4 Hz.

Combustion turbines operating in a simple cycle mode:

Combustion turbines, not operating in a “combined cycle mode”, governor shall be set at 5% droop or lower.  The 5% droop curve shall linearly add frequency response and attain the 5% droop curve characteristic when frequency deviation reaches +/-3.0 Hz.

Wind turbine:

Wind turbines that have droop capability shall have a droop setting of 5% or lower.  The 5% droop curve shall linearly add frequency response and attain the 5% droop curve characteristic when frequency deviation reaches +/-3.0 Hz.

Other Generation Resources:

Other Generation Resources that have droop capability shall have a droop setting of 5% or lower.  The 5% droop curve shall linearly add frequency response and attain the 5% droop curve characteristic when frequency deviation reaches +/-3.0 Hz.

Part 2:  Minimum performance of turbine governors during actual grid frequency deviations.

The measurement of frequency response can be challenging.  There are conditions when the mathematical calculations that perform the measurement of performance do not account for all control functions of a Generation Resource.  The following situations are known to cause measurement techniques to improperly measure performance:

- Previous AGC or manual control to change the Generation Resources output.  If the Generation Resource is ramping from one output level to another during a measurable frequency deviation, frequency response may be difficult to measure.  This is true if the ramp direction is in the same direction as the frequency deviation, that is, the Generation Resource is in a down ramp during a low frequency deviation (see Figure 1 below) or up ramp during a high frequency deviation.  This is especially true for Generation Resources that have high ramp rates in comparison to their maximum capability.  All Generation Resources shall be responsive to all frequency deviations exceeding the governor dead band while ramping.  If frequency response is visually apparent during these ramps and the direction of the ramp causes the measurement of the frequency response to be below the minimum performance level, the Event may be removed from the Generation Resources’ 12 month rolling average performance measure.

- Conventional steam driven turbines will have some initial steam pressure drop following large low frequency deviations.  This pressure drop should be minimized by the control functions of the steam generator while remaining within the thermal and physical limits of the steam generator.  (see Figure 2 below)  The same effect is true for high frequency deviations.  Steam generator pressure will rise from the frequency response of the turbine thereby reducing the net frequency response of the turbine.  The Generator Owner may provide an estimation of this effect in the form of a “parameter” curve to be added to the measurement spreadsheet that accounts for this stored energy limitation.

- Steam turbines of combined cycle Generation Resources.  These turbines depend on the waste heat of combustion turbines to provide additional steam supply for their frequency response.  The cycle time of the heat recovery boiler is typically longer than the performance measure of this standard and performance of these Generation Resources will measure below normal droop characteristic curves.

- Generation Resources located at the same site as the Generation Resource that causes the perturbation may have a shift in site auxiliary load assignment during the measurement period.  This may result in a decrease in “Net” output of the Generation Resource and affect the measurement of frequency response.  In this scenario Gross megawatt values for Generation Resource output and Gross High Operating Limit may be used for the evaluation of the frequency response measurement of the Generation Resource.

- Generation Resources may have auxiliary equipment that must be placed in service throughout the load range of the Generation Resource.  If the Generation Resource is operating at an output level that requires placing in service auxiliary equipment, frequency response of the Generation Resource may be limited.  This may result in below minimum frequency response performance.  The Generation Owner shall document this limitation on each occurrence during a Measurable Event.  Once the equipment is placed in service, full frequency response is expected.

- Generation Resources operating near the High Operating Limit (HOL) of the Generation Resource can measure below the minimum frequency response performance level.  The expected performance shall be limited to the HOL of the Generation Resource.

- Generation Resources operating at extremely low output levels may have limited frequency response.  This output level may be defined as the Emergency Low Operating Limit, and responding to frequency deviations may place the Generation Resource at risk.  The Generator Owner shall identify and document these operating ranges.

- Generation Resources operating at extremely high output levels may have limited frequency response.  This output level may be defined as the Emergency High Operating Limit, and responding to frequency deviations may place the Generation Resource at risk.  The Generator Owner shall identify and document these operating ranges.  Generation Resources operating in this range shall not be assigned Responsive Reserve Service since frequency response is not available.  This may include these operating conditions:

  - Over-pressure operation of the steam generator

  - Duct burner operation of combined cycle Generation Resources

  - Steam augmentation of combustion turbines and the injection of steam into the turbine combustors.

- Figure 1:  Combustion Turbine – 4% Droop during “Down Ramp”

- Figure 2:  Conventional Steam Turbine @ 5% Droop and Effects of available stored energy.

- Figure 3.  Effects of governor dead band and limited stored energy on frequency response

- Measurement of Generation Resource Frequency Response

- The method used to calculate Generation Resource frequency response is similar to the method used in calculating the Interconnection frequency response.  The same averaging periods of Pre and Post perturbation are used.  The output, in megawatts, of the Generation Resource is used in place of the “Resource Lost” data.  Additional Generation Resource information is required for the evaluation.  These data are HOL, governor droop setting, governor dead band setting and any parameter that reduces Generation Resource performance as in “limited stored energy” or “reduced mass flow” at lower speeds (frequency).  Excel spreadsheets are attached that provide measurement processes of droop performance of steam turbines and combustion turbines.  These same spreadsheets can be used by combustion turbines operating in combined cycle mode or simple cycle mode.  Other non steam turbine Generation Resources can use the steam turbine spreadsheet as well.  The spreadsheet names are:

- Droop Calc 0.0166 Hz db 5% Steam Unit.xls

- Droop Calc 0.0166 Hz db 4% CT and ST.xls

- Each spreadsheet calculates five performance levels of the Generation Resource.  (see Figure 4 below)  The first evaluation is exact droop target based on the droop setting of the Generation Resource (4 or 5%).  The second evaluation is the exact droop target adjusted for the governor dead band of the Generation Resource.  The third evaluation is the “target droop performance” derived from the target droop performance based on the governor deadband and adjusted for “available stored energy” or “reduced mass flow at lower speeds” parameter for the particular Generation Resource.  The Generator Owner must develop the “limiting parameter” curve for each Generation Resource.  This limiting parameter curve must be technically justifiable.  The fourth evaluation is the “minimum frequency response performance” level for this Generation Resource on this event.  The value is derived from 75% of the third evaluation calculation.  The fifth and final evaluation is the actual performance of the Generation Resource.  The performance of the Generation Resource will then be calculated on a per unit measure by dividing the “Actual” performance by the “Minimum” performance.  This value will be used to develop the twelve month rolling average performance of the Generation Resource.  The Minimum Performance value shall be limited by the HOL and LOL of the Generation Resource.

- Figure 4:  Measured Droop Performance and Minimum Performance

Attachment 3

The goal of these criteria is to capture 30 to 40 events each year.  These criteria shall be adjusted by the BA to achieve at least the minimum target number of events.

Part 1:  Frequency deviation criteria

In the attached Excel spreadsheet “ERCOT Measurable Event Detection.xls” ERCOT scan rate frequency data is collected and automatically analyzed for frequency deviations.  The size of the frequency deviation used in the analysis can be controlled in cell C1 of the first worksheet “2secHz” and is presently set at 0.100 Hz (100 mHz).  This value in Hz deviation will control how many “events” will be detected from the data set.  The data set will collect eleven days of 2 second data and summarize the total number of events detected in the data column.  Not all events detected by the spreadsheet will be valid frequency events for performance measurement.  Any event detected that results in the “post–perturbation” average frequency ending within the turbine governor deadbands (~60.020 to ~59.980 Hz) should be eliminated.  Also, any event that has a median frequency deviation near 60.000 Hz should be eliminated.  This would require the Pre to Post perturbation frequency to center around 60.000 Hz.  This measurement of Interconnection frequency response would include dead bands in both directions from 60.000 Hz and turbine governor performance will be reduced due to the dead band impact of the non responsive regions.  Valid frequency deviations for performance evaluation shall have the Post-perturbation frequency further from 60.000 Hz than the Pre-perturbation frequency.

As the performances of Generation Resources improve as a result of this standard, the Interconnection frequency profile will improve and fewer “false” event detections will be detected by the spreadsheet.  It is also likely that with this improved frequency response, the frequency deviation value in cell C1 will have to be decreased to achieve the target number of Measurable Events.

Part 2:  MW change causing or contributing to the perturbation

Accurate accounting of the change in megawatts contributing to the perturbation is necessary for proper evaluation of Interconnection frequency response.  Most events will be the result of a single Generation Resource or group of Generation Resources (combined cycle plants).  However, the Balancing Authority should consider changes in “non-conforming load” during the measurement period and include sympathetic Generation Resource trips that occur during the measurement period.  Generation Operators are required to report such trips to the BA.  This standard sets 550 MW within 20 seconds as the trigger level to perform an Event analysis.  The BA may adjust this value to achieve the targeted number of Measurable Events each year.