## Slide 1: Texas Phasor Project
ERCOT
Reliability and Operations Subcommittee (ROS)
February 12, 2009
Milt Holloway, Center for the Commercialization of Electric Technologies
Manu Parashar, Consortium for Electric Reliability Technology Solutions
John Adams, ERCOT

## Slide 2: Who is CCET?
University
Researchers
Electric Utilities & Competitive Retailers
High-Tech
Companies
The Center for the Commercialization of Electric Technologies brings together electric utilities, university researchers and high-tech companies to find technology solutions to challenges facing the electric power industry
Technology Solutions
2

## Slide 3: CCET Members
University
Researchers
High-Tech
Companies
3
Electric Utilities & Competitive Retailers
Electric Utilities
Competitive Retailers

## Slide 4: CCET: A Unique Approach
Through CCET, electric utilities, technology companies and educational institutions collaborate and fund projects to enhance the:
Security
Reliability
Efficiency
Power Quality
Safety
of the Texas electric infrastructure through:
Research
Development
Demonstration and
Commercialization of advanced technologies
within the Electric Reliability Council of Texas (ERCOT) interconnected grid.
4

## Slide 5: CCET Has Funded Five Projects
Demand Response Pilot
Synchronized Sampling and Phasor Development
Remote Terminal Unit Development
Common Information Model
IEEE Student Contest to Develop Transformer Monitor
5

## Slide 6: Who Is CERTS? Why Are We Here?
The Consortium for Electric Reliability Technology Solutions (CERTS) was organized in 1999 as a partnership among four DOE national labs (LBNL, ORNL, PNNL, SNL), universities (PSERC), and the Electric Power Group
CERTS has been managing phasor research since 2002 and has extensive experience with phasor technology, applications, and utilization within the Eastern Interconnection and Western Interconnection
Under the direction of the DOE Office of Electric Delivery and Energy Reliability, CERTS provided technical support for the start-up of the Eastern Interconnection Phasor Project, which has now transitioned to be the industry-led North American Synchrophasor Initiative (NASPI) managed by NERC
On September 4, 2008, the CCET Board passed a resolution inviting DOE/NASPI/CERTS to transfer expertise and provide resources to support CCET/ERCOT/Texas utilities deploy phasor technology in Texas

## Slide 7: What is Phasor Technology?  Key for the Grid of The Future
Page <number>
02.12.09
Page <number>
02.12.09
Phasor Measurement Units – Mature Hardware, Emerging Networks and Applications
  Supplements 4-second scan rate of current SCADA technology with higher resolution scans (e.g., 30 samples per second)
  GPS time stamping enables synchronization of data from multiple sources spanning an entire interconnection
Provides MRI Quality Visibility of a Power System Compared to X-ray Quality Visibility From Traditional SCADA
Addresses Current Industry Problems
  Visualization – wide area, common data, common displays
  Security Assessment – safe operating zones
  Post-disturbance Analysis and Model Validation
  Renewables Integration
  Reliability Standards Monitoring

## Slide 8: Starter Phasor Measurement System Architecture – Currently Installed at ERCOT
Advantages
Scalable architecture design to include other Texas utilities in the future
Expansion Steps
Install BPA-developed PDC at ERCOT
Network additional AEP and Oncor PMUs to ERCOT PDC
Install and network PMUs at other utilities to ERCOT PDC
Leverage NASPI technical specifications and distributed architecture designs/protocols – Install next generation PDC at ERCOT
AEP PDC sending data to RTDMS Web Server installed at ERCOT via VPN

## Slide 9: Real Time Dynamics Monitoring System (RTDMS)
Page <number>
02.12.09
Page <number>
02.12.09
Purpose
RTDMS™ (and Phasor-RTDMS) is a software application platform that utilizes high resolution time-synchronized data for electric power grid reliability monitoring and management by electric power grid operators, reliability coordinators, reliability managers, and operating engineers
Uses -- RTDMS application helps identify:
Grid Stress --- phase angle measurements
Grid Robustness – damping status and trend
Dangerous Oscillations – low damping
Frequency Instability – frequency variation across interconnection
Voltage Instability – low voltage zones
Reliability Margin – “How far are we from the edge” – sensitivity metrics
Application Users
The first prototype application was tested in 2003 – currently in use at CAISO, BPA, TVA, WECC utilities, and other NASPI participants
Real Time Dynamics Monitoring System. ®Built upon GRID-3P Platform, U.S. Patent 7,233,843. Electric Power Group. All rights reserved.

## Slide 10: Real Time Dynamics Monitoring System - ERCOT
Page <number>
090408
GAUGE
Quantifies the worst performing metric
LOCATION INDICATORS
Provides information for specific locations or jurisdictions
TRAFFIC LIGHTS
Provides status of specific metrics across the interconnection
R
Y

## Slide 11: Phasor-Grid Dynamics Analyzer (PGDA) – Offline Analysis Tool (Dec. 16, 2008 Event)

## Slide 12: What Are ERCOT’s Plans for 2009?
Install BPA PDC at Taylor
Expand network of PMUs (AEP, Oncor)
Gain experience with RTDMS; improve data quality
Initiate studies of damping on ERCOT system
Research thresholds for intelligent alarming
Determine value of PMUs for ERCOT operations; if net positive, assess options and next steps for sustaining a monitoring capability at ERCOT (e.g., acquire production grade PDC from commercial vendor in 2010)
Work with NERC/NASPI staff to resolve data sharing issues

## Slide 13: Texas Phasor Research and Implementation --Proposed Time-line
 | 2008 | 2009 | 2010 | 2011
INFRASTRUCTURE |  |  |  | 
Current | √ | √ |  | 
Expanded |  | √ | √ | √
Production Grade |  |  |  | √
REAL-TIME MONITORING |  |  |  | 
Visualization and Alarming | √ | √ | √ | √
Advanced Stability Applications |  | √ | √ | √
OFFLINE ANALYSIS |  |  |  | 
Banked Data | √ | √ | √ | √

## Slide 14: Schweitzer has provided UT Austin with starter PMU network for research and educational purposes
UT’s measurements are being made at distribution voltages; no information has been provided on the signal processing algorithms used
Without additional information or context, it is difficult to draw conclusions from these data
Technical analysis is planned (enabled by RTDMS) to determine the significance of these measurements for the reliable operation TX’s high voltage transmission system
UT Austin’s efforts to date demonstrate the ease by which new technologies are enabling information previously available only to grid operators is becoming available to wider audiences – this trend cannot be reversed
ERCOT recognizes this trend and plans to be pro-active in assessing the value these efforts may offer for improving the operation of the grid

## Slide 15: Contacts and Follow Up
ERCOT |  | 
John Adams | jadams@ercot.com | 512.694.3364
CCET |  | 
Milt Holloway | mholloway@electrictechnologycenter.com | 512.472.3800
NASPI |  | 
Alison Silverstein | alisonsilverstein@mac.com | 512.670.3497
Jimmy Glotfelty | JGlotfelty@icfi.com | 713.445.2002
Stan Johnson | stan.johnson@nerc.net | 609.524.7012
DOE |  | 
Phil Overholt | Philip.Overholt@hq.doe.gov | 202.586.8110
CERTS |  | 
Joe Eto | jheto@lbl.gov | 510.486.7284
Carl Imhoff | carl.imhoff@pnl.gov | 509.375.4328
Manu Parashar | parashar@electricpowergroup.com | 626.685.2015
  http://www.naspi.org/

## Slide 16
BACKUP SLIDES

## Slide 17: What is the State of Art in Use of Phasor Technology?
NASPI
Successor to EIPP and covers all of North America
TVA hosting phasor data hub for Eastern Interconnection; transitioning to a NERC-funded activity
Over 80 PMUs networked in the East
RTDMS server installed at TVA; over 60 RTDMS users across the Eastern Interconnection
Developing, with DOE support, NASPInet data architecture for a fully distributed phasor data network
Addressing data sharing issues - NERC and FERC
CAISO
Started from concept and research in 2002, moved phasor system to control room in 2007
Over 50 PMUs from around WECC sending data to CAISO
RTDMS server installed at CAISO and networked with 14 users
Bonneville Power Administration
Pioneer in use of phasor technology since mid-90’s
RTDMS implemented at BPA
Research collaboration with CERTS and universities
Western Electric Coordinating Council
Well-established model validation and post disturbance analysis procedures based on utilization of phasor data
International
China, Brazil, Europe (UCTE), India all actively engaged in phasor technology

## Slide 18: Starter Phasor Monitoring System (SPMS) – Accomplishments to Date
American Electric Power (AEP)
AEP enabled 3 SEL 421 Relays within AEP Texas with PMU capability
SEL 421 Relays sending data in real-time to AEP PDC at Columbus, Ohio
AEP PDC supports IEEE C37.118 format
AEP PDC is sending AEP Texas data via VPN to ERCOT
ERCOT
RTDMS server installed at ERCOT
Data transmittal in real-time to RTDMS server at ERCOT
CERTS - Electric Power Group
Installed RTDMS server software at ERCOT
Provided RTDMS client software and training to ERCOT
Issues to be Resolved in Texas
Data Sharing – Nondisclosure Agreement

## Slide 19
2009
2008
2010+
Proposed Phasor Technology Planning
Roadmap for ERCOT
2010+
Past Accomplishments (Completed)
Future Activities
Establish Starter Phasor Monitoring System
(SPMS) utilizing existing infrastructure:
Integrate existing 3 AEP PMUs.
Leverage AEP PDC at Columbus
for time-synchronization
Establish VPN link between AEP & ERCOT
Real-Time
Monitoring
Offline
Analysis
Planned (In Progress)
INFRASTRUCTURE
PLATFORM
APPLICATIONS
Expand ERCOT Phasor Network:
Install PDC at ERCOT
Integrate additional PMUs from AEP, Oncor,
Centerpoint (others).
- Resolve data quality issues.
Install Real Time Dynamics Monitoring
System (RTDMS) at ERCOT:
RTDMS Server installed at ERCOT Taylor facility.
RTDMS Visualization Clients accessible at
ERCOT Taylor and Austin facilities over Citrix.
- Archive Phasor data in Database
(30 day historical archive)
Capture & permanently store event files
(5 minutes of pre-event & post-event data)
Install Phasor-Grid Dynamics Analyzer (PGDA)
offline analysis tool.
Implement intelligent alarming on:
Angular separation.
Oscillations.
Transient events.
Benchmark planning studies using
measurement data.
Perform event analysis using PMU data.
Identify and baseline ERCOT oscillatory
modes & damping.
Establish alarming limits and triggering
thresholds.
Migrate to production
grade hardware.
Define operator
actions.
- Prototype advanced
stability
applications.
Establish
‘Best Practices’ for:
Event Analysis
Model Validation

## Slide 20: Phasor Technology Utilization in Texas -- Vision
Starter System
  Utilize existing infrastructure
Expanded Coverage
  Incorporate additional PMUs at Texas utilities
Objective: Reliable, Fully-Integrated, Production Quality Systems
  Migration to production hardware with redundancy (example: CAISO)
Data Compilation & Clean Up
  Establish system/protocols for data archiving
Event Tagging
  Incorporate event detection, tagging & file management processes
Analysis Tools
  Include phasor-based offline analysis into planning practices
Phasor Data Acquisition
Real Time
Archived Data

## Slide 21: Texas Phasor Project -- Building Blocks & Roles and Responsibilities
Org. | Building Block | Activities
NASPI/ DOE/ CERTS | Technical Knowledge and Knowledge Transfer | Provide technical know-how and expertise Work with CCET, ERCOT, and Texas utilities on phasor project roadmap Provide assistance with phasor network architecture, deployment, connectivity, applications Facilitate deployment of RTDMS phasor applications currently in use in other interconnections
ERCOT | Test Bed, Technology Adoption and Integration with Operations for Wide-Area Applications | Assign lead engineer/project manager for ERCOT phasor technology initiative Deploy phasor applications and PDC in test bed environment Build knowledge base among ERCOT planners, engineers, and operators Migrate technology to operating environment and integrate with operations Scale-up – expanded coverage, PDC
Utilities | Infrastructure Deployment and Data Communications | Deploy phasor measurement units – new or existing relay-based Network PMUs and transmit data Expand coverage with PMUs Install PDCs Develop local networks and applications – RAS, dynamics, state estimation
CCET | Coordination & Research Management | Coordinate Texas phasor research and phasor implementation plan Obtain funding commitments from DOE, ETF, ERCOT, utilities
Universities | Research Future Workforce Development | Leading edge research on application of phasor technology Target Areas Equipment Placement State Estimation Equipment Monitoring, e.g., PSS
  RAS
  Dynamic Ratings
  Global Voltage Monitoring and
  Local Control