| OGRR Number | 219 | OGRR Title | Time Error Correction |  |
| --- | --- | --- | --- | --- |
| Timeline | Urgent | Recommended Action |  | Approval |
| Date of Decision |  | February 9, 2009 |  |  |
| Guide Section Requiring Revision |  | 1.5, Conformance to NERC Policies, Procedures, and Reliability Standards |  |  |
| Proposed Effective Date |  | April 1, 2009 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) removes the requirement that ERCOT perform time error corrections for accumulated time errors exceeding five (5) seconds. |  |  |
| Overall Market Benefit |  | This OGRR reduces the need for time error correction and could possibly eliminate the need to perform time error correction as a North American Electric Reliability Corporation (NERC) Reliability Standard. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | No impact is anticipated. However, data gathered from this field trial is needed to determine that the end consumer is not affected by removing the time error correction and to prove that system reliability is not compromised. |  |  |
| Procedural History |  | - On 2/4/09, OGRR219 and the Impact Analysis were posted. - On 2/6/09, OGRR219 was granted Urgent status via e-mail vote. - On 2/9/09, OWG considered OGRR219. |  |  |
| OWG Decision |  | On 2/9/09, OWG was in consensus to recommend approval of OGRR219 as submitted. |  |  |
| Summary of OWG Discussion |  | On 2/9/09, there were questions regarding the need for Urgent status. ERCOT provided the reason for requesting Urgent status. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 | Eliminating the time error corrections should have no adverse affect on the consumer or Market Participants. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None identified. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | None identified. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | Eliminating time error corrections will reduce the need for Market Participants to operate and perform differently (not 60Hz) in an effort to rectify a time error that was accumulated in the past. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | ERCOT is in a unique situation to participate in the field trial and facilitate the NERC BACSDT in removing time error correction as a reliability standard. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

| Original Sponsor |  |
| --- | --- |
| Name | Ken McIntyre |
| Company | ERCOT |
| Market Segment | Not applicable. |

Comments

Background Information:

The NERC BACSDT is conducting the field trial to gather enough information and support for eliminating the Standard BAL-004, Time Error Correction of the Reliability Standards for the Bulk Electric Systems of North America.  The NERC BACSDT does not believe that performing time error corrections support or are required for reliability.  Performing time error corrections can force a system closer to its frequency limits and can be detrimental to frequency performance and event recovery.

ERCOT Interconnect is in a unique situation of having ERCOT ISO as the single Balancing Authority and as the Reliability Coordinator (Interconnect Time Monitor).  ERCOT having only Direct Current (DC) interconnections is not faced with the complicated issues of Inadvertent flows with other Balancing Authorities.  Therefore ERCOT, in comparison to the Eastern or Western Interconnects, would be able to concentrate and isolate any effects of not performing time error corrections and therefore would be best suited to perform the field trial.  ERCOT will record frequency performance and log industry issues that arise.  ERCOT will also continue to monitor time error and if issues arise, ERCOT, as the Interconnect Time Monitor, can quickly schedule and perform a time error correction as needed.

Proposed Guide Language Revision

- 1.5 Conformance to NERC Policies, Procedures, and Reliability Standards

The Electric Reliability Council of Texas (ERCOT) Operating Guides are for the purpose of outlining specific practices for the ERCOT System.  These practices are consistent with the North American Electric Reliability Corporation (NERC) Operating Policies and standards.  For application in ERCOT, some NERC Policies must be adapted to fit the unique characteristics of the ERCOT System. Specific necessary adaptations are listed below:

| NERC Policy | ERCOT Adaptation |
| --- | --- |
| Time and Frequency Control | Sustained frequency deviations from 60 Hz result in time error. |
| Time Error Monitoring | ERCOT will monitor accumulated time error and initiate time corrections. The instantaneous time error is available to all ERCOT Qualified Scheduling Entities (QSEs) on the ERCOT website. When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction. The correction will be ended when the error is less than ±0.5 seconds. The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction. . |
| Time Error Correction | When a time correction is necessary, ERCOT will adjust scheduled frequency in the following manner. ERCOT will arrange for more or less Resources. Information to be passed along will include the correction frequency (59.98 Hz for fast and 60.02 Hz for slow) and the start time. A time correction may be terminated after five (5) hours, after any hour without a one-half (0.5) second error reduction. The Control Area Authority (CAA) will provide adequate notice of ending the time correction. |
| Inadvertent Interchange Management | The only Inadvertent Energy will be between ERCOT and Southwest Power Pool (SPP) and/or Comision Federal de Electricidad (CFE). Accounting / payback will be handled according to NERC policy. The hourly difference between a Control Area’s actual net interchange and a Control Area’s scheduled net interchange is classified as inadvertent energy. All inadvertent energy is placed in an Inadvertent Payback Account to be paid back in kind. |
| Control Surveys | Not all of the surveys defined by NERC apply to a system the size of ERCOT and /or a single Control Area interconnection such as ERCOT. |
| Load Shedding and System Restoration | Automatic firm Load shedding will be initiated as follows: Frequency % Load Relief 59.3 Hz 5% 58.9 Hz 10% 58.5 Hz 10% Load shedding will be widely dispersed in each Transmission Distribution Service Provider (TDSP), with no preference to Load Serving Entities (LSEs), and will be accomplished by using high-speed under-frequency relays. The frequency measuring relays shall have a time delay of no more than thirty (30) cycles (or one-half (0.5) seconds for relays that do not count cycles). If the frequency and time values are reached, an irretrievable trip is initiated. Total time from the time when frequency first reaches one of the values specified above to the time Load is interrupted should be no more than forty (40) cycles, including all relay and breaker operating times. Under-frequency relays may be installed on Transmission Facilities under the direction of ERCOT, provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay. Load restoration will be under the direction of the ERCOT CAA. A TDSP may by mutual agreement, with the approval of the Technical Advisory Committee (TAC), arrange to have all or part of its automatic Load shedding obligation carried by another TDSP. ERCOT will be notified and provided with the details of any such arrangement prior to implementation. |
| Information Exchange – Disturbance Reporting | ERCOT will record the following data from the ERCOT System for frequency deviations of .175 Hz or greater and will use this information to generate the ERCOT initial Disturbance Report: - ERCOT and individual QSE control biases. - Net MW Capability (including any capability lost) at the time of the disturbance. - Net System Load (MW) for the hour ending closest to the time of the disturbance. - Scheduled Net Interchange (MW) at the time of the disturbance. - Amount of interruptible load (MW) tripped. - Reference: Protocol Section 6.10.5.4, Responsive Reserve Services Deployment Performance Monitoring Criteria (In Part) …For all frequency deviations exceeding 0.175 Hz, ERCOT shall measure and record each two (2) second scan rate values of real power output for each QSE Resource providing Responsive Reserve Service. ERCOT shall measure and record the MW data beginning one (1) minute prior to the start of the frequency excursion event or Manual / Dispatch Instruction until ten (10) minutes after the start of the frequency excursion event or Manual / Dispatch Instruction… |
| Reliability Criteria | ERCOT operating reserve requirements are more restrictive than the concepts in the NERC Operating Manual. The ERCOT Responsive Reserve Obligation is a minimum of 2300 MW. |