## Questionnaire
| ERCOT Station ID | Question Explanation | WGR1 | WGR2 | WGR3 | WGR4 | WGR5 | WGR6 | WGR7 | WGR8 | WGR9 | WGR10 | WGR11 | WGR12 | WGR13 | WGR14 | WGR15 | WGR16 | WGR17 | WGR18 | WGR19 | WGR20 | WGR21 | WGR22 | WGR23 | WGR24 | WGR25 | WGR26 | WGR27 | WGR28 | WGR29 | WGR30 | WGR31 | WGR32 | WGR33 | WGR34 | WGR35 | WGR36 | WGR37 | WGR38 | WGR39 | WGR40 | WGR41 | WGR42 | WGR43 | WGR44 | WGR45 | WGR46 | WGR47 | WGR48 | WGR49
| Turbine Manufacturer | Make and Model | SIEMENS | GAMESA | SIEMENS | MITSUBISHI | VESTAS | GENERAL ELECTRIC | SIEMENS | Mitsubishi 1000A | Mitsubishi 1000A | GE 1.5S | GE 1.5S | GE 1.5 SE | GE 1.5 SLE | Mitsubishi | GE 1.5 SLE | Mitsubishi | Siemens | Siemens | Mitsubishi NWT 1000A | GE 1.5 | 88 Gamesa 383s + 12 Gamesa 1287s) | Gamesa G 87 | 42 Vestas V47s + 4 Vestas V66s | Siemens SWT-2.3-93 | Clipper Liberty C-96 | GE 1.5 SLE? | ? | ? | GE 1.5 | Vestas V47 | Vestas V47 | Vestas V47 | Zond 750 | Bonus 1.3 | Bonus 1.3 | Bonus 1.3 | Bonus 1.3 | Micon 750 | KVS 33 | GE 1.5 | GE 1.5 | Siemens 2.3 | GE 1.5 | Siemens 2.3 | GE 1.5 | Siemens 2.3 | GE 1.5 | GE 1.5 | GE 1.5
1 | Name of farm |  | WGR1 | WGR2 | WGR3 | WGR4 | WGR5 | WGR6 | WGR7 | WGR8 | WGR9 | WGR10 | WGR11 | WGR12 | WGR13 | WGR14 | WGR15 | WGR16 | WGR17 | WGR18 | WGR19 | WGR20 | WGR21 | WGR22 | WGR24 | WGR25 | WGR26 | WGR27 | WGR28 | WGR29 | WGR30 | WGR31 | WGR32 | WGR33 | WGR34 | WGR35 | WGR36 | WGR37 | WGR38 | WGR39 | WGR40 | WGR41 | WGR42 | WGR43 | WGR44 | WGR45 | WGR46 | WGR47 | WGR48 | WGR49 | WGR50
2 | TDSP |  | Oncor | Oncor | Oncor | Oncor | AEP Texas North Company | AEP Texas North Company | AEP Texas North Company | Oncor | Oncor | AEP | AEP | LCRA | LCRA | LCRA | LCRA | LCRA | LCRA | LCRA | LCRA | Oncor | Oncor | Oncor | Oncor | AEP TEXAS NORTH COMPANY | Oncor | Oncor | Oncor | Oncor | BRAZOS ELECTRIC CORP | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | RIO GRANDE ELECTRIC CO-OP (TDSP) | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | AEP TEXAS NORTH COMPANY | TAYLOR ELECTRIC CO-OP (TDSP) | TAYLOR ELECTRIC CO-OP (TDSP) | AEP TEXAS NORTH COMPANY | LCRA TRANSMISSION SERVICES CORP | LCRA TRANSMISSION SERVICES CORP | LCRA TRANSMISSION SERVICES CORP | LCRA TRANSMISSION SERVICES CORP | BRAZOS ELECTRIC CORP
3 | QSE
4 | Point of Interconnection (POI) - Station
5 | Miles of transmission line between POI and Project substation breaker | Miles of transmission (69/138/345KV) between the Project substation breaker and the Point of interconnection | 6 miles | 6.2 miles | 10 miles | 5 miles | 12 miles 138KV | 12 miles 138KV | 12 miles 138KV | 28 miles | 28 miles | 2.5 miles 138 kv | 6.3 miles 138 kv | None | None | None | None | 20 miles | 20 miles | 20 miles | <1 mile | 3 miles | None | 0 Miles | None. Directly under the trans line | 20.23 miles 69KV | 5.5 Miles | 7 miles 138 kV | 8 miles and 138 kV | 8 miles and 138 kV | 15 Miles | < 1.0 | 11 | 5 | N/A | 6 | 6 | 4 | 8 | 4 | na | < 1 | <1 | 13.5 | 20.3 | <1 | 7.5 to Substation | 8.25 to Substation | 13 to substation | 2 | 5.3
6 | Total Number of turbines / Capacity of each turbine / Total MW capacity of the wind farm |  | 54 turbines 2.3MW each 24.2MW total | 45 turbines 2MW each 90MW total | 55 turbines 2.3MW each 126.5MW total | 209 turbines 1MW each 209MW total | 67 turbines 1.8MW each 120.6MW total | 155 turbines 1.5MW each 232.5MW total | 74 turbines 2.3MW each 170.2MW total | 99 turbines 1MW each 99MW total | 61 turbines 1MW each 61MW total | 56 turbines 1.5 MW each 84 MW total | 51 turbines 1.5 MW each 76.5 MW total | 25 turbines 1.5 MW each 37.5 MW total | 61 turbines 1.5 MW each 91.5 MW total | 16 turbines 1 MW each 16 MW total | 90 turbines 1.5 MW each 135 MW total | 119 turbines 1 MW each 119 MW total | 46 turbines 2.3 MW each 105.8 MW total | 35 turbines 2.3 MW each 80.5 MW total | 80 turbines 1 MW each 80 MW total | 100 turbines 1.5 MW each 150 MW total | 100 turbines 2 MW each 200 MW total | 100 turbines 2 MW each 200 MW total | 42 Turbines / 0.66MW each / 27.72 MW total 4turbines / 1.65MW each / 6.6 MW total | 26 turbines 2.3 MW each 59.8 MW total | 24 turbines 2.5 MW each 60 MW total | 80 turbines 1.5MW each 120MW total | 87 Turbines 1.5MW each 130.5 MW Total | 80 Turbines 1.5MW each 120 MW Total | 56 turbines 84 MW | 125 turbines 82.5 MW | 242 turbines 159.72 MW |  | 38 turbines 28.5 MW | 61 turbines 79.3 MW | 61 turbines 79.3 MW | 31 turbines 40.3 MW | 61 turbines 79.3 MW | 107 turbines 80.25 MW | 110 turbines 39.60 MW | 76 turbines 114.0 MW | 142 turbines 213.0 MW | 279 turbines 522.5 MW |  |  | 334 turbines 550.0 MW |  |  | 75 turbines 112.5 MW | 75 Turbines 112.5 MW
7 | Facility's response to balancing energy instructions | Does ERCOT call the plant directly or does it go through QSE? Is the curtailment achieved by feathering blades or turning off turbines etc… Done through SCADA remotely? | QSE calls and a follow up email | QSE calls | QSE calls | QSE calls | Verbal instructions from QSE to control room | Verbal instructions from QSE to control room | Verbal instructions from QSE to control room | QSE calls operator. Operator stops units. 25 turbines at a time (one circuit at a time) | QSE calls operator. Operator stops units. 25 turbines at a time (one circuit at a time) | ERCOT communicates with QSE. Set point entered manually by QSE into Wind Farm Management System (WFMS). Curtailment is controlled by blade pitch. System control is very good. Curtailment ramp rate is 6 MW/Min | ERCOT communicates with QSE. Set point entered manually by QSE into Wind Farm Management System (WFMS). Curtailment is controlled by blade pitch. System control is very good. Curtailment ramp rate is 6 MW/Min | QSE Contacts Operator. Operator calls CC in NY to bring it to MWs requested | QSE -> Operator -> Enters number into SCADA. Blades feather out / pitch out. Feather out till idle | QSE ->Operator -> Enters number into GH (Garrat Hassan) SCADA for Max MWs | QSE -> Operarator -> Enters number into SCADA. Blades feather out / pitch out. Feather out till idle. Which ever QSE gets instruction contacts Operator | QSE ->Operator-> Enters number into GH (Garrat Hassan) SCADA for Max MWs | QSE -> Operator -> Enters number into GH (Garrat Hassan) SCADA for Max MWs | QSE -> Operator -> Enters number into GH (Garrat Hassan) SCADA for Max MWs | ERCOT phone call or electronic to QSE, QSE to Mission, Call Site or cell phone/backup/ 2nd backup. Login remote SCADA & use auto control function to adj High and Low MW value, SCADA turns off turbines. If SCADA down, site manager goes to site and opens br | KW setpoint is entered into WFMS (Wind Farm Management System) remotely by GE-CSC. Turbine blades are feathered to spill wind energy. | ERCOT -> QSE -> APX -> Control Center. APX has ability to enter curtailment set-points via internet. If unable to perform this, contacts CC. CC issues a set point either feather blades upto 30% then shut down turbines | ERCOT will contact APX, our 24-hour call center for curtailments, to perform them. APX has the ability to enter curtailment set-points via internet. If APX is unable to perform them, they have a list of contacts from Operator who can respond | QSE calls and instructs and plant handles deployments | ERCOT call QSE. WGR and QSE have agreed that QSE 24/7 realtime desk controls MW output from their control desk by sending signal to alter output to desired level. QSE send conformation by fax to WW. If / When QSE unable to control, calls WGR 24/7 number and WGR staff would respond / attempt to manually change setpoint | ERCOT -> APX -> Operations Center, implemented remotely through SCADA | QSE calls SCADA center and they use the WFMS to lower the output of the facility | QSE calls SCADA center at and they use the WFMS to lower the output of the facility | QSE calls SCADA center at and they use the WFMS to lower the output of the facility | See attached diagram.Currently in process of changing to automated curtailment. | 1. Control Center receives name and energy schedule for the curtailed resource from the site QSE. 2. Control Center enters the energy schedule into the resource park pilot. 3. Control Center enters the energy schedule in the resource wind forecaster. 4. Control Center creates a log entry containing the resource, original generation, final generation, and wind speed. | 1. Control Center receives name and energy schedule for the curtailed resource from the site QSE. 2. Control Center enters the energy schedule into the resource park pilot. 3. Control Center enters the energy schedule in the resource wind forecaster. 4. Control Center creates a log entry containing the resource, original generation, final generation, and wind speed. | 1. Control Center receives name and energy schedule for the curtailed resource from the site QSE. 2. Control Center enters the energy schedule into the resource park pilot. 3. Control Center enters the energy schedule in the resource wind forecaster. 4. Control Center creates a log entry containing the resource, original generation, final generation, and wind speed. | 1. Control Center receives name and energy schedule for the curtailed resource from the site QSE. 2. Control Center enters the energy schedule into the resource park pilot. 3. Control Center enters the energy schedule in the resource wind forecaster. 4. Control Center creates a log entry containing the resource, original generation, final generation, and wind speed. | 1. Control Center receives name and energy schedule for the curtailed resource from the site QSE. 2. Control Center enters the energy schedule into the resource park pilot. 3. Control Center enters the energy schedule in the resource wind forecaster. 4. Control Center creates a log entry containing the resource, original generation, final generation, and wind speed. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | 1. Control Center receives name and energy schedule for the curtailed resource from the site QSE. 2. Control Center enters the energy schedule into the resource park pilot. 3. Control Center enters the energy schedule in the resource wind forecaster. 4. Control Center creates a log entry containing the resource, original generation, final generation, and wind speed. | 1. Control Center receives name and energy schedule for the curtailed resource from the site QSE. 2. Control Center enters the energy schedule into the resource park pilot. 3. Control Center enters the energy schedule in the resource wind forecaster. 4. Control Center creates a log entry containing the resource, original generation, final generation, and wind speed. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment. | See attached diagram. Currently in process of changing to automated curtailment.
8 | Transmission injection voltage at POI | Base voltage at Point of Interconnection | 138kV | 138kV | 345kV | 345kV | 138KV | 138KV | 138KV | 138KV | 138KV | 138 KV | 138 KV | 345 kv | 345 kv | 345 kv | 345 kv | 345 kv | 345 kv | 345 kv | 345kv | 138KV | 345KV | 345KV | 69KV | 69KV | 138KV | 138 kV | 138KV | 138KV | 138kV | 138kV | 138kV | 138kV | 34.5kV | 138kV | 138kV | 138kV | 138kV | 138kV | 34.5kV | 138kV | 138kV | 138kV | 138kV | 138kV | 345kV | 345kV | 345kV | 345kV | 138kV
9 | How many circuit miles of transmission line are on your side of the generator breaker? Also give the voltage (345/138/69 kV)? | Miles of transmission (69/138/345KV) between the project substation breaker and the feeders | N/A | N/A | 10 - miles 345kV | 5 - miles 345kV | 8miles 138KV | 8miles 138KV | 8miles 138KV | ? | ? | None | None | 6.6 miles 34.5 kv underground | 10.25 miles of 138 kv overhead | 10.25 miles of 138 kv overhead. | 14 miles of 138kv over head | None | None | None. Goes straight from GSU into the feeder breakers | < 1mile | 0miles of trans line 7 miles of collection system 25 miles of underground cables | None | 8 Miles of 138kv | Approx 8 to 10 miles of 24.9 KV feeder lines from low side of station to the groups of turbines | None - Generator breaker located mid project all 34.5kV distrubtion via undground cable. | None | 0 miles | 0 miles | 0 miles | 15 Miles | 0 Miles | 6.5 Miles | 7.6 Miles | 0 Miles | 2 Miles | 5.1 Miles | 10.8 Miles | 5.8 Miles | 2.8 Miles | 0 Miles | 0 Miles | 0.3 Miles | 13.5 Miles | 20.4 Miles | 0.1 Miles | 0 Miles | 0 Miles | 0 Miles | 4 Miles
10 | Is your control room “On-Site” or “Remote” from your wind farm? |  | Remote | Remote | On Site-day Remote - night | On Site-day Remote - night | Remote | Remote | Remote | Onsite - Office hours Remote - Rest of the time Phone forwarded to Staff | Onsite - Office hours Remote - Rest of the time Phone forwarded to Staff | 24X7 - GE Schenectady,NY On-Site 7:00 AM - 6:00 PM | 24X7 - GE Schenectady,NY On-Site 7:00 AM - 6:00 PM | remote 24X7 Onsite during office hours | remote 24X7 Onsite during office hours | remote 24X7 Onsite during office hours | remote 24X7 Onsite during office hours | remote 24X7 Onsite during office hours | remote 24X7 Onsite during office hours | remote 24X7 onsite during office hours | Onsite | Both. GE- CSC located in Schenectady, NY | We are on-site, but we can access the SCADA as well as the substation HMI remotely. In addition, APX’s 24-hour desk is located remotely | We are on-site, but we can access the SCADA as well as the substation HMI remotely. In addition, APX’s 24-hour desk is located remotely(California) APX functions - Start/Stop Turbines - Curtailments - Voltage support - Remotely open any breaker | Remote: 24X7 Onsite: Mon-Fri 0700 - 1530 | Wind farm is monitored from both site and off site locations. Control room is virtual and not in one fixed location Day to day MW control is normally handed by QSE at real time desk, non-operation emergency or other is handled by own staff on call | Remote (Primary) in Houston TX On-site office hours operations | On-Site during day and Remote for off hours | On-Site | On-Site | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote | Remote
11 | Is your control room staffed 24 X 7? If not explain how off hour request are completed. List all 24 X 7 phone number(s) in order of preference.
12 | To request a change in your voltage set point, does the TSP contact you directly or are you requiring them to go through your QSE? |  | Contact directly | Contact directly | Contact directly | Contact directly | Contact directly | Contact directly | Contact directly | Contacts directly. No voltage control. Have to shut down turbines. Plant is set to unit pf to be sure pf remains above 0.95 | Contacts directly. No voltage control. Have to shut down turbines. Plant is set to unit pf to be sure pf remains above 0.95 | Contacts CSC directly. This can be changed to allow either the TSP or QSE to enter voltage set point directly | Contacts CSC directly. This can be changed to allow either the TSP or QSE to enter voltage set point directly | No voltage capabilities for the 25 turbines. No WFMS or caps | TSP contacts Operator directly | TSP contacts Operator directly. | TSP contacts Operator directly | TSP contacts Operator directly | TSP contacts Operator directly | TSP contacts Operator directly | Directly (Hasn’t happened yet) | TSP contacts GE-CSC directly | TDSP contacts the QSE representative which is APX | TDSP goes through the QSE representative which is APX | NA - Runs at 0.98pf most times | Contact directly right now. If the gird conditions changed and this became regular would look at having programmed into QSE desk for quicker response | Go through QSE | Directly | Directly | Directly | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center | Contact site directly and if they need assistance they will coordinate with Control center
13 | How long does it take to make a voltage set point change when requested by the TSP or QSE? | What steps are invloved in changing the voltage set point after receiving an instruction from TSP? | >2kV 5 minutes Up to 1 1/2 hrs for changes on the GSU taps | >2kV 5 minutes Up to 1 1/2 hrs for changes on the GSU taps | >2kV 5 minutes Up to 1 for changes on the GSU taps | 1 hr for voltage changes Remote SCADA in 2 months | Less than 30 Mins | Less than 30 Mins | Less than 30 Mins | we can shut off turbines thus raising the voltage right away | we can shut off turbines thus raising the voltage right away | < 1min. Typically close to 15 sec, The set point is changed remotely by the GE CSC as requested by TSP.. Response is near immediate | < 1min. Typically close to 15 sec, The set point is changed remotely by the GE CSC as requested by TSP.. Response is near immediate | 20 mins through other plants | 20 mins | 20 min | 20 min | 20 min | 20 min | 20 min | Don’t have ability to make voltage set point change. Can connect caps | GE-CSC executes setpoint changes via WFMS. <1min after instruction is received. | APX can respond within 2-3 minutes. We can respond within 3-4 minutes | APX can respond within 2-3 minutes. We can respond within 3-4 minutes | NA | 15 Minutes for skilled enginner. - Issues found with Voltage cotrol unit hardware. Prototype unit will be hardware upgraded with latest working version expected early 09 Once upgraded and main voltage control is full auto mode and stable then will be controlled via operator by simply enetering PU setpoint with anticiapated reponce time of 1 to 5 minutes | ?? | within 15 min | within 15 min | within 15 min | How long should the operator wait before calling again? Who should be called? | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds | 5-10 seconds
14 | At what locations does your staff monitor voltage. Low side of GSU, High Side of GSU, Point of interconnect, etc? | [5 empty] | Low and Highside of GSU at both substations | Low and Highside of GSU at both substations | Low and Highside of GSU at both substations | Through SCADA, low side, high side and interconnection voltage | Through SCADA, low side, high side and interconnection voltage | Both sides of the substation transformers. Voltage set point is referenced to the highside of Bus 1 substation transformer (138 kv) | Both sides of substation transformers. Voltage set point is referenced to the high side of Bus 2 substation transformer (138 KV). | High & low side of GSU & turbine. In this farm highside of GSU effectively same as interconnection point | High & low side of GSU & turbine. In this farm highside of GSU effectively same as interconnection point | High & low side of GSU & turbine. In this farm highside of GSU effectively same as interconnection point | High & low side of GSU & turbine. In this farm highside of GSU effectively same as interconnection point | High & low side of GSU & turbine. In this farm highside of GSU effectively same as interconnection point | High & low side of GSU & turbine. In this farm highside of GSU effectively same as interconnection point | High & low side of GSU & turbine. In this farm highside of GSU effectively same as interconnection point | capacity control relay monitors 34.5kv side | Voltage is monitored on both sides of GSU 34.5 & 138 kv @ Project substation | POI 345KV | POI 345KV | High side of transformer at substation 69KV | High side of GSU for auto VC lowside GSU (WTG terminals) for temp-auto (temporary) | Both lowside and Highside of GSU. | High side of the GSU | High side of the GSU | High side of the GSU | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection | PI Tags are located at the Point of Interconnection
15 | Please explain how your Automatic Voltage Control works. (Control system with generator set point, capacitor /reactor switching, LTC tap change, etc.) Indicate if SCADA is used in any of the methods. |  | AVR @ termial of the generator & Park Pilot system monitoring the 34.5kV (medium) bus for larger steps | AVR @ termial of the generator & Park Pilot system monitoring the 34.5kV (medium) bus for larger steps | AVR @ termial of the generator & Park Pilot system monitoring the 34.5kV (medium) bus for larger steps | Inductive motor 600V LTC set to 34.5kV | Utilizes a combination of LTC on the main GSU abd switched shunt caps on the turbines and in the subs 34.5kv bus. This system normally operates on a pf schedule | Utilizes (+/-)0.95 dynamic pf control of GE turbines coordinated with automatic switching of 34.5kv shunt caps on low side of GSU. Noramlly operates on voltage regulation schedule | Utilizes (+/-)0.90 dynamic pf control of siemens turbines and is planned to operate on pf schedule | Relays and meters control cap switching based on voltage and var flows. LTC is automatic | Relays and meters control cap switching based on voltage and var flows. LTC is automatic | AVC is accomplished through the GE SCADA Wind Farm Management System (WFMS) by sending a pf control signal to each turbine based on difference between set point and POI voltage. The turbines respond based upon reactive capability of +/- 726 KVAR,(+/- .90 pf at generator terminals) per turbine | AVC is accomplished through the GE SCADA Wind Farm Management System (WFMS) by sending a pf control signal to each turbine based on difference between set point and POI voltage. The turbines respond based upon reactive capability of +/- 726 KVAR,(+/- .90 pf at generator terminals) per turbine | No voltage capabilities for the 25 turbines. No WFMS or caps. Use other units for voltage control. Also there is a LTC on the GSU. Takes input from low side of GSU. No SCADA control | WFMS sends a control signal to all turbines can be set to PF or voltage control made. TSP asks to lower or raise 2kv. All done through SCADA, can be done both Operator, NY (GE) | No voltage capability. Use other unit capability of voltage control. TSP asks to lower or raise 2kv. All done through SCADA, can be done both Operator, NY (GE) | WFMS sends a control signal to all turbines can be set to PF or voltage control made. TSP asks to lower or raise 2kv. All done through SCADA, can be done both Operator, NY (GE) | GSUs has LTC automatically controlled through backward system. Works in a % of nominal voltage. Doesn’t have PF control | GSUs LTC automatically controlled through backward system. Works in a % of nominal voltage. Doesn’t have PF control | GSU has a LTC is locally controlled there using the nominal voltage from the PTs at 34.5 Also through GH SCADA in increments of 1% upto 10% either way | Automatic swithcing of caps based on Power factor, could manually operate within 20 mins. Switch to voltage control would require GE assistance & some time | AVC is accomplished through the GE SCADA Wind Farm Management System (WFMS) by sending a control signal to each turbine. The turbines respond based upon their output level up to +/- 726KVAR. VAR output would be limited if turbine padmount voltage exceeds | Automatic HTC tap change and automatic VC capacitors. Monitor 345KV and puts caps on and off | Automatic HTC tap change and automatic VC capacitors. Monitor 345KV and puts caps on and off | Automatic voltage control is capacitor banks mounted in the controller of each turbine and controlled by the software Makes a decision in 1 sec and puts the caps in to maintain 0.98pf | Siemens Advanced park pilot system – varies voltage using convertor based technology at each individual WTG. The advanced park pilot is a secondary independent scada system which is linked and access through the regular WTG scada system | No AVC. Manual tap and cap switching | Control system with voltage set point - uses SCADA | Control system with voltage set point - uses SCADA | Control system with voltage set point - uses SCADA | GE Wind Farm Management System Monitors the Voltage and Current at the Scurry Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | No Dynamic Voltage Control at the Point of Interconnect. | No Dynamic Voltage Control at the Point of Interconnect. | No Dynamic Voltage Control at the Point of Interconnect. | LCRA owns the substation | No Dynamic Voltage Control at the Point of Interconnect. | No Dynamic Voltage Control at the Point of Interconnect. | No Dynamic Voltage Control at the Point of Interconnect. | No Dynamic Voltage Control at the Point of Interconnect. | No Dynamic Voltage Control at the Point of Interconnect. | LCRA owns the substation | GE Wind Farm Management System Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | GE Wind Farm Management System Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | Siemens Wind Park Supervisor Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | GE Wind Farm Management System Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | Siemens Wind Park Supervisor Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | GE Wind Farm Management System Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | Siemens Wind Park Supervisor Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | GE Wind Farm Management System Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | GE Wind Farm Management System Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters. | GE Wind Farm Management System Monitors the Voltage and Current at the Substation and makes setpoint adjustments via comm link to the turbine controllers. The TCU send power commands to the converters.
16 | On your AVR, Where is the input voltage for control measured. |  | At the lowside of the GSU 34.5kV (medium) bus | At the lowside of the GSU 34.5kV (medium) bus | 345kV bus | 34.5kV (medium) bus | Low side of transformer - 34.5kv | Low side of transformer - 34.5kv | Low side of transformer - 34.5kv | High side bus. Vars measured on lowside | High side bus. Vars measured on lowside | Highside of Bus 1 substation transformer (138kv) | Highside of Bus 2 substation transformer (138kv) | PT is on low side of GSU | CCVT on highside of GSU | CCVT on highside of GSU | CCVT on highside of GSU | Lowside of GSU 34.5 kv bus | Lowside of GSU 34.5 kv bus | Lowside of GSU 34.5 kv bus | capacity control relay monitors 34.5kv side | Project substation 138kV bus | POI 345KV | POI 345KV | at the turbine - 690kv | Currently at each generator 690V terminal . This will however change to high side of GSU breaker. | NA | High side of the GSU | High side of the GSU | High side of the GSU | High Side of GSU | Capacitor Banks which switch in and out to control voltage |  |  | LCRA owns the substation | Capacitor Banks which switch in and out to control voltage | Capacitor Banks which switch in and out to control voltage | Capacitor Banks which switch in and out to control voltage | Capacitor Banks which switch in and out to control voltage | Capacitor Banks which switch in and out to control voltage | LCRA owns the substation | At the substation | At the substation | At the substation | At the substation | At the substation | At the substation | At the substation | At the substation | At the substation | At the substation
17 | With generator breaker closed and zero MW output (little or no wind) what are your MVAR capability (both in consuming and in injecting MVARs into the transmission system)? | What is the amount of MVAr injection/consumption (uncontrolled) from the grid during No-wind / 0MW output from the plant | 10 MVAR reactive | 2 MVAR reactive | 20 MVAR capacitive | 40 MVAR capacitive | Later | Later | Later | No reactor banks. So 5-10 MVAr injection | No reactor banks. So 5-10 MVAr injection | 2.1 MVAR lag uncontrollable, (injection) | 1.9 MVAR lag uncontrollable, (injection) | 2.42 MVAr exporting | 0.506 MVAR exporting | 0.506 MVAR exporting | 0.670 MVAR export | 0.1 MVAR export | 0.1 MVAR export | 0.1 MVAR export | ~ 5 MVARs | 0 Lead, 4 Lag(static) | 10 MVAR into the system with no production No consuming capability with out generation | 10 MVAR into the system with no production No consuming capability with out generation Normally set to PF control for unity AVR only works when machines running | With little or no wind, there are no generator breakers closed. There are no turbines generating - Need to answer this again. Incorrect interpretation of term 'Generator Breaker' | Will depend if each WTG is still conencted or not. Likely to be connected even if no generation - If all are not connected then See numbers in email. | Provide later | Constant, but we can control the size of the cap banks | Constant, but we can control the size of the cap banks | Constant, but we can control the size of the cap banks | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information.
18 | Do you understand your responsibility in meeting .95 PF requirements? Explain your understanding of this requirement. | ERCOT's expectation : Each generator (wind farm) must have the capability to control within -0.95 to +0.95 pf of the unit maximum MW capacity at the POI | Less than 4 MW generaotrs may not be able to maintain .95 PF | Less than 2 MW generaotrs may not be able to maintain .95 PF | Less than 4 MW generaotrs may not be able to maintain .95 PF | Less than 4 MW generaotrs may not be able to maintain .95 PF | Our understanding is that we are required to have the capability to meet the 0.95 requirement on a total project basis for the 3 projects combined since we have one interconnection point and one EPS meter for the combined projects. | Our understanding is that we are required to have the capability to meet the 0.95 requirement on a total project basis for the 3 projects combined since we have one interconnection point and one EPS meter for the combined projects. | Our understanding is that we are required to have the capability to meet the 0.95 requirement on a total project basis for the 3 projects combined since we have one interconnection point and one EPS meter for the combined projects. | Generation resources are required to control voltages within normal operating ranges between 0.95 leading and 0.95 lagging power factor range measured at the high side of the main transformer | Generation resources are required to control voltages within normal operating ranges between 0.95 leading and 0.95 lagging power factor range measured at the high side of the main transformer | This is not the case as required in our Interconnect Agreements. Note: WGR is capable of +/- .95 at POI throughout most of the load range (slightly less lagging, injection, at full load). This is a "V" curve as opposed to a "D" curve typical of conventional synchronous generators. A "D" curve is simply not possible with current technology. WGR was constructed in 2001 and is compliant with current protocol. | This is not the case as required in our Interconnect Agreements. Note: WGR is capable of +/- .95 at POI throughout most of the load range (slightly less lagging, injection, at full load). This is a "V" curve as opposed to a "D" curve typical of conventional synchronous generators. A "D" curve is simply not possible with current technology. WGR was constructed in 2001 and is compliant with current protocol. | No voltage capability on its own. But when winds are blowing we should be able to move within the +/- 0.95 range using other plants | When winds are blowing we should be able to move within the +/- 0.95 range | When winds are blowing we should be able to move within the +/- 0.95 range | When winds are blowing we should be able to move within the +/- 0.95 range | When winds are blowing we should be able to move within the +/- 0.95 range | When winds are blowing we should be able to move within the +/- 0.95 range | When winds are blowing we should be able to move within the +/- 0.95 range | Based on current ERCOT legal interpretation issued 11/13/08, technical support is evaluating our capabilities. | Provides voltage support up to +/- .95 pf when requested by TDSP. TDSP controls voltage schedule for the WGR Interconnection. WGR is exempt from protocol since site was constructed prior to Feb. 17, 2004. | Yes, the wind farm is required to maintain our power factor within the band of .95leading to .95 lagging during normal operations or, at the request of ERCOT through our QSE, maintain a specific set point within this band to support the current grid conditions. When the grid condition requiring a specific set point no longer exists, the wind farm will be returned to our normal operating range by ERCOT through the QSE | Yes, the wind farm is required to maintain our power factor within the band of .95leading to .95 lagging during normal operations or, at the request of ERCOT through our QSE, maintain a specific set point within this band to support the current grid conditions.When the grid condition requiring a specific set point no longer exists, the wind farm will be returned to our normal operating range by ERCOT through the QSE | ? | Yes, Protocal is open to interption, our intererpartion is: Wind farm must have the capability to control within -0.95 to +0.95 pf (of the unit current output MW at the POI) | Provide later | Per protocol 6.5.7.1 and 6.7.6, we are required to meet leading/lagging .95PF at the point of interconnection - | Per protocol 6.5.7.1 and 6.7.6, we are required to meet leading/lagging .95PF at the point of interconnection - | Per protocol 6.5.7.1 and 6.7.6, we are required to meet leading/lagging .95PF at the point of interconnection - | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols | Comply with Interconnection Agreement requirements and ERCOT Protocols
19 | What MW output is required before you start meeting the .95 PF requirements? |  | Less than 4 MW generaotrs may not be able to maintain .95 PF | Less than 2 MW generaotrs may not be able to maintain .95 PF | Less than 4 MW generaotrs may not be able to maintain .95 PF | Less than 4 MW generaotrs may not be able to maintain .95 PF | 1MW | 1MW | 1MW | 25% of rated cap Equals 24.75 MWs | 25% of rated cap Equals 15.25 MWs | As long as the MW > 0, able to provide reactive support. WGR is capable of +/- .95 at POI throughout most of the load range (slightly less lagging, injection, at full load). This is a "V" curve as opposed to a "D" curve typical of conventional synchronous generators. See attached POI Reactive Capability Curves. | As long as the MW > 0, able to provide reactive support. WGR is capable of +/- .95 at POI throughout most of the load range (slightly less lagging, injection, at full load). This is a "V" curve as opposed to a "D" curve typical of conventional synchronous generators. See attached POI Reactive Capability Curves. | do not know right now | do not know right now | do not know right now | do not know right now | do not know right now | do not know right now | do not know right now | NA | 1MW | We will be able to meet the .95 laging requirement regardless of MW output due to the installed capacitance in our substations. To meet the full .95 leading requirement the wind farm will have to be at approximately 25MW of output, however, we would be able to meet lesser leading requirements at lower outputs | We will be able to meet the .95 laging requirement regardless of MW output due to the installed capacitance in our substations. To meet the full .95 leading requirement the wind farm will have to be at approximately 25MW of output, however, we would be able to meet lesser leading requirements at lower outputs | ? | Net 0 MW at POI (if WTG connected should meet requriemnts at Gross 0.01MW) | Provide later | Once the turbine can achieve power output, we can achieve the .95 PF | Once the turbine can achieve power output, we can achieve the .95 PF | Once the turbine can achieve power output, we can achieve the .95 PF | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols. | Has not been asked to perform specific studies to measure this requirement. In the process of developing criteria for a study which will provide this information. Sites are built to comply with Interconnection Agreement requirements and ERCOT Protocols.
20 | Does your facility include capacitor banks and or reactors? |  | No | Yes | Yes | Yes | Yes | Yes | No | Caps | Caps | No | No | No | No caps or reactors | No | No | Cap banks | No | No | Yes | No | Yes.Caps | Yes.Caps | Caps banks in turbines only | YES Capcaitor | 2Caps X11 MVArs = 22MVArs | Yes cap banks | Yes cap banks | Yes cap banks | Capacitor Bank at the Substation | Capacitor Bank at the Substation | None | None | N/A | Capacitor Bank at the Substation | Capacitor Bank at the Substation | Capacitor Bank at the Substation | Capacitor Bank at the Substation | Capacitor Bank at the Substation | N/A | Capacitor Bank at the Substation | No Capacitor Bank at the Substation | Capacitor Bank at the Substation | Capacitor Bank at the Substation | Capacitor Bank at the Substation | Capacitor Bank at the Substation | None | None | None
21 | If your facility includes capacitor banks or reactors please explain how they are controlled. Are they automatic, SCADA controlled or manual. Are they available for voltage control when there are zero MWs? List size of each capacitor bank and reactor. | How many banks and what sizes? | N/A | 3 - 10 MVAR capacitors (30 MVAR) Automatic and/or Manual | 1 - 8 MVAR capacitors (8 MVAR) Automatic and/or Manual | 8 - 17.5 MVAR capacitors (140 MVAR) Automatic set to maintain 34.5kv or Manual | 6 X 10.8 = 64.8 MVAr Uses PLC Logic to control caps | 2 banks 6 X 7.2 86.4 MVAr total Integrated with GE supervisory system | None | 2 X 9 MVArs controlled by SEL 734 meter | 4 X 4.5 MVArs controlled by SEL 451 relay that measure VAR flow and voltages | None installed | None installed | NA | NA | NA | NA | 3X22 = 66MVAR 3 stages per bank | NA | NA | 45 MVAR caps available Automatic PF control could be changed with few days notice | No reactor or capacitor banks. | 2 X 6 = 12 caps Automatic, but also can be controlled remotely Max of 4 caps in each bank can be closed remotely at one time 10MVAr X 12 = 120 MVAr | 2 X 6 = 12 caps Automatic, but also can be controlled remotely Max of 4 caps in each bank can be closed remotely at one time 10MVAr X 12 = 120 MVAr | Cap banks are automaticly controlled by the turbine software, and are active only when turbine is generating. Each turbine has a capacitor bank of 18 12.5 KVAR capacitors or 225 KVAR | In field / local manual operation or as part of automated voltage contorl system. No SCADA control can not be operated remotely. 4 banks of 2.6MVAR. Due to possible tranisent harmonics identified in final asbuilt harmoic study, cap banks are currnetly off line, WTG currently meeting day to day requirement. Additional filters have been ordered expected installaion around 16 wks time. | Manual | yes we have 4 capacitor banks and they are manually controlled on site via the control building at the sub station Each is 7.8 MVAR | yes we have 8 capacitor banks and they are manually controlled on site via the control building at the sub station Each is 7.8 MVAR | yes we have 8 capacitor banks and they are manually controlled on site via the control building at the sub station Each is 7.8 MVAR | Automatic and manual mode only / not SCADA controlled. | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | No Capacitor Bank at the Substation | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW | Automatic control and have voltage control but are not available with zero MW
22 | When your facility was energized, did you have an agreement with the local TSP to provide a portion of your voltage support requirements? | If you are not able to meet the 0.95 PF requirement, did your TSP agree to provide this support for you? | No | No | No | No | No | No | No | No | No | The agreement states we would provide reactive capability as per our turbine design but no requirement was included to require +/- .95 pf. The turbines at WGR modulate pf +/- .9 . There has been no request from TSP to provide reactive devices. I am unaware of any agreement requiring the TSP to provide voltage support. | The agreement states we would provide reactive capability as per our turbine design but no requirement was included to require +/- .95 pf. The turbines at WGR modulate pf +/- .9 . There has been no request from TSP to provide reactive devices. I am unaware of any agreement requiring the TSP to provide voltage support. | No | No | None | No | No | No |  | No | No | No | No | Deffered for later | NA / No | Yes. Provide more info later | We are not aware of any agreement | We are not aware of any agreement | We are not aware of any agreement | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No
23 | Do your individual turbines control voltage? If so how is this control implemented (voltage control, power factor control, etc) |  | Yes, At the lowside of the GSU 34.5kV (medium) bus | No, Induction Generator | Yes, At the lowside of the GSU 34.5kV (medium) bus | No, Induction Generator | No | Yes. pf control | Yes. Voltage control | Yes. Internal Caps on turbines switch in and oout to control voltage | Yes. Internal Caps on turbines switch in and oout to control voltage | Yes. Individual turbines control voltage automatically as required to meet setpoint on high side of substation transformers (Modulating power factor set point from SCADA WFMS to each turbine as required to meet voltage requirement) | Yes. Individual turbines control voltage automatically as required to meet setpoint on high side of substation transformers (Modulating power factor set point from SCADA WFMS to each turbine as required to meet voltage requirement) | No voltage control for turbines in this farm' | Yes. Through SCADA each turbine helps control | No | Yes. Through SCADA each turbine helps control | No | Yes using siemens voltage control system sends out control to each turbine |  | No. Except for automatic compensation internal to hold PF | Yes. Voltage control at the project level is done by supervision of the WFMS via instructions to each turbine to output “x” kVAR. That kVAR output would be up to it’s capability at load “y”. Otherwise, each turbine operates at unit pf if unsupervised by WFMS. | Yes the turbines can control voltage. Control is implemented using PF mode. To be determined whether it can be put on Voltage control | Yes the turbines can control voltage. Control is implemented using PF mode. To be determined whether it can be put on Voltage control | Our turbines only have capacitor banks that of course are for power factor | Yes- Voltage control - Note / FYI WTG can not be run in PF control due to GE paitent. | No | The Wind Farm Management Systems is used to control individual turbines based upon the total for the wind farm on an aggregate basis either in voltage control mode or power factor mode | The Wind Farm Management Systems is used to control individual turbines based upon the total for the wind farm on an aggregate basis either in voltage control mode or power factor mode | The Wind Farm Management Systems is used to control individual turbines based upon the total for the wind farm on an aggregate basis either in voltage control mode or power factor mode | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "GE1.5 SLE" Tab | Yes, Each turbine has capacitors that step in based on power factor. | Yes, Each turbine has capacitors that step in based on power factor. | Yes, Each turbine has capacitors that step in based on power factor. | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "Zond 750" Tab | Yes, Each turbine has capacitors that step in based on power factor. | Yes, Each turbine has capacitors that step in based on power factor. | Yes, Each turbine has capacitors that step in based on power factor. | Yes, Each turbine has capacitors that step in based on power factor. | Yes, Each turbine has capacitors that step in based on power factor. | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "KVS-33" Tab | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "GE1.5 SLE" Tab | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "GE1.5 SLE" Tab | Yes, The Siemens turbines have a power converter on the generator stator to control Power Output and Power Factor. | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "GE1.5 SLE" Tab | Yes, The Siemens turbines have a power converter on the generator stator to control Power Output and Power Factor. | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "GE1.5 SLE" Tab | Yes, The Siemens turbines have a power converter on the generator stator to control Power Output and Power Factor. | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "GE1.5 SLE" Tab | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "GE1.5 SLE" Tab | Yes, Each turbine has a Power Converter that switches the current to the Generator Rotor to control Power Output and Power Factor. Attached Diagram "GE1.5 SLE" Tab
24 | If individual turbines control voltage, what is the control point used to govern their reactive output. (voltage on gathering network, low side of transformer interconnection point, interconnection point) |  | N/A | N/A | N/A | N/A | N/A | Low side of substation bus | Low side of substation bus | N/A? | N/A? | The control point/process point is the voltage as measured on the high side of the substation transformer, (138 KV side/POI). SCADA WFMS sends a pf command to each individual turbine, based on the error between the set point and actual voltage. | The control point/process point is the voltage as measured on the high side of the substation transformer, (138 KV side/POI). SCADA WFMS sends a pf command to each individual turbine, based on the error between the set point and actual voltage. | NA | Voltage on gathering network, lowside of transformer at interconnection point and at interconnection point | NA | Voltage on gathering network, lowside of transformer at interconnection point and at interconnection point | NA | Voltage on gathering network, lowside of transformer at interconnection point and at interconnection point |  | NA | Supervisory control is through WFMS based upon the project substation 138kV bus voltage as compared to the voltage setpoint | Deffered for later | Deffered for later | NA | In temp-auto mode set point at WTG terminals In full auto mode set point at high side of GSU | NA | Monitoring the high side of POI and trying to meet voltage at the POI. Although the metering equipment is physically located on the High Side of the GSU, the software compensates for any line-drop. | Monitoring the high side of POI and trying to meet voltage at the POI. Although the metering equipment is physically located on the High Side of the GSU, the software compensates for any line-drop. | Monitoring the high side of POI and trying to meet voltage at the POI. Although the metering equipment is physically located on the High Side of the GSU, the software compensates for any line-drop. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine. | Voltage and current is measured on the low site of the padmount transformer in each turbine.
25 | Is your farm involved in a Special Protection Scheme (SPS)? Explain its operation. |  | Yes, Automatic Scheme reduces generation | Yes, Automatic Scheme reduces generation | No | No | No | No | Yes. Refer to Q25 in attachement | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes | No | Yes. Refer to question 25 in the attachement | Yes. Refer to question 25 in the attachement | Yes. Refer to question 25 in the attachement | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No
26 | Are there any temperature restrictions or operational restrictions that ERCOT might need to be aware of to better model or study operations of your facility for either Real or Reactive power production? | High / Low ambient temperature limits that can cause a sizeable portion of the farm to shutdown. | N/A | >104° turbine shuts down due to high temperaure | N/A | N/A | Later | 60+ C in cell (140 F) | 60+ C in cell (140 F) | Ambinet temp of 113 F | Ambinet temp of 113 F | No temperature limits. 110% over-voltage on turbine padmount transformers/generator terminals, (could occur in lagging operation when grid voltage is well below set point). | No temperature limits. 110% over-voltage on turbine padmount transformers/generator terminals, (could occur in lagging operation when grid voltage is well below set point). | 25 m/sec for 10 min average > 28 m/sec instantaneous ambient -30 C or 50 C within the cell Icing in the hub | 25 m/sec for 10 min average > 28 m/sec instantaneous ambient -30 C or 50 C within the cell Icing in the hub | Yaw motor time out or anamometer out - Shut down -10 C for 2 secs, resets on -8 C 40 C for 2 sec, resets on 38 C 60 C for 10 sec inside cell Resets below 60 C for 30 sec 25 m/sec instantaneous | Yaw motor time out or anamometer out - Shut down -10 C for 2 secs, resets on -8 C 40 C for 2 sec, resets on 38 C 60 C for 10 sec inside cell Resets below 60 C for 30 sec 25 m/sec instantaneous | Yaw motor time out or anamometer out - Shut down -10 C for 2 secs, resets on -8 C 40 C for 2 sec, resets on 38 C 60 C for 10 sec inside cell Resets below 60 C for 30 sec 25 m/sec instantaneous | - 20 C / 45 C 28m/sec for 30 sec 32m/sec for 1 sec | - 20 C / 45 C 28m/sec for 30 sec 32m/sec for 1 sec | -10C for more than 2 secs 54C for more than 2secs | 110% over-voltage on turbine padmount transformers is limit for lagging operation when grid voltage is >141kV | Ambient temp of 103F 50mph for 10 min avg 65-70mph for 1 min avg resets at 45mph Icing events can lower production | Ambient temp of 103F 50mph for 10 min avg 65-70mph for 1 min avg resets at 45mph Icing events can lower production | offline at 109F | Yes – Above 40C(104F ambinet) the wind turbine may shut down for mechanical safety reasons. This is measured at each turbine and is controlled at each individual WTG. Low temp is -20deg c for components | None. Designed to operate at all temps | Cut-in wind speed at approximately 3 m/s Cut-out wind speed at approximately 25 m/s (sustained over 10 minute average) Cut-out wind speed at approximately 28 m/s (30 second average) Cut-out wind speed at approximately 30 m/s (3 second average) TUrbine will not restart until the wind speed drops below 22 m/s Cold temperature -15 C Hot temperature 40 C | Cut-in wind speed at approximately 3 m/s Cut-out wind speed at approximately 25 m/s (sustained over 10 minute average) Cut-out wind speed at approximately 28 m/s (30 second average) Cut-out wind speed at approximately 30 m/s (3 second average) TUrbine will not restart until the wind speed drops below 22 m/s Cold temperature -15 C Hot temperature 40 C | Cut-in wind speed at approximately 3 m/s Cut-out wind speed at approximately 25 m/s (sustained over 10 minute average) Cut-out wind speed at approximately 28 m/s (30 second average) Cut-out wind speed at approximately 30 m/s (3 second average) TUrbine will not restart until the wind speed drops below 22 m/s Cold temperature -15 C Hot temperature 40 C | Low Ambient Temp -30C High Winds 28 m/s | High Ambient Temp 40C Low Ambient Temp -20C High Winds 25 m/s | High Ambient Temp 40C Low Ambient Temp -20C High Winds 25 m/s | Currently gathering the data to answer this question | Currently gathering the data to answer this question | Currently gathering the data to answer this question | Currently gathering the data to answer this question | Currently gathering the data to answer this question | Currently gathering the data to answer this question | Low Ambient Temp -10C High Winds 30 m/s | Currently gathering the data to answer this question | Low Ambient Temp -30C High Winds 28 m/s | Low Ambient Temp -30C High Winds 28 m/s | High Ambient Temp 45C Low Ambient Temp -20C High Winds 28 m/s | Low Ambient Temp -30C High Winds 28 m/s | High Ambient Temp 45C Low Ambient Temp -20C High Winds 28 m/s | Low Ambient Temp -30C High Winds 28 m/s | High Ambient Temp 45C Low Ambient Temp -20C High Winds 28 m/s | Low Ambient Temp -30C High Winds 28 m/s | Low Ambient Temp -30C High Winds 28 m/s | Low Ambient Temp -30C High Winds 28 m/s
27 | What is you ability to ramp your wind generation into the system via staggering windmills on or controlling individual ramp rates via blade pitch, braking or some other method. | [5 empty] | Later | Pitch angle | Blade pitch system | Staggered command on the SCADA - 5MW / Min etc | Staggered command on the SCADA - 5MW / Min etc | Ramp Rates installed, 6 MW/min. Applicable to changes in curtailment instructions (not applicable to increases in wind speed) | Ramp Rates installed, 6 MW/min. Applicable to changes in curtailment instructions (not applicable to increases in wind speed) | Working with the SCADA personel. Should not be a problem | Working with the SCADA personel. Should not be a problem | Working with the SCADA personel. Should not be a problem | Working with the SCADA personel. Should not be a problem | Working with the SCADA personel. Should not be a problem | Working with the SCADA personel. Should not be a problem | Working with the SCADA personel. Should not be a problem | Uses Garrad Hassan SCADA which has an auto-control function, allowing us to ramp generation into and out of the system. | Has an overall ramp rate that is in effect during curtailment instructions. Accomplished by feathering turbine blades via WFMS supervisory instructions. | Capability exists Can set a 20MW/Min Combine blade feathering and turbines comning on and off | Capability exists Can set a 20MW/Min Combine blade feathering and turbines comning on and off | No pitch control - Ramprate control through staggering wind mills | Currently being investiagted. Believe should have around 10% per min waiting for feedback on practically to impliment / confirm not issue with SPS for up rate . - Note no down ramp rate can currently be offered due to incompatablity with SPS system | Yes. Staggering wind turbines | Our plants are configured to respond to an SPS, so our ramp rates are set to allow a quick reduction in output. The control system is not able to have multiple ramp rates to automatically control the output. The output of the farm can be manually controlled by the operations staff. | Our plants are configured to respond to an SPS, so our ramp rates are set to allow a quick reduction in output. The control system is not able to have multiple ramp rates to automatically control the output. The output of the farm can be manually controlled by the operations staff. | Our plants are configured to respond to an SPS, so our ramp rates are set to allow a quick reduction in output. The control system is not able to have multiple ramp rates to automatically control the output. The output of the farm can be manually controlled by the operations staff. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | TURBINES feather blades to curtail. We believe that they can follow a ramp, but they have not tested | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | TURBINES feather blades to curtail. We believe that they can follow a ramp, but they have not tested | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | TURBINES feather blades to curtail. We believe that they can follow a ramp, but they have not tested | Turbines shut down to curtail. There is no vendor installed ramping ability installed. | Turbines shut down to curtail. There is no vendor installed ramping ability installed.
28 | Discussion by the wind generator of the turbine/generator protection systems such as “high speed trip” and any other protection systems that cause a trip of the turbine so that we understood this better. At what wind speed does the turbine trip. Do all your turbines trip at the same wind speed? etc. | High wind speed limits Over/Under Voltage/Freq limits |  |  |  |  | Over/Under voltage and frequency (in the GARF) | Over/Under voltage and frequency (in the GARF) | Over/Under voltage and frequency (in the GARF) | Over speed tripping / rotor over speed / high shaft speed - 2095 rpm 25 m/sec for 10 mins or 30 m/sec instantaneous Over voltage trip - 120% of primary or secondary | Over speed tripping / rotor over speed / high shaft speed - 2095 rpm 25 m/sec for 10 mins or 30 m/sec instantaneous Over voltage trip - 120% of primary or secondary | 56 mph (10 minute average) or gusts to 60 MPH. Offline for 30 sec and if wind goes down it will switch back. Most I have seen is 5% of capacity. Low voltage of 70% for more than 1min and 65% instantaneous. Frequency < 59 HZ or > 61 HZ. | 56 mph (10 minute average) or gusts to 60 MPH. Offline for 30 sec and if wind goes down it will switch back. Most I have seen is 5% of capacity. Low voltage of 70% for more than 1min and 65% instantaneous. Frequency < 59 HZ or > 61 HZ. | [7 empty] | inst 30m/sec for >2sec 10 min avg > 25m/sec >61hz for more than 0.3sec <29hz for more than 0.3sec | High wind speed cutoff is 56mph. Undervoltage trip is at 30% of nominal voltage for 6 cycles then trip. |  |  | 25 m/s - 10 min avg turbulent wind extreme hot/cold over/under voltage +/- 0.90 grid voltage 59.5 & 60.5 frequency | Cut in wind speed 4 m/s Cut out wind speed 25m/s Temperature Operational range -20DegC to 40DegC Substation Settings Freq: 57.5Hz instantaneous 58 Hz for 2.08s 58.4 Hz for 30.2s 59.4 Hz for 540.3s 60.6 Hz for 540.3s 62.5 Hz instantaneous WTG Settings U/O Volts/Freq see email. Also note the WTGs have activated LVRT | 25m/s |  |  |  | Grid Voltage Drop: 0.30pu for 0.1 sec Under Voltage: 0.74pu for 1.1 sec Over Voltage: 1.11pu for 1.2 secs Grid Spike: 1.20pu for 0.1 sec Low Freq: 57.3Hz for 1.0 sec High Freq : 61.8Hz for 1.0 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3.5 m/s See Fault List on "GE 1.5 SLE" Tab | Under Voltage: 0.85pu for 0.4 sec Over Voltage: 1.13pu for 0.2 secs Low Freq: 57.0Hz for 0.2 sec High Freq : 61.92Hz for 0.2 sec Gen Overspeed: 106% High Wind Speed: 25 m/s for 30 sec Start Wind Speed: 4.5 m/s See Fault List on "Vestas V47" Tab | Under Voltage: 0.85pu for 0.4 sec Over Voltage: 1.13pu for 0.2 secs Low Freq: 57.0Hz for 0.2 sec High Freq : 61.92Hz for 0.2 sec Gen Overspeed: 106% High Wind Speed: 25 m/s for 30 sec Start Wind Speed: 4.5 m/s See Fault List on "Vestas V47" Tab | Under Voltage: 0.85pu for 0.4 sec Over Voltage: 1.13pu for 0.2 secs Low Freq: 57.0Hz for 0.2 sec High Freq : 61.92Hz for 0.2 sec Gen Overspeed: 106% High Wind Speed: 25 m/s for 30 sec Start Wind Speed: 4.5 m/s See Fault List on "Vestas V47" Tab | Under Voltage: 0.92pu Over Voltage: 1.05pu Low Freq: 59Hz for 0.2 sec High Freq : 61Hz for 0.2 sec Gen Overspeed: 110% High Wind Speed: 30 m/s Start Wind Speed: 4 m/s See Fault List on "Zond 750" Tab | Grid Voltage Drop: 0.80pu for 0.2 sec Under Voltage: 0.90pu for 60 secs Over Voltage: 1.06pu for 60 secs Grid Spike: 1.09pu for 0.2 sec Low Freq: 57Hz for 0.2 sec High Freq : 61Hz for 0.2 sec Gen Overspeed: 106% for 0.4 ses High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3 m/s Cutout reverse power: -100kW See Fault List on "Bonus 1.3" Tab | Grid Voltage Drop: 0.80pu for 0.2 sec Under Voltage: 0.90pu for 60 secs Over Voltage: 1.06pu for 60 secs Grid Spike: 1.09pu for 0.2 sec Low Freq: 57Hz for 0.2 sec High Freq : 61Hz for 0.2 sec Gen Overspeed: 106% for 0.4 ses High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3 m/s Cutout reverse power: -100kW See Fault List on "Bonus 1.3" Tab | Grid Voltage Drop: 0.80pu for 0.2 sec Under Voltage: 0.90pu for 60 secs Over Voltage: 1.06pu for 60 secs Grid Spike: 1.09pu for 0.2 sec Low Freq: 57Hz for 0.2 sec High Freq : 61Hz for 0.2 sec Gen Overspeed: 106% for 0.4 ses High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3 m/s Cutout reverse power: -100kW See Fault List on "Bonus 1.3" Tab | Grid Voltage Drop: 0.80pu for 0.2 sec Under Voltage: 0.90pu for 60 secs Over Voltage: 1.06pu for 60 secs Grid Spike: 1.09pu for 0.2 sec Low Freq: 57Hz for 0.2 sec High Freq : 61Hz for 0.2 sec Gen Overspeed: 106% for 0.4 ses High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3 m/s Cutout reverse power: -100kW See Fault List on "Bonus 1.3" Tab | Grid Voltage Drop: 0.76pu for 0.1 sec Under Voltage: 0.80pu for 60 secs Over Voltage: 1.04pu for 60 secs Grid Spike: 1.07pu for 0.1 sec Low Freq: 57Hz for 0.2 sec High Freq : 61Hz for 0.2 sec Gen Overspeed: 105% & 110% High Wind Speed: 30 m/s for 30 sec Start Wind Speed: 3 m/s Cutout reverse power: -100kW See Fault List on "Micon 750" Tab | Under Voltage: 0.80pu for 60 sec Over Voltage: 1.04pu for 60 secs Grid Spike: 1.07pu for 0.1 sec Low Freq: 57Hz for 0.2 secs High Freq : 61Hz for 0.2 sec Gen Overspeed: 105% & 110% High Wind Speed: 30 m/s for 30 sec Start Wind Speed: 3 m/s Cutout reverse power: -100kW See Fault List on "KVS-33" Tab | Grid Voltage Drop: 0.30pu for 0.1 sec Under Voltage: 0.74pu for 1.1 sec Over Voltage: 1.11pu for 1.2 secs Grid Spike: 1.20pu for 0.1 sec Low Freq: 57.3Hz for 1.0 sec High Freq : 61.8Hz for 1.0 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3.5 m/s See Fault List on "GE 1.5 SLE" Tab | Grid Voltage Drop: 0.30pu for 0.1 sec Under Voltage: 0.74pu for 1.1 sec Over Voltage: 1.11pu for 1.2 secs Grid Spike: 1.20pu for 0.1 sec Low Freq: 57.3Hz for 1.0 sec High Freq : 61.8Hz for 1.0 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3.5 m/s See Fault List on "GE 1.5 SLE" Tab | Grid Voltage Drop: 0.40pu for 0.1 sec Under Voltage: 0.9pu for 3.0 sec Over Voltage: 1.10pu for 1.0 secs Grid Spike: 1.20pu for 0.2 sec Low Freq: 57Hz for 0.2 sec High Freq : 62Hz for 0.2 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3 m/s See Fault List on "Siemens 2.3" Tab | Grid Voltage Drop: 0.30pu for 0.1 sec Under Voltage: 0.74pu for 1.1 sec Over Voltage: 1.11pu for 1.2 secs Grid Spike: 1.20pu for 0.1 sec Low Freq: 57.3Hz for 1.0 sec High Freq : 61.8Hz for 1.0 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3.5 m/s See Fault List on "GE 1.5 SLE" Tab | Grid Voltage Drop: 0.40pu for 0.1 sec Under Voltage: 0.9pu for 3.0 sec Over Voltage: 1.10pu for 1.0 secs Grid Spike: 1.20pu for 0.2 sec Low Freq: 57Hz for 0.2 sec High Freq : 62Hz for 0.2 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3 m/s See Fault List on "Siemens 2.3" Tab | Grid Voltage Drop: 0.30pu for 0.1 sec Under Voltage: 0.74pu for 1.1 sec Over Voltage: 1.11pu for 1.2 secs Grid Spike: 1.20pu for 0.1 sec Low Freq: 57.3Hz for 1.0 sec High Freq : 61.8Hz for 1.0 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3.5 m/s See Fault List on "GE 1.5 SLE" Tab | Grid Voltage Drop: 0.40pu for 0.1 sec Under Voltage: 0.9pu for 3.0 sec Over Voltage: 1.10pu for 1.0 secs Grid Spike: 1.20pu for 0.2 sec Low Freq: 57Hz for 0.2 sec High Freq : 62Hz for 0.2 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3 m/s See Fault List on "Siemens 2.3" Tab | Grid Voltage Drop: 0.30pu for 0.1 sec Under Voltage: 0.74pu for 1.1 sec Over Voltage: 1.11pu for 1.2 secs Grid Spike: 1.20pu for 0.1 sec Low Freq: 57.3Hz for 1.0 sec High Freq : 61.8Hz for 1.0 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3.5 m/s See Fault List on "GE 1.5 SLE" Tab | Grid Voltage Drop: 0.30pu for 0.1 sec Under Voltage: 0.74pu for 1.1 sec Over Voltage: 1.11pu for 1.2 secs Grid Spike: 1.20pu for 0.1 sec Low Freq: 57.3Hz for 1.0 sec High Freq : 61.8Hz for 1.0 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3.5 m/s See Fault List on "GE 1.5 SLE" Tab | Grid Voltage Drop: 0.30pu for 0.1 sec Under Voltage: 0.74pu for 1.1 sec Over Voltage: 1.11pu for 1.2 secs Grid Spike: 1.20pu for 0.1 sec Low Freq: 57.3Hz for 1.0 sec High Freq : 61.8Hz for 1.0 sec Gen Overspeed: 110% High Wind Speed: 28 m/s for 30 sec Start Wind Speed: 3.5 m/s See Fault List on "GE 1.5 SLE" Tab

## Sheet1
Do you follow a Voltage Profile or do you only change voltage when the TO ask you to change | No Controls to 141kV unless directed from TO | No Controls to 141kV unless directed from TO | No Controls to 355kV unless directed from TO | No Controls to 355kV unless directed from TO
ERCOT posted Voltage Profile on-peak (08-22) off-peak (23-07) | on-peak 143kV off-peak 144kV | on-peak 143kV off-peak 144kV | on-peak 357kV off-peak 350kV | on-peak 357kV off-peak 350kV

## Sheet2
| ERCOT Station ID | SGMNT | WEC | SWEC | CSEC | CSEC | FLTCK
| ERCOT Generation ID in MOI | SGMNT_SIGNALMT | WEC_WECG1 | SWEC_G1 | CSEC_CSECG1 | CSEC_CSECG2 | FLTCK_SSI
| ERCOT Generation ID in SCADA | SIGNALMT | WECG1 | G1 | CSECG1 | CSECG2 | SSI
ERCOT MOI QSE
Turbine Manufacturer
1 | Name of farm | TEXAS BIG SPRINGS | WHIRLWIND | STANTON WIND | CAMP SPRINGS | CAMP SPRINGS | SILVER STAR
2 | Name of interconnection TSP (who is interconnection agreement with)
3 | QSE
4 | Interconnection point (station)
5 | How many miles of transmission are on your side of the interconnection point?
6 | How may wind turbines are installed on your farm and what is the total installed capacity of your wind farm in MW.
7 | Please describe how your facility responds to balancing energy instructions. (energy dispatch instructions)
8 | What is the transmission injection voltage (345/138/69 kV)?
9 | How many circuit miles of transmission line are on your side of the generator breaker? Also give the voltage (345/138/69 kV)?
10 | Is your control room “On-Site” or “Remote” from your wind farm?
11 | Is your control room staffed 24 X 7? If not explain how off hour request are completed. List all 24 X 7 phone number(s) in order of preference.
12 | To request a change in your voltage set point, does the TSP contact you directly or are you requiring them to go through your QSE?
13 | How long does it take to make a voltage set point change when requested by the TSP or QSE?
14 | At what locations does your staff monitor voltage. Low side of GSU, High Side of GSU, Point of interconnect, etc?
15 | Please explain how your Automatic Voltage Control works. (Control system with generator set point, capacitor /reactor switching, LTC tap change, etc.) Indicate if SCADA is used in any of the methods.
16 | On your AVR, Where is the input voltage for control measured.
17 | With generator breaker closed and zero MW output (little or no wind) what are your MVAR capability (both in consuming and in injecting MVARs into the transmission system)?
18 | Do you understand your responsibility in meeting .95 PF requirements? Explain your understanding of this requirement.
19 | What MW output is required before you start meeting the .95 PF requirements?
20 | Does your facility include capacitor banks and or reactors?
21 | If your facility includes capacitor banks or reactors please explain how they are controlled. Are they automatic, SCADA controlled or manual. Are they available for voltage control when there are zero MWs? List size of each capacitor bank and reactor.
22 | When your facility was energized, did you have an agreement with the local TSP to provide a portion of your voltage support requirements?
23 | Do your individual turbines control voltage? If so how is this control implemented (voltage control, power factor control, etc)
24 | If individual turbines control voltage, what is the control point used to govern their reactive output. (voltage on gathering network, low side of transformer interconnection point, interconnection point)
25 | Is your farm involved in a Special Protection Scheme (SPS)? Explain its operation.
26 | Are there any temperature restrictions or operational restrictions that ERCOT might need to be aware of to better model or study operations of your facility for either Real or Reactive power production?
27 | What is you ability to ramp your wind generation into the system via staggering windmills on or controlling individual ramp rates via blade pitch, braking or some other method.
28 | Discussion by the wind generator of the turbine/generator protection systems such as “high speed trip” and any other protection systems that cause a trip of the turbine so that we understood this better. At what wind speed does the turbine trip. Do all your turbines trip at the same wind speed? etc.