## Slide 1: SAPS to Menard 138 kV line
TAC Meeting
March 5, 2009
Presented by Paul Hassink
AEPSC Texas Transmission Planning

## Slide 2: Isolation and Redirection
With over 6000 MW of simultaneous West Texas wind production available today, the overloads of the 138 kV and 69 kV lines east and south of Abilene and San Angelo have become routine
By separating wind generation from the 138 kV and 69 kV lines that cross the interface between West Texas and ERCOT load centers, power can be forced to flow on the 345 kV system
Additionally, Phase Shift Transformers can buck the power flow on 138 kV lines by increasing the power angle across the lines

## Slide 3: Isolation and Redirection
Phase Shift Transformers block power flow from weaker transmission systems
Split Busses in Substations Isolate Wind from Load and route wind to 345 kV system
345 kV Export Path
345 kV
Export
Path
Abilene
San Angelo
Big Lake

## Slide 4: Status of the SAPS to Menard 138 kV line
AEP performs surveys of a line, when it appears that the line will be exposed to extended periods of heavy loading.
  The SAPS to Menard 138 kV line was identified through interconnection studies to fit this criteria.
  As a result, the Light Detection and Ranging (LiDAR) survey was performed to enable improvement of the line's capacity, which in combination with other system upgrades, such as the Yellow Jacket Phase Shift Transformer (PST), should relieve constraints.
Field verification of the survey results were completed 2/26/09, resulting in determination of the new line rating on 2/27/09 and release of the SR to reduce the rating of the line the same day.
  Contrary to our expectation, analysis this past week of the line survey data and follow-up validation of the results demonstrated that the ground clearance of certain spans of the line were not sufficient.
  Since the new rating is limited by ground clearance of the line, it was necessary to open the line at this time.

## Slide 5: Status of the SAPS to Menard 138 kV line
Without the SAPS to Menard 138 kV line in-service, load in the Menard area is at risk of voltage collapse.
  AEP's intent is to maximize the capacity of the line in the time that is available before this summer.
Roughly 10% of the line's spans constrain the line's capacity below the original 151/170 MVA rating.
  Work is commencing to secure materials and perform engineering to raise the offending spans.
  With only two and one-half months before load levels in the Menard area could peak, not all offending spans can be raised before this summer.
AEP is discussing options with ERCOT to reconfigure the transmission system in the area during off peak periods to mitigate constraints.
  Solutions that take advantage of the diversity between wind energy availability and customer peak demand are being pursued.