ERCOT Operations Report

March 2009 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 3/1/2009 19:10 | 59.862 | 58 | Unit trip with 405 MW online |
| 3/8/2009 8:02 | 60.11 | 425 | SCE change +1100 in 10 mins, out of DRS |
| 3/9/2009 22:39 | 59.89 | 2 | Unit trip with 360 MW online |
| 3/10/2009 23:51 | 59.898 | 18 | SCE change -1200 in 8 mins |
| 3/13/2009 10:02 | 59.898 | 16 | Unit trip with 112 MW online and slow unit response |
| 3/18/2009 7:14 | 59.823 | 168 | Unit trip with 765 MW online |
| 3/20/2009 0:04 | 60.105 | 176 | SCE change +900 in 5 mins |
| 3/22/2009 1:05 | 60.101 | 132 | Offset was calculated to compensate for the loss of 600 MW SCE, but SCE recovered on its own |
| 3/26/2009 7:55 | 59.87 | 19 | Unit trip with 561 MW |
| 3/27/2009 9:54 | 59.856 | 34 | Unit trip with 451 MW |
| 3/29/2009 19:40 | 59.83 | 115 | Unit trip with 618 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 3/01 19:10:42 | 3/01 19:21:22 | 0:10:40 | 570.25 |  |
| 3/09 08:11:52 | 3/09 08:25:10 | 0:13:18 | 364.32 | Unit Trip (557 MW) |
| 3/09 13:42:24 | 3/09 13:51:36 | 0:09:12 | 337.94 | Unit Trip (288 MW) |
| 3/09 22:39:04 | 3/09 22:54:12 | 0:15:08 | 422.41 |  |
| 3/10 23:43:16 | 3/11 00:12:44 | 0:29:28 | 401.28 |  |
| 3/11 15:38:24 | 3/11 15:59:00 | 0:20:36 | 353.77 | Unit Trip (360 MW) |
| 3/13 10:02:48 | 3/13 10:24:13 | 0:21:25 | 401.28 |  |
| 3/17 21:59:56 | 3/17 22:23:30 | 0:23:34 | 332.34 | SCE change -1200 MW in 5 min |
| 3/18 07:14:02 | 3/18 07:30:54 | 0:16:52 | 855.37 |  |
| 3/20 23:58:31 | 3/21 00:12:51 | 0:14:20 | 327.36 | SCE change -700 MW in 5 min |
| 3/26 07:55:05 | 3/26 08:12:07 | 0:17:02 | 528.01 |  |
| 3/26 22:04:06 | 3/26 22:22:32 | 0:18:26 | 343.21 | SCE change -1180 MW in 9 min |
| 3/27 09:54:53 | 3/27 10:23:57 | 0:29:04 | 601.93 |  |
| 3/29 19:40:48 | 3/29 19:57:51 | 0:17:03 | 739.20 |  |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | Total |
| --- | --- | --- | --- | --- | --- |
| W RIO | 96 | 0 | 0 | 0 | 96 |
| North | 33 | 0 | 4 | 4 | 37 |
| Austin | 26 | 0 | 1 | 1 | 27 |
| Laredo | 0 | 9 | 5 | 14 | 14 |
| DFW | 5 | 1 | 6 | 7 | 12 |
| Western | 0 | 1 | 9 | 10 | 10 |
| San Antonio | 0 | 0 | 10 | 10 | 10 |
| Bryan Area | 7 | 0 | 0 | 0 | 7 |
| Houston | 2 | 0 | 3 | 3 | 5 |
| Corpus | 2 | 0 | 0 | 0 | 2 |
| South | 0 | 2 | 0 | 2 | 2 |
| Northeast | 0 | 0 | 2 | 2 | 2 |
| E RIO | 0 | 1 | 0 | 1 | 1 |
|  | 171 | 14 | 40 | 54 | 225 |

| Historical Totals | Mar-09 | Mar-08 | Feb-09 |
| --- | --- | --- | --- |
| Austin | 26 | 10 | 6 |
| Bryan Area | 7 | 7 | 0 |
| Corpus | 2 | 2 | 0 |
| DFW | 6 | 6 | 43 |
| E RIO | 1 | 19 | 3 |
| Houston | 2 | 7 | 11 |
| Laredo | 9 | 59 | 6 |
| North | 33 | 4 | 17 |
| Northeast | 0 | 10 | 5 |
| San Antonio | 0 | 2 | 1 |
| South | 2 | 0 | 1 |
| W RIO | 96 | 0 | 93 |
| Western | 1 | 60 | 8 |
| Total | 185 | 186 | 194 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Comanche Peak SES - Decordova SES & Wolf Hollow - Rocky Creek 345KV | Concord 345/138KV autotransformer | 30 |
| Aspermont - Spur 138KV | Jayton - Spur 69 kV | 21 |
| Santa Anna - Ballinger 138KV | Ballinger - Humble 69KV | 16 |
| Abilene South - Eskota Switch 138KV | Eskota Switch 138/69KV autotransformer | 12 |
| Ballinger - San Angelo Red Creek 138KV | Miles - Rowena 69KV | 11 |
| Jack County - Reno 138KV | Rhome - Decatur Tap 138KV | 10 |
| Baytown Energy Center - Chambers 345KV | Baytown Energy Center 345/138KV Autotransformer AT2 | 8 |
| Aspermont - Spur 138KV | Matador - Paducah 69KV | 7 |
| Dilley Switch - North Laredo 138KV | North Laredo - Asherton 138KV | 6 |
| Roanoke Switch - West Denton and Lewisville Switch 345KV | West Denton - Airport 138KV | 6 |
| STP - Hillje and STP - White Point 345KV | Blessing - Lolita 138KV | 6 |
| Lon Hill - Coleto Creek 345KV | Victoria - Warburton 138KV | 5 |
| Oasis - PH Robinson 345KV | Garrott - Midtown 138KV | 5 |
| Austrop - Lost Pines 345KV | Winchester - Fayetteville 138KV | 4 |
| Austrop - Sandow Switch 345kV | Sandow Switch - Elgin Switch 138KV | 3 |
| Baytown Energy Center 345/138KV Autotransformer AT2 | Baytown Energy Center 345/138KV Autotransformer AT1. | 3 |
| Golden Switch - Bluff Creek 138KV | Sun Switch - Sacroc 138KV | 3 |
| San Angelo Red Creek - Ballinger 138KV | Ballinger - Miles 69KV | 3 |
| Austrop 345/138KV autotransformer #2 | Austrop 345/138KV autotransformer #1 | 2 |
| Decatur - Wise County 138KV | Bowie TMPP 138/69KV autotransformer | 2 |
| Dilley Switch - San Miguel 138KV | Derby - Pearsall 69KV | 2 |
| Graham - Long Creek 345KV | Paint Creek - Murray 138KV | 2 |
| Graham - Long Creek 345KV | Putnam 138/69KV autotransformer | 2 |
| Greenbelt - Comanche 138KV | Heights - Texas City Water Treat Sub 69KV | 2 |
| Jack County - Reno 138KV | Agnes Switch - Weatherford Switch 138KV | 2 |
| Royse Switch - Farmersville 345KV | Royse Switch - Farmersville 345KV | 2 |
| Wichita Falls South Switch - Patton Street - Lone Star 138KV | Bowie 138/69KV autotransformer | 2 |
| Abilene South - Eskota 138KV | Trent - Merkel 69KV | 1 |
| Angleton - West Columbia 138KV | West Columbia 138/69KV Auto | 1 |
| Austrop - Sandow 345KV | Elgin Switch - Butler 138KV | 1 |
| Basecase | Jayton CSW - Spur 69KV | 1 |
| Bosque Switch - Whitney 138KV | Lake Whitney - Whitney 138KV | 1 |
| Coleto 345/138KV auto T1 | Coleto - Victoria 138KV | 1 |
| Dyann - South Lane City 138KV | Brazos Valley - Fort Bend 138KV | 1 |
| Eagle Mountain - Roanoke Switch - Parker Switch 345KV | West Denton - Roanoke Switch 345KV | 1 |
| Falcon Switch - Zapata 138KV | North Laredo Switch - Asherton 138KV | 1 |
| Ferguson - Gillespie 138KV | Lake way - Marshall Ford 138KV | 1 |
| Gibbons Creek - Obrien and Singleton - TH Wharton 345KV | Campwood - Rock Springs 69KV | 1 |
| Graham - Long Creek 345KV | Cisco - Putnam 69KV | 1 |
| Graham - Long Creek 345KV | Putnam - Abilene South 138KV | 1 |
| Graham SES - Long Creek Switching Station and Cook Field Road Switching Station 345KV | Albany - Hubbard BSTR 2 69KV | 1 |
| Jack County - Reno 138KV | Decatur Tap - Decatur 138KV | 1 |
| Jewett - Singleton and Gibbons Creek - Singleton 345KV | Sutton - Tabor 69KV | 1 |
| Kendall 345/138KV Autotransformer | Raymond F Barker - Comfort 138KV | 1 |
| Lon Hill - Coleto Creek 345KV | Kennedy Switch - Kennedy Sub 69KV | 1 |
| Lon Hill - North Edinburg 345KV | MVEC Burns - MVEC Heidelberg 138KV | 1 |
| Lon Hill - North Edinburg 345KV | MVEC Burns - Rio Hondo 138KV | 1 |
| Long Shore Switch - Odessa Ector 345KV | Morgan Creek 345/138KV Auto #1 | 1 |
| Moore - Uvalde 138KV | Leakey - Campwood 69KV | 1 |
| Morgan Creek - McDonald 138KV | McDonald - Forsan Tap 138KV | 1 |
| Nelson Sharpe - Rio Hondo 345KV | Raymondville 1 - Raymondville 2 69KV | 1 |
| Odessa EHV - Morgan Creek SES and Quail Switch 345KV | Big Spring Switch - Big Spring West 138KV | 1 |
| Roanoke Switch - Lewisville Switch 345KV | Teasley - West Denton 138KV | 1 |
| San Angelo Power Station - Live Oak 138KV | San Angelo Concho - San Angelo Lake Nasworthy 69KV | 1 |
| San Miguel 345/138KV Auto | Pleasanton 138/69KV Auto | 1 |
| STP - Hillje and STP - White Point 345KV | Blessing - Port Lavaca 69KV | 1 |
| STP - Hillje and STP - White Point 345KV | Formosa - Lolita 138KV | 1 |
| TH Wharton - Jewett & Obrien - Gibbons Creek 345KV | Ridge - Watson Chapel | 1 |
| Tradinghouse - Temple Pecan Creek 345KV | Seaton 138/69KV Transformer | 1 |
| Tradinghouse - Venus Switch 345KV | Goldthwaite - Evant 138KV | 1 |
| Twin Buttes - San Angelo 345KV | Big Lake - Twin Buttes 138KV | 1 |
| Twin Oak Switch - Gibbons Creek and Twin Oak Switch - Jack Creek 345kV | Ridge - Robertson 138KV | 1 |
| Watermill - West Levee & Todd Sargent Road 345KV | Cedar Hill Switch - Mountain Creek SES 138KV | 1 |
| TH Wharton - Jewett & Obrien - Gibbons Creek 345KV | Potential voltage collapse | 1 |
| LaPalma 138/69KV autotransformer #1 | Harlingen Switch - Harlingen #1 69KV | 1 |
| Sun Switch - Golden Switch 138KV | China Grove Switch - Bluff Creek Switch 138KV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West-North | 20 |
| North-Houston | 9 |
| North-South | 6 |
| South-North | 3 |
| North-West | 1 |

New RAP (Date indicates last update of RAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 03/18/2009 | Transmission & Security Desk V 3 Rev 100 | 404 |
| 03/06/2009 | Frequency Control Desk V 3 Rev 74 | 403 |

## Blackout/Load Shed Incidences

None

EECP

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

None

Communication

None

## ERCOT peak (Unofficial)

03/02 	   08:00 39,309 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2006 | 2007 | 2008 | 2009 |
| January | 4.79 | 4.55 | 3.30 | 4.11 |
| February | 4.81 | 3.75 | 3.59 | 3.49 |
| March | 4.95 | 2.70 | 3.29 | 3.24 |
| April | 5.59 | 3.00 | 2.45 | NA |
| May | 3.59 | 3.22 | 3.01 | NA |
| June | 2.65 | 4.46 | 2.81 | NA |
| July | 2.62 | 4.29 | 2.55 | NA |
| August | 2.09 | 3.11 | 3.66 | NA |
| September | 4.03 | 3.78 | 4.99 | NA |
| October | 3.63 | 3.08 | 2.79 | NA |
| November | 3.28 | 2.95 | 2.60 | NA |
| December | 3.44 | 3.74 | 4.54 | NA |
| Annual Average | 3.79 | 3.55 | 3.29 | 3.61 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 3/6/09 | 11:59 | 15:08 | OCN issued for possible capacity shortage for HE 1500 - 1700. |
| 3/8/09 | 7:15 | 18:15 | OCN issued for projected capacity shortage for HE 1300 - 2100. |
| 3/11/09 | 17:50 | 22:15 | OCN issued for projected capacity shortage. |
| 3/11/09 | 20:15 | 21:45 | Deployed NSRS in all zones due to deployment of all Balancing Energy bids. |
| 3/24/09 | 5:15 | 7:00 | Deployed NSRS due to VSAT results for Houston. Loss of Singleton - Obrien 345KV would result in voltage collapse. |

Transmission

03/27  04:44	Transmission Alert in Turkey area due to a forced outage in Matador area with no market solution.

03/27  13:47	Transmission Alert for the loss of Lon Hill - Coleto Creek 345KV overloads Warburton - Victoria 138KV beyond first contingency criteria.

03/27  13:47	Transmission Alert for the loss of Ballinger 138/69KV auto beyond first contingency criteria with no market solution.

Emergency Notice

03/04   13:30	Emergency Notice issued due to Ancillary Service Market for 03/05/09 did not meet the time line.

03/04   18:00	Emergency Notice issued due to RPRS Market for 03/05/09 failed to meet the time line.

03/08   17:50	Emergency Notice issued due to RPRS Market for 03/09/09 failed to meet the time line.

03/19   13:30	Emergency Notice issued due to Ancillary Service Market for 03/20/09 did not meet the time line.

03/21   13:00	Emergency Notice issued due to Ancillary Service Market for 03/21/09 did not meet the time line.

Texas RE Event Analysis

03/04   13:30	Emergency Notice issued due to Ancillary Service Market for 03/05/09 did not meet the time line.

03/04   18:00	Emergency Notice issued due to RPRS Market for 03/05/09 failed to meet the time line.

03/08   17:50	Emergency Notice issued due to RPRS Market for 03/09/09 failed to meet the time line.

03/09   10:18	Ocotillo Wind Farm SPS activated.

03/18   07:14	Station breaker failed resulting in unit trips.

03/19   13:30	Emergency Notice issued due to Ancillary Service Market for 03/20/09 did not meet the time line.

03/21   13:00	Emergency Notice issued due to Ancillary Service Market for 03/21/09 did not meet the time line.