## 025NOGRR-04
Group Review | Target Completion Date | Man Power Needed | EST Time for Completion of Monitoring Prg. | Nodal Operating Guides Section | Nodal Protocol Section 8 reference | NDSML Report ID# | Requirement | Data Purpose | Applies to Zonal? | Applies to Nodal? | Frequency of Report | Method | Report Format | Responsible Entity
QMWG | 2009-07-31 | TBD |  | 9.1 | 8.1(3)(a)-(b) | NP8-374-SG | ERCOT shall produce reports annually which summarize the seasonal test results provided by Qualified Scheduling Entities (QSEs). The QSE shall provide these results to ERCOT upon completion of Net Dependable Capability testing. | Establish HSL | Yes | Yes | Annual | Manual | Excel | QSE
QMWG | 2009-07-31 | TBD |  | 9.2(2) | 8.1(3)(c)(i)-(iii) | NP8-478-SG | ERCOT shall produce reports annually which describe when the last reactive capability test took place, what the MW and MVAR outputs were during the test period, how long the output was held, and a minimum of four MW/MVAR pairs describing the CURL of the unit. This data shall be provided by the QSE to ERCOT when reactive testing indicates a change in unit capability and at a minimum of once every two years. | TBD | Yes | Yes | Annual | Manual | Excel/Word | QSE
NDSWG | 2009-07-31 | TBD |  | 9.3(a)(i) | 8.1(3)(c)(i) | NP8-475-ER | ERCOT shall produce monthly reports as required describing the compliance with the Protocols and the Technical Advisory Committee (TAC) approved Telemetry Standards. Included in these reports shall be telemetry availability statistics. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
NDSWG | 2009-07-31 | TBD |  | 9.3(b)(i) | 8.1(3)(c)(ii) | NP8-472-ER | ERCOT shall produce monthly reports describing the percentage availability of each participants Inter-Control Center Protocol (ICCP) data link to ERCOT. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
NDSWG | 2009-07-31 | TBD |  | 9.3( c)(i) | 8.1(3)(c)(iii) | <new> | ERCOT shall produce monthly telemetry availability reports for Dynamically Scheduled Resource (DSR) Loads. A DSR Load telemetry failure greater than five minutes will be recorded as an unavailable period. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
NDSWG | 2009-07-31 | TBD |  | 9.3( c)(ii) | 8.1(3)(c)(i) | NP8-475-ER | ERCOT shall produce monthly telemetry availability reports for Resources and the reports shall at a minimum consist of the following: Resource status, Resource Gross MWs, Resource Net MWs, and Resource High Sustained Limit (HSL). | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.4 | 8.1(3)(f) | NP8-510 | ERCOT shall produce monthly reports describing Qualified Scheduling Entity (QSE) and Resource valid dispatch instruction performance. A valid dispatch instruction is a Security-Constrained Economic Dispatch (SCED) Base Point. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
NDSWG | 2009-07-31 | TBD |  | 9.5(1)(a) | 8.1(3)(i) | <new> | Number of Network Operations Model Change Requests (NOMCRs) submitted by QSE; | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
NDSWG | 2009-07-31 | TBD |  | 9.5(1)(b) | 8.1(3)(i) | <new> | Number of invalid NOMCRs rejected by ERCOT and returned to the QSE; and | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
NDSWG | 2009-07-31 | TBD |  | 9.5(1)( c) | 8.1(3)(i) | <new> | Number of Notices of interim updates submitted to the Public Utility Commission of Texas (PUCT) accumulated by QSE. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
NDSWG | 2009-07-31 | TBD |  | 9.5(2) | 8.1(3)(i) | <new> | ERCOT shall post reports (model) showing individual QSE and TSP performance on the Market Information System (MIS) Secure Area. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(a) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler greater than 335 days (11 months) in advance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(b) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between 90 and 334 days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(c) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between eight and 89 days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(d) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between three and seven days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(e) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted less than three days in advance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(f) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outages by Outage type. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(g) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Total Number of Outages that were requested, accepted, approved, cancelled, and withdrawn. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(2) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | ERCOT shall post reports showing individual owner performance on the MIS Secure Area. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.7 | 8.1(3)(l) | NP8-70-M | ERCOT shall produce a report identifying the date of backup control testing and the success or failure of that test. Results shall be provided by the Qualified Scheduling Entity (QSE) to ERCOT at the completion of all tests. Backup control tests shall be conducted at least annually. | TBD |  | Yes | Annual | Manual | Word | ERCOT
QMWG | 2009-07-31 | TBD |  | 9.8 | 8.1(3)(n) | NP8-70-M | A QSE shall maintain a 24x7 scheduling center with qualified personnel with the authority to commit and bind the QSE. ERCOT shall report to the Texas Regional Entity (TRE), instances of suspected non-performance following ERCOT’s investigation. | TBD |  | Yes | Adhoc | Manual | Word | ERCOT/TRE
QMWG | 2009-07-31 | TBD |  | 9.9(1) | 8.1(3)(o) | NP8-65-M | ERCOT shall record QSE provided AVR test reports which will include:(a) The minimum and maximum excitation limiters settings and associated time limits; (b) Volts/hertz settings;(c) Gain and time constants; (d) Date tested; and (e) Voltage regulator control setting; | TBD |  | Yes | Adhoc | Manual | Word | QSE ERCOT
QMWG | 2009-07-31 | TBD |  | 9.9(2) | 8.1(3)(o) | NP8-65-M | ERCOT shall produce a report that will identify Resources that have not submitted test reports within the last 60 months. | TBD |  | Yes | Adhoc | Manual | Word | ERCOT
QMWG | 2009-07-31 | TBD |  | 9.10(1) | 8.1(3)(r) 8.1.2 | NP8-140-ER | ERCOT shall report the number of times that telemeter limits captured by Security Constrained Economic Dispatch (SCED) differ by greater than 5% with the Current Operating Plan (COP) limits as captured in a snapshot five minutes before the Operating Hour begins. The report shall be prepared monthly and shall include Resource names, deviations greater than 5%, and total number of SCED intervals analyzed. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(2) | 8.1.2 | NP8-140-ER | ERCOT shall report when a Resource has not submitted a COP for seven consecutive Operating Days by 1500 of each day. This report shall be prepared monthly and posted on the MIS Secure Area. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(3) | 8.1.2 | NP8-140-ER | ERCOT shall report in the Day-Ahead when the capacity of Resources in the Operating Day COP at 1430 is not sufficient to supply Ancillary Service requirements. ERCOT shall provide a monthly summary of the total days failed and total days analyzed. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(4) | 8.1.2 | NP8-140-ER | ERCOT shall report deviations between the Day-Ahead COP at 1530 and actual committed Resources for the same hour in the Operating Day COP of Resources with Energy-Offer curves and Output Schedules and that are supplying Ancillary Service requirements. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(5) | 8.1.2 | NP8-140-ER | ERCOT shall report when an Energy Offer Curve or Output Schedule is not provided for a Generation Resource that is scheduled On-Line in COP for the next hour. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(6) | 8.1.2 | NP8-140-ER | ERCOT shall report the number of instances when a Resource’s Outage Schedule does not match its COP. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
OWG | 2009-07-31 | TBD |  | 9.11.1 | 8.3 | NP8-505-M | ERCOT in the first quarter of each year or provide notice that the rating methodology has not changed since the previous year. ERCOT shall keep records describing the rating methodologies of each TSP in the ERCOT Region. | TBD | Yes | Yes | Annually (first quarter) | Manual | Word/ MIS | ERCOT
OWG | 2009-07-31 | TBD |  | 9.11.1 | 8.3 | NP8-505-M | ERCOT shall prepare an annual report summarizing these rating methodologies and submit this information to the TRE. | TBD | Yes | Yes | Annually | Manual | Word | ERCOT
NDSWG | 2009-07-31 | TBD |  | 9.11.2 | 8.3(1)(b) | NP8-365-ER | ERCOT shall produce monthly reports describing Real-Time data performance of TSPs. These reports shall include measurements as detailed in the Technical Advisory Committee (TAC) approved Telemetry Standards. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(a) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler greater than 335 days (11 months) in advance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(b) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between 90 and 334 days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(c) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between eight and 89 days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(d) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between three and seven days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(e) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted less than three days in advance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(f) | 8.3(1)(c) | NP8-409-ER | Number of Outages by Outage type. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(g) | 8.3(1)(c) | NP8-409-ER | Total Number of Outages that were requested, accepted, approved, cancelled, and withdrawn. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(2) | 8.3(1)(c) | NP8-409-ER | ERCOT shall post reports showing individual owner performance on the Market Information System (MIS) Secure Area. (Outages) | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
NDSWG | 2009-07-31 | TBD |  | 9.11.4 (1)(a) | 8.3(1)(d) | <new> | Number of Network Operations Model Change Requests (NOMCRs) submitted during the month by the TSP; | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
NDSWG | 2009-07-31 | TBD |  | 9.11.4 (1)(b) | 8.3(1)(d) | <new> | Number of invalid NOMCRs rejected by ERCOT and returned to the TSP; and | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
NDSWG | 2009-07-31 | TBD |  | 9.11.4 (1)(c) | 8.3(1)(d) | <new> | Number of interim reports submitted to the Public Utility Commission of Texas (PUCT) accumulated by TSP. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
NDSWG | 2009-07-31 | TBD |  | 9.11.4 (2) | 8.3(1)(d) | <new> | ERCOT shall post monthly reports showing individual TSP performance on the MIS Secure Area. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
OWG | 2009-07-31 | TBD |  | 9.11.5 | 8.3(1)(g) | NP8-510 | ERCOT shall produce monthly reports describing Transmission Service Provider (TSP) valid Dispatch Instruction performance. | TBD |  | Yes | Monthly | Manual | Word/MIS | TSP
OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(i) | 8.2(2)(a) | NP8-403-M | Transmission equipment ratings that are exceeded; | TBD | Yes | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(ii) | 8.2(2)(a) | NP8-403-M | Violations of system operating limits or power transfer limitations set by ERCOT to guard against post-contingency stability exceedance for over ten minutes; and | TBD | Yes | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(iii) | 8.2(2)(a) | NP8-403-M | Violations of system operating limits or power transfer limitations set by ERCOT to guard against post-contingency stability exceedance for over thirty minutes. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(iv) | 8.2(2)(a) | NP8-403-M | N-1 post-contingency violations of equipment ratings provided by TSPs and QSEs for over 30 minutes. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(v) | 8.2(2)(a) | NP8-403-M | Base power violations detected during the month, the time duration of the loading above normal operating limit or, the average operating limit exceeded if the element was dynamically rated, and the average percentage loading. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(a) | 8.2(2)(a) | NP8-403-M | ERCOT shall prepare reports describing the number of Forced Outages by TSP by month; | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(b) | 8.2(2)(a)(ii) | NP8-501-ER | ERCOT shall post on the Market Information System (MIS) Secure Area its performance in processing TSP Outage requests in accordance with the following table including justification for rolling Outages from one timeline to another: | TBD |  | Yes | Daily | Automatic | CDR/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(c) | 8.2(2)(a)(ii) | NP8-403-M | ERCOT shall post on the MIS Secure Area its performance in sending TSPs rejection Notices. The report will include specific concerns that caused the rejection. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(d) | 8.2(2)(a)(ii) | NP8-403-M | ERCOT shall post on the MIS Secure Area, by TSP, the number of withdrawals of approved Outages. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(e) | 8.2(2)(a)(ii) | NP8-403-M | ERCOT shall post on the MIS Secure Area, by TSP, the number of approved Outages that were rescheduled by ERCOT. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/QMWG/ SDAWG | 2009-07-31 | TBD |  | 9.12.1(3)(a)(i) | 8.2(2)(l) | NP8-403-M | Reliability Unit Commitment (RUC) charges uplifted; | TBD |  | Yes | Monthly | Automatic | MIS | ERCOT
ERCOT/QMWG/ SDAWG | 2009-07-31 | TBD |  | 9.12.1(3)(a)(ii) | 8.2(2)(l) | NP8-403-M | Voltage support charges uplifted; and | TBD |  | Yes | Monthly | Automatic | MIS | ERCOT
ERCOT/QMWG/ SDAWG | 2009-07-31 | TBD |  | 9.12.1(3)(a)(iii) | 8.2(2)(l) | NP8-403-M | Uplift payments due to Base Point deviations charges. | TBD |  | Yes | Monthly | Automatic | MIS | ERCOT
ERCOT/NDSWG | 2009-07-31 | TBD |  | 9.12.1(4)(a) | 8.2(2)(a)(iii) | NP8-403-M | ERCOT shall report State Estimator performance in accordance with the Protocols and the TAC-approved standard and post such report on the MIS Secure Area. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
QMWG | 2009-07-31 | TBD |  | 9.12.2(1)(a) | 8.2(2)(b)(ii)(a) | NP8-403-M | Average sum of Regulation Up (Reg-Up) and Regulation Down (Reg-Down) energy - ERCOT shall report for each month the difference between the 5-minute average monthly sum of Reg-Up energy deployed and the 5-minute average monthly sum of Reg-Down energy deployed for each 5-minute interval of the Operating Day. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
QMWG | 2009-07-31 | TBD |  | 9.12.2(1)(b) | 8.2(2)(b)(ii)(b) | NP8-403-M | Total Reg–Up and Reg-Down per interval - ERCOT shall develop a monthly report detailing the total amount of Reg-Up energy deployed in the Settlement Interval and the total amount of Reg-Down energy deployed for each Settlement Interval of the Operating Day. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
OWG | 2009-07-31 | TBD |  | 9.12.2(2)(a) | 8.2(2)(b)(iii) | NP8-403-M | ERCOT shall prepare monthly reports describing amounts of time that it operated without sufficient operating reserves as defined in the Protocols. | TBD | Yes | Yes | Monthly | Automatic | EDW/MIS | ERCOT
QMWG | 2009-07-31 | TBD |  | 9.12.2(3)(a) | 8.2(2)(b)(iv) | NP8-403-M | For each month, ERCOT shall report, Generation Resources committed in the RUC process, including Resource name, intervals deployed, process in which the Resource was committed, and any deviation from Resources committed and actual Resource performance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
QMWG | 2009-07-31 | TBD |  | 9.12.2(4)(a) | 8.2(2)(b)(v) | NP8-403-M | ERCOT shall produce monthly reports for DSR Load signal failures of more than five minutes. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.12.2(5)(a) | 8.2(2)(b)(v) | NP8-403-M | ERCOT shall record and report, on a monthly basis, instances of Dispatch Instructions to Resources not providing Regulation Service in which there is an inflection in the instruction for four consecutive Security-Constrained Economic Dispatch (SCED) intervals for validation and review. Inflection is defined as a reversal in ramp direction between consecutive intervals. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
PDCWG | 2009-07-31 | TBD |  | 9.12.2(6)(a) | 8.2(2)(b)(viii) | NP8-403-M | ERCOT shall report monthly the resulting system performance for each measurable frequency event. | TBD | Yes | Yes | Monthly | Manual | Excel / Word | ERCOT
ERCOT/QMWG | 2009-07-31 | TBD |  | 9.12.3(a) | 8.2(2)(c)(i) | NP8-403-M | The accuracy of each day’s System Load forecast posted at 0600 in the Day-Ahead of the Operating Day as compared with the actual average ERCOT Load for each hour of the Operating Day; | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
ERCOT/QMWG | 2009-07-31 | TBD |  | 9.12.3(b) | 8.2(2)(c)(ii) | NP8-403-M | Accuracy of the system Load forecast used for Day-Ahead Reliability Unit Commitment (RUC) compared to the actual average ERCOT Load for each hour of the Operating Day; and | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
NDSWG | 2009-07-31 | TBD |  | 9.12.3(c) | 8.2(2)(c)(iii) | NP8-403-M | The accuracy of the Load forecast for the following items compared to the average of the State Estimated Load at each Electrical Bus with a modeled Load for each hour: | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
ERCOT/QMWG | 2009-07-31 | TBD |  | 9.12.3(d) | 8.2(2)(c)(iii)(b) | NP8-403-M | Hourly Load forecast used in the Day-Ahead RUC by Weather Zone; | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
ERCOT/QMWG | 2009-07-31 | TBD |  | 9.12.3(e) | 8.2(2)(c)(iii)(d) | NP8-403-M | Hourly Load forecast used in the Hourly RUC by Weather Zone; and | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
NDSWG | 2009-07-31 | TBD |  | 9.12.3(f) | 8.2(2)(c)(iii)(e) | NP8-403-M | The accuracy of the Load forecast used in the Day-Ahead RUC for the largest MW and MVA differences between the hourly Bus Load Forecast and the Real-Time Load at each Electrical Bus, by Weather Zone. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
ERCOT/CMWG | 2009-07-31 | TBD |  | 9.12.4(a) | 8.2(2)(d) | NP8-403-M | Three consecutive days of a particular congestion constraint (constraints passed to Security-Constrained Economic Dispatch (SCED) from Network Security Analysis (NSA)) in Real-Time not identified in the Day Ahead Market (DAM); | TBD |  | Yes | Daily | Automatic | CDR/MIS | ERCOT
ERCOT/CMWG | 2009-07-31 | TBD |  | 9.12.4(b) | 8.2(2)(d) | NP8-403-M | Two consecutive hours of a particular congestion constraint in Real-Time not identified in the Hourly Reliability Unit Commitment (HRUC) process; and | TBD |  | Yes | Daily | Automatic | CDR/MIS | ERCOT
ERCOT/CMWG | 2009-07-31 | TBD |  | 9.12.4(c) | 8.2(2)(d) | NP8-403-M | Two consecutive days of a particular congestion constraint in Real-Time not identified in the Day-Ahead Reliability Unit Commitment (DRUC) process. | TBD |  | Yes | Daily | Automatic | CDR/MIS | ERCOT
NDSWG | 2009-07-31 | TBD |  | 9.12.5 | 8.2(2)(f)-(g) | NP8-403-M | ERCOT shall report monthly on the Network Operations Model update implementation performance. The report shall include the total number of Network Operations Model Change Requests (NOMCR) submitted, approved, rejected, withdrawn and any other status contained in the Protocols or defined by ERCOT. The report shall also include the number of interim updates and reasons provided (previously included in Protocol-required Public Utility Commission of Texas (PUCT) reports) for the interim updates provided by Market Participants. The timeline defined in the Protocols shall be used in the performance evaluation. The report should itemize any non-Generation Resource Transmission Element whose limits were changed outside of the NOMCR process. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
QMWG/ OWG | 2009-07-31 | TBD |  | 9.12.6(1)(a) | 8.2(2)(h) | NP8-403-M | Qualified Scheduling Entities (QSEs) and Transmission Service Providers (TSPs) which have approved back-up procedures on file with ERCOT and the date that the plan was last updated; and | TBD | Yes | Yes | Annually (first quarter) | Manual | Word | ERCOT
ERCOT/QMWG/ OWG | 2009-07-31 | TBD |  | 9.12.6(1)(b) | 8.2(2)(h) | NP8-403-M | The status of ERCOT’s back-up plan and the status of back-up training for QSEs and TSPs. | TBD |  | Yes | Annually (first quarter) | Manual | Word | ERCOT
QMWG/OWG | 2009-07-31 | TBD |  | 9.12.6(2) | 8.2(2)(h) | NP8-403-M | ERCOT shall confirm that a staffing plan is part of the procedures submitted by QSEs and TSPs. | TBD |  | Yes | Annually (first quarter) | Manual | Word | ERCOT
BSTF | 2009-07-31 | TBD |  | 9.12.7 | 8.2(2)(i) | NP8-403-M | ERCOT shall develop an annual Black Start Plan and post on the MIS Secure Area. | TBD | Yes | Yes | Annually | Manual | Word | ERCOT
ERCOT/OWG | 2009-07-31 | TBD |  | 9.12.8 | 8.2(2)(k) | NP8-403-M | ERCOT shall report monthly the performance of its computer and communications systems as compared to its standards. | TBD | Yes | Yes | Monthly | Manual | Word | ERCOT
ERCOT/OWG | 2009-07-31 | TBD |  | 9.12.9 | 8.2(2)(a)(iv) | NP8-403-M | (a) Number of Real-Time voltage violations and metrics describing duration of such violations; (b) Number of N-1 voltage based security violations and metrics describing duration of such violations; (c) Metrics describing reactive reserve in voltage constrained areas; and (d) Metrics describing N-1 import limitations in voltage constrained areas. ERCOT shall monitor voltage violations, N-1 voltage violations, reactive reserves, and import margins to voltage constrained areas not resolved within 15 minutes. ERCOT shall produce monthly reports for each Transmission Service Provider (TSP) summarizing: | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13 | 8.1.2 | NP8-143-CD | ERCOT shall monitor Ancillary Service energy deployment according to the criteria outlined in Protocol Section 8, Performance Monitoring and Compliance. Reports required by Protocol Section 8.1.1.4, QSE Ancillary Service Energy Deployment Monitoring Criteria, will be posted on the Market Information System (MIS) Certified Area. | TBD |  | Yes | Monthly | Automatic/Manual | COGNOS/PI | QSE
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13.1 | 8.1.1.4.1 | NP8-501-ER | ERCOT shall produce monthly and yearly reports of Qualified Scheduling Entity (QSE) and Resource specific regulation performance metrics as required in the Protocols. | TBD |  | Yes | Monthly / Annual | Automatic / Manual | COGNOS/PI | QSE
QMWG | 2009-07-31 | TBD |  | 9.13.2 | 8.1(3)(g) | NP8-502-M | ERCOT shall produce monthly reports of Hydro responsive tests and verify results submitted by Qualified Scheduling Entity (QSE) for qualification. | TBD |  | Yes | Monthly | Manual | PI / RQT | QSE
BSTF | 2009-07-31 | TBD |  | 9.13.3 | 8.1(3)(h) | NP8-87--M | ERCOT shall produce annual reports containing record(s) of if and when a black start procedure was last received at ERCOT including the Qualified Scheduling Entity (QSE) or Transmission Service Provider (TSP) name and date procedure received. The QSEs participating in Black Start Service and TSPs shall provide an updated black start procedure to ERCOT by the end of the 1st quarter and when the procedure has changed. | TBD |  | Yes | Annual | Manual | Excel / Word | QSE / TSP
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13.4 | 8.1(3)(k) | NP8-542-ER | ERCOT shall develop monthly reports detailing Resource-specific Responsive Reserve performance, for both capacity deployment and energy delivered, as required in the Protocols. | TBD |  | Yes | Monthly | Automatic / Manual | COGNOS/PI | QSE / Resource
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13.5 | 8.1.1.2.1.1(2) | NP8-418-M | ERCOT shall survey Qualified Scheduling Entities (QSEs) qualified to provide Regulation Services to attest that the QSEs have the capability to operate in constant frequency control mode. ERCOT shall develop annual summaries of QSEs surveyed. | TBD |  | Yes | Annual | Manual | Excel / Word | QSE
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13.6 | 8.1(3)(m) | NP8-504-ER | ERCOT shall develop a monthly summary for Non-Spinning Reserve (Non-Spin) deployed by Resource, and the Resource response after 30 minutes. Each Resource shall meet at all times the Non-Spin energy deployment criteria as described in the Protocols. | TBD |  | Yes | Monthly | Automatic / Manual | COGNOS/PI | QSE / Resource
Note on J2: ERCOT: Hydro Only
Note on K2: ERCOT: Yes, needs clarification

## QMWG Only
Group Review | Target Completion Date | Man Power Needed | EST Time for Completion of Monitoring Prg. | Nodal Operating Guides Section | Nodal Protocol Section 8 reference | NDSML Report ID# | Requirement | Data Purpose | Applies to Zonal? | Applies to Nodal? | Frequency of Report | Method | Report Format | Responsible Entity
QMWG | 2009-07-31 | TBD |  | 9.1 | 8.1(3)(a)-(b) | NP8-374-SG | ERCOT shall produce reports annually which summarize the seasonal test results provided by Qualified Scheduling Entities (QSEs). The QSE shall provide these results to ERCOT upon completion of Net Dependable Capability testing. | Establish HSL | Yes | Yes | Annual | Manual | Excel | QSE
QMWG | 2009-07-31 | TBD |  | 9.4 | 8.1(3)(f) | NP8-510 | ERCOT shall produce monthly reports describing Qualified Scheduling Entity (QSE) and Resource valid dispatch instruction performance. A valid dispatch instruction is a Security-Constrained Economic Dispatch (SCED) Base Point. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.8 | 8.1(3)(n) | NP8-70-M | A QSE shall maintain a 24x7 scheduling center with qualified personnel with the authority to commit and bind the QSE. ERCOT shall report to the Texas Regional Entity (TRE), instances of suspected non-performance following ERCOT’s investigation. | TBD |  | Yes | Adhoc | Manual | Word | ERCOT/TRE
QMWG | 2009-07-31 | TBD |  | 9.10(1) | 8.1(3)(r) 8.1.2 | NP8-140-ER | ERCOT shall report the number of times that telemeter limits captured by Security Constrained Economic Dispatch (SCED) differ by greater than 5% with the Current Operating Plan (COP) limits as captured in a snapshot five minutes before the Operating Hour begins. The report shall be prepared monthly and shall include Resource names, deviations greater than 5%, and total number of SCED intervals analyzed. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(2) | 8.1.2 | NP8-140-ER | ERCOT shall report when a Resource has not submitted a COP for seven consecutive Operating Days by 1500 of each day. This report shall be prepared monthly and posted on the MIS Secure Area. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(3) | 8.1.2 | NP8-140-ER | ERCOT shall report in the Day-Ahead when the capacity of Resources in the Operating Day COP at 1430 is not sufficient to supply Ancillary Service requirements. ERCOT shall provide a monthly summary of the total days failed and total days analyzed. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(4) | 8.1.2 | NP8-140-ER | ERCOT shall report deviations between the Day-Ahead COP at 1530 and actual committed Resources for the same hour in the Operating Day COP of Resources with Energy-Offer curves and Output Schedules and that are supplying Ancillary Service requirements. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(5) | 8.1.2 | NP8-140-ER | ERCOT shall report when an Energy Offer Curve or Output Schedule is not provided for a Generation Resource that is scheduled On-Line in COP for the next hour. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.10(6) | 8.1.2 | NP8-140-ER | ERCOT shall report the number of instances when a Resource’s Outage Schedule does not match its COP. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.12.2(1)(a) | 8.2(2)(b)(ii)(a) | NP8-403-M | Average sum of Regulation Up (Reg-Up) and Regulation Down (Reg-Down) energy - ERCOT shall report for each month the difference between the 5-minute average monthly sum of Reg-Up energy deployed and the 5-minute average monthly sum of Reg-Down energy deployed for each 5-minute interval of the Operating Day. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
QMWG | 2009-07-31 | TBD |  | 9.12.2(1)(b) | 8.2(2)(b)(ii)(b) | NP8-403-M | Total Reg–Up and Reg-Down per interval - ERCOT shall develop a monthly report detailing the total amount of Reg-Up energy deployed in the Settlement Interval and the total amount of Reg-Down energy deployed for each Settlement Interval of the Operating Day. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
QMWG | 2009-07-31 | TBD |  | 9.12.2(3)(a) | 8.2(2)(b)(iv) | NP8-403-M | For each month, ERCOT shall report, Generation Resources committed in the RUC process, including Resource name, intervals deployed, process in which the Resource was committed, and any deviation from Resources committed and actual Resource performance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
QMWG | 2009-07-31 | TBD |  | 9.12.2(4)(a) | 8.2(2)(b)(v) | NP8-403-M | ERCOT shall produce monthly reports for DSR Load signal failures of more than five minutes. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.12.2(5)(a) | 8.2(2)(b)(v) | NP8-403-M | ERCOT shall record and report, on a monthly basis, instances of Dispatch Instructions to Resources not providing Regulation Service in which there is an inflection in the instruction for four consecutive Security-Constrained Economic Dispatch (SCED) intervals for validation and review. Inflection is defined as a reversal in ramp direction between consecutive intervals. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE
QMWG | 2009-07-31 | TBD |  | 9.13.2 | 8.1(3)(g) | NP8-502-M | ERCOT shall produce monthly reports of Hydro responsive tests and verify results submitted by Qualified Scheduling Entity (QSE) for qualification. | TBD |  | Yes | Monthly | Manual | PI / RQT | QSE
QMWG | 2009-07-31 | TBD |  | 9.2(2) | 8.1(3)(c)(i)-(iii) | NP8-478-SG | ERCOT shall produce reports annually which describe when the last reactive capability test took place, what the MW and MVAR outputs were during the test period, how long the output was held, and a minimum of four MW/MVAR pairs describing the CURL of the unit. This data shall be provided by the QSE to ERCOT when reactive testing indicates a change in unit capability and at a minimum of once every two years. | TBD | Yes | Yes | Annual | Manual | Excel/Word | QSE
QMWG | 2009-07-31 | TBD |  | 9.9(1) | 8.1(3)(o) | NP8-65-M | ERCOT shall record QSE provided AVR test reports which will include:(a) The minimum and maximum excitation limiters settings and associated time limits; (b) Volts/hertz settings;(c) Gain and time constants; (d) Date tested; and (e) Voltage regulator control setting; | TBD |  | Yes | Adhoc | Manual | Word | QSE ERCOT
QMWG | 2009-07-31 | TBD |  | 9.9(2) | 8.1(3)(o) | NP8-65-M | ERCOT shall produce a report that will identify Resources that have not submitted test reports within the last 60 months. | TBD |  | Yes | Adhoc | Manual | Word | ERCOT
Note on J2: ERCOT: Hydro Only
Note on K2: ERCOT: Yes, needs clarification

## ERCOT_QMWG
Group Review | Target Completion Date | Man Power Needed | EST Time for Completion of Monitoring Prg. | Nodal Operating Guides Section | Nodal Protocol Section 8 reference | NDSML Report ID# | Requirement | Data Purpose | Applies to Zonal? | Applies to Nodal? | Frequency of Report | Method | Report Format | Responsible Entity
ERCOT/QMWG | 2009-07-31 | TBD |  | 9.12.3(a) | 8.2(2)(c)(i) | NP8-403-M | The accuracy of each day’s System Load forecast posted at 0600 in the Day-Ahead of the Operating Day as compared with the actual average ERCOT Load for each hour of the Operating Day; | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
ERCOT/QMWG | 2009-07-31 | TBD |  | 9.12.3(b) | 8.2(2)(c)(ii) | NP8-403-M | Accuracy of the system Load forecast used for Day-Ahead Reliability Unit Commitment (RUC) compared to the actual average ERCOT Load for each hour of the Operating Day; and | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
ERCOT/QMWG | 2009-07-31 | TBD |  | 9.12.3(d) | 8.2(2)(c)(iii)(b) | NP8-403-M | Hourly Load forecast used in the Day-Ahead RUC by Weather Zone; | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT
ERCOT/QMWG | 2009-07-31 | TBD |  | 9.12.3(e) | 8.2(2)(c)(iii)(d) | NP8-403-M | Hourly Load forecast used in the Hourly RUC by Weather Zone; and | TBD |  | Yes | Monthly | Automatic | EDW/MIS | ERCOT

## OWG_QMWG
Group Review | Target Completion Date | Man Power Needed | EST Time for Completion of Monitoring Prg. | Nodal Operating Guides Section | Nodal Protocol Section 8 reference | NDSML Report ID# | Requirement | Data Purpose | Applies to Zonal? | Applies to Nodal? | Frequency of Report | Method | Report Format | Responsible Entity
OWG/QMWG | 2009-07-31 | TBD |  | 9.7 | 8.1(3)(l) | NP8-70-M | ERCOT shall produce a report identifying the date of backup control testing and the success or failure of that test. Results shall be provided by the Qualified Scheduling Entity (QSE) to ERCOT at the completion of all tests. Backup control tests shall be conducted at least annually. | TBD |  | Yes | Annual | Manual | Word | ERCOT
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(a) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler greater than 335 days (11 months) in advance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(b) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between 90 and 334 days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(c) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between eight and 89 days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(d) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between three and seven days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(e) | 8.3(1)(c) | NP8-409-ER | Number of Outage requests submitted less than three days in advance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(f) | 8.3(1)(c) | NP8-409-ER | Number of Outages by Outage type. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(1)(g) | 8.3(1)(c) | NP8-409-ER | Total Number of Outages that were requested, accepted, approved, cancelled, and withdrawn. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.11.3(2) | 8.3(1)(c) | NP8-409-ER | ERCOT shall post reports showing individual owner performance on the Market Information System (MIS) Secure Area. (Outages) | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(i) | 8.2(2)(a) | NP8-403-M | Transmission equipment ratings that are exceeded; | TBD | Yes | Yes | Monthly | Automatic | EDW/MIS | TSP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(a) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler greater than 335 days (11 months) in advance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(b) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between 90 and 334 days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(c) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between eight and 89 days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(d) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted in the ERCOT Outage Scheduler between three and seven days in advance of the desired Outage date. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(e) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outage requests submitted less than three days in advance. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(f) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Number of Outages by Outage type. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(1)(g) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | Total Number of Outages that were requested, accepted, approved, cancelled, and withdrawn. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.6(2) | 8.1(3)(j) 8.1(3)(q) | NP8-409-ER | ERCOT shall post reports showing individual owner performance on the MIS Secure Area. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | QSE/TSP/TOP
OWG/QMWG | 2009-07-31 | TBD |  | 9.12.6(1)(a) | 8.2(2)(h) | NP8-403-M | Qualified Scheduling Entities (QSEs) and Transmission Service Providers (TSPs) which have approved back-up procedures on file with ERCOT and the date that the plan was last updated; and | TBD | Yes | Yes | Annually (first quarter) | Manual | Word | ERCOT
OWG/QMWG | 2009-07-31 | TBD |  | 9.12.6(2) | 8.2(2)(h) | NP8-403-M | ERCOT shall confirm that a staffing plan is part of the procedures submitted by QSEs and TSPs. | TBD |  | Yes | Annually (first quarter) | Manual | Word | ERCOT

## ERCOT_OWG_QMWG
Group Review | Target Completion Date | Man Power Needed | EST Time for Completion of Monitoring Prg. | Nodal Operating Guides Section | Nodal Protocol Section 8 reference | NDSML Report ID# | Requirement | Data Purpose | Applies to Zonal? | Applies to Nodal? | Frequency of Report | Method | Report Format | Responsible Entity
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(ii) | 8.2(2)(a) | NP8-403-M | Violations of system operating limits or power transfer limitations set by ERCOT to guard against post-contingency stability exceedance for over ten minutes; and | TBD | Yes | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(iii) | 8.2(2)(a) | NP8-403-M | Violations of system operating limits or power transfer limitations set by ERCOT to guard against post-contingency stability exceedance for over thirty minutes. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(iv) | 8.2(2)(a) | NP8-403-M | N-1 post-contingency violations of equipment ratings provided by TSPs and QSEs for over 30 minutes. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(1)(a)(v) | 8.2(2)(a) | NP8-403-M | Base power violations detected during the month, the time duration of the loading above normal operating limit or, the average operating limit exceeded if the element was dynamically rated, and the average percentage loading. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(a) | 8.2(2)(a) | NP8-403-M | ERCOT shall prepare reports describing the number of Forced Outages by TSP by month; | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(b) | 8.2(2)(a)(ii) | NP8-501-ER | ERCOT shall post on the Market Information System (MIS) Secure Area its performance in processing TSP Outage requests in accordance with the following table including justification for rolling Outages from one timeline to another: | TBD |  | Yes | Daily | Automatic | CDR/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(c) | 8.2(2)(a)(ii) | NP8-403-M | ERCOT shall post on the MIS Secure Area its performance in sending TSPs rejection Notices. The report will include specific concerns that caused the rejection. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(d) | 8.2(2)(a)(ii) | NP8-403-M | ERCOT shall post on the MIS Secure Area, by TSP, the number of withdrawals of approved Outages. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.1(2)(e) | 8.2(2)(a)(ii) | NP8-403-M | ERCOT shall post on the MIS Secure Area, by TSP, the number of approved Outages that were rescheduled by ERCOT. | TBD |  | Yes | Monthly | Automatic | EDW/MIS | TSP
ERCOT/OWG/QMWG | 2009-07-31 | TBD |  | 9.12.6(1)(b) | 8.2(2)(h) | NP8-403-M | The status of ERCOT’s back-up plan and the status of back-up training for QSEs and TSPs. | TBD |  | Yes | Annually (first quarter) | Manual | Word | ERCOT
10

## PDCWG_QMWG
Group Review | Target Completion Date | Man Power Needed | EST Time for Completion of Monitoring Prg. | Nodal Operating Guides Section | Nodal Protocol Section 8 reference | NDSML Report ID# | Requirement | Data Purpose | Applies to Zonal? | Applies to Nodal? | Frequency of Report | Method | Report Format | Responsible Entity
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13 | 8.1.2 | NP8-143-CD | ERCOT shall monitor Ancillary Service energy deployment according to the criteria outlined in Protocol Section 8, Performance Monitoring and Compliance. Reports required by Protocol Section 8.1.1.4, QSE Ancillary Service Energy Deployment Monitoring Criteria, will be posted on the Market Information System (MIS) Certified Area. | TBD |  | Yes | Monthly | Automatic/Manual | COGNOS/PI | QSE
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13.1 | 8.1.1.4.1 | NP8-501-ER | ERCOT shall produce monthly and yearly reports of Qualified Scheduling Entity (QSE) and Resource specific regulation performance metrics as required in the Protocols. | TBD |  | Yes | Monthly / Annual | Automatic / Manual | COGNOS/PI | QSE
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13.4 | 8.1(3)(k) | NP8-542-ER | ERCOT shall develop monthly reports detailing Resource-specific Responsive Reserve performance, for both capacity deployment and energy delivered, as required in the Protocols. | TBD |  | Yes | Monthly | Automatic / Manual | COGNOS/PI | QSE / Resource
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13.5 | 8.1.1.2.1.1(2) | NP8-418-M | ERCOT shall survey Qualified Scheduling Entities (QSEs) qualified to provide Regulation Services to attest that the QSEs have the capability to operate in constant frequency control mode. ERCOT shall develop annual summaries of QSEs surveyed. | TBD |  | Yes | Annual | Manual | Excel / Word | QSE
PDCWG/ QMWG | 2009-07-31 | TBD |  | 9.13.6 | 8.1(3)(m) | NP8-504-ER | ERCOT shall develop a monthly summary for Non-Spinning Reserve (Non-Spin) deployed by Resource, and the Resource response after 30 minutes. Each Resource shall meet at all times the Non-Spin energy deployment criteria as described in the Protocols. | TBD |  | Yes | Monthly | Automatic / Manual | COGNOS/PI | QSE / Resource

## ERCOT_QMWG_SDAWG
Group Review | Target Completion Date | Man Power Needed | EST Time for Completion of Monitoring Prg. | Nodal Operating Guides Section | Nodal Protocol Section 8 reference | NDSML Report ID# | Requirement | Data Purpose | Applies to Zonal? | Applies to Nodal? | Frequency of Report | Method | Report Format | Responsible Entity
ERCOT/QMWG/ SDAWG | 2009-07-31 | TBD |  | 9.12.1(3)(a)(i) | 8.2(2)(l) | NP8-403-M | Reliability Unit Commitment (RUC) charges uplifted; | TBD |  | Yes | Monthly | Automatic | MIS | ERCOT
ERCOT/QMWG/ SDAWG | 2009-07-31 | TBD |  | 9.12.1(3)(a)(ii) | 8.2(2)(l) | NP8-403-M | Voltage support charges uplifted; and | TBD |  | Yes | Monthly | Automatic | MIS | ERCOT
ERCOT/QMWG/ SDAWG | 2009-07-31 | TBD |  | 9.12.1(3)(a)(iii) | 8.2(2)(l) | NP8-403-M | Uplift payments due to Base Point deviations charges. | TBD |  | Yes | Monthly | Automatic | MIS | ERCOT