ERCOT Nodal Operating Guides

Section 8

Attachment E

Biennial Unit Reactive Limits (Lead and Lag) Verification

November 1, 2007

(Effective Upon Texas Nodal Market Implementation)

# Biennial Unit Reactive Limits (Lead and Lag) Verification

General Information

Unit Code (16 character): *			Location (County): *

Unit Name:  *					Date of test: *

Generator’s QSE: *				Resource Entity: *

For test details, reference Section 3.3.2.2, Non-Coordinated Reactive Testing and 3.3.2.3, Coordinated Reactive Testing.

* This entry is required for all tests

*CORRECTED UNIT REACTIVE LIMIT (CURL) CURVE: (1)

Maximum Lagging Reactive at current Gross Dependable MW Output			 MVAR(Gross) at 	 MW(Gross) (1)

Maximum Lagging Reactive at current Gross Low Sustained Limit MW Output		 MVAR(Gross) at 	 MW(Gross) (1)

Maximum Leading Reactive at current Gross Dependable MW Output			 MVAR(Gross) at 	 MW (Gross) (1)

Maximum Leading Reactive at current Gross Low Sustained Limit MW Output	_______ MVAR(Gross) at 	 MW(Gross) (1)

* Defined Test:

 Coordinated Test

 Non-Coordinated Test

*Test Performed:			*Location at which data observed (specify all that apply):

 Maximum Leading Reactive		 Generator Terminals (preferred)

 Maximum Lagging Reactive		 High Voltage side of Generator Step-Up (GSU) Transformer

 Other (specify location):

TESTED REACTIVE CAPABILITY

*Generator Gross Reactive (MVAR): (+/-) _____ (2)

*Auxiliary Reactive Load (MVAR): _____ (3)	 Observed     Calculated

*Net Reactive to the Transmission System (MVAR): (+/-) _____ (5)   Observed     Calculated

*Net Generator Reactive (MVAR): _______ (6)   Observed     Calculated

TEST CONDITIONS:

*Start Time: ________________	*Stop Time: ______________

*Generator Gross Generation (MW): _____ (7)

*Net Dependable Unit Generation (MW): _____ (8)

*Auxiliary Load (MW): _____ (4)		*Generator Terminal Power Factor: _____

*Transmission Bus Voltage (kV): _____ (9)	*Nominal Transmission Bus Voltage (kV): _____

*Generator Terminal Voltage (kV): _____	Auxiliary Bus Voltage (kV): _____ (10)

Ambient Air Temperature (°F): _____ (10)

*Generator Hydrogen Pressure, if applicable (psig): _____ (11)

*Generator Step Up transformer tap setting: _____Ratio: HV _____kV/ LV ______kV (12)

*Abnormal Conditions at Time of Test: (13)

*Briefly describe factors that limited reactive capability during test:

 Maximum Generator Voltage with Auxiliary loads		 Steady State Stability Limit

 Maximum Generator Voltage without Auxiliary loads	 Maximum Gross MW capability

 Minimum Generator Voltage with Auxiliary loads		 Minimum Gross MW capability

 Minimum Generator Voltage without Auxiliary loads	 Minimum Excitation Limiter

 Main transformer capability plus Auxiliary loads		 Loss of Field Relay

 Other:

Submittal

*Resource Entity Representative:

*QSE Representative:

*QSE/Resource Entity Contact Phone Number:

Email Address:

*Date submitted to ERCOT Rep.:

Notes:	Maximum Leading and Maximum Lagging tests may be conducted at different times of the year.

Metered Auxiliary

Load

Generator Terminal

(Gross)

MVAR    (2)

MW        (7)

(5)  Location Where Net Reactive to the

Transmission System is to be determined.

Generator Step Up Transformer

(6)  Location Where Net Generator Reactive is to be determined.

MVAR   (3)

MW       (4)

Load Host

Consumption

Low Side (14)

Transmission Bus

(10) Auxiliary

Bus Voltage

G

W

W

W

(9)  Transmission Bus Voltage

Load Host

Consumption

High Side (14)

Notes

(1)	These quantities are taken directly from the Corrected Machine Capability Curve.  The MVAR reactive maximum lagging value is the expected output at the generator terminal (gross output) with the generating unit at the Gross Dependable MW Output.  This is the Gross equivalent of the Net Dependable Output.  The MVAR reactive maximum leading value is the expected output at the generator terminal (gross output) with the generating unit at the Gross Low Sustained Limit MW output.  This is the Gross equivalent of the Net Low Sustained Limit.  The Maximum Lagging Reactive at current Gross Low Sustained Limit and Maximum Leading Reactive at current Gross Low Sustained Limit are used for curve validation only.

(2)	Metered reactive at the generator’s terminals.

(3)	Auxiliary Reactive Load (Load only associated with Generator such as fans, boiler pumps etc.).

(4)	Metered Auxiliary Real Load (Load only associated with Generator).

(5)	Observed – metered reactive on the high side of the generator step up transformer to the transmission system (Show leading reactive value as a negative (-) number).

Calculated - (+/-) metered reactive at the generator’s terminals minus metered Auxiliary Reactive consumption minus generator step up transformer reactive losses minus Load host reactive consumption (Load host does not apply to most generators but only pertains to generators with self serve load).

(6)	Observed - (+/-) as metered, Gross generator reactive minus metered Auxiliary Reactive consumption (Show leading reactive value as a negative (-) number).
Calculated - (+/-) metered net reactive to the transmission system minus generator step up transformer reactive losses minus Load host reactive consumption (Load host does not apply to most generators but only pertains to generators with self serve load),

(7)	Metered at the generator terminals.

(8)	Most current tested value on record at ERCOT,

(9)	Required for Coordinated Test.

(10)	(if limiting).

(11)	PSIG can be determined from PSIA by subtracting 14.7 from the PSIA gauge reading.

(12)	Actual tap setting – not nominal tap setting.

(13)	Describe fully.

(14)	Load Host consumption exists on either the low side or the high side of the step up transformer but typically not both.