## Slide 1: BAL-001-TRE-01
ERCOT CPS2 R2 Waiver
Regional Variance
April 16, 2009
Sydney Niemeyer

## Slide 2: Work Product
Draft standard consistent with SAR on which it was based.
  include requirements concerning frequency response contained in the ERCOT Protocols, section 5
  include Requirements, Measures, and Levels of Non-Compliance sections
  FERC determined that the minimum frequency response needed for reliability and requiring appropriate generators to have specific governor droop to be a more stringent practice than requirement R2 in BAL-001-0

## Slide 3: Workshop March 31st
Drafting Team met with ERCOT Market Participants and provided detailed information on the proposed draft variance.
  Held halfway through 30 day comment period.
Tools in the form of Excel Spreadsheets provided with Draft posting for use in the evaluation of Resources to the draft variance.

## Slide 4: Goals of the Variance
Reliability Impact.
  Improved frequency profile will increase probability that frequency will be near 60.000 Hz when a perturbation occurs.
  Improved frequency stability even with an increase in variable generation.
  Support for Voltage and Automatic Voltage Regulators by supplying appropriate energy delivery during perturbations.

## Slide 5: Goals of the Variance, continued
If an electrical island forms within the ERCOT Interconnection, this variance will provide the best probability of both islands surviving.
  Resources, through correct frequency response, will know immediately the correct action to take to balance the generation to the demand of each island.

## Slide 8: Interconnection Changed in Source of Frequency Response after 2001
Retirement of many conventional steam units.
  Many had mechanical fly-ball governors that had various amounts of deadband.
  These Resources provided linear frequency response once the deadband was crossed.
Installation of many Combined Cycle Units.
  All had electronic/digital governors with deadband capabilities.
  Most deadbands were set at the maximum allowed setting of +/-0.036 Hz.
  To meet the 5% droop performance characteristic they were encouraged to have non-linear response to overcome deadband region.

## Slide 10
Existing +/-0.036 Hz allowable deadband
ERCOT ACE +/- 237.6 MW
CPS2 10 minute average ACE Limit = 143.2 MW (0.0217 Hz)
Due to the small amount of frequency response within the deadband, MW needed in Resource movement to return to schedule frequency is much less than ERCOT ACE.

## Slide 12
ERCOT ACE +/- 110 MW
Proposed +/-0.0166 Hz allowable deadband
CPS2 10 minute average ACE Limit = 143.2 MW (0.0217 Hz)
Smaller deadband on Resources provides resistance to frequency change sooner. This results in three things 1) Overall frequency response needed from the Resource is less. 2) ERCOT ACE more closely represents the MW needed to return frequency to schedule. 3) Greater frequency stability.

## Slide 13
Droop Characteristic of Resource with 5% Droop setting and +/-0.036 Hz Deadband

## Slide 14
Droop Characteristic of Resource with 5% Droop setting and +/- 0.0166 Hz Deadband

## Slide 15: Draft Regional Variance Future Direction
Drafting team will meet on May 4 to begin the process of responding to the Industry comments received.
Modify Draft Variance based on Industry guidance.
Request second posting for comments once modifications are complete and have team consensus.

## Slide 16: Questions?
Sydney L. Niemeyer
NRG Texas Power
713-795-6108
Sydney.niemeyer@nrgenergy.com