## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  | Summary of Key Data points | Value
File Description: Cont_ Jewett to Singleton and Jewett to Singleton OL_ Gibbons to Singleton_ckt_75
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K27 |  | Number of units | 645
|  |  | Dec PTDF cutoff point | 254
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  | Dec PTDF cutoff unit | FRNDDRCS
|  |  | Dec 10% unit | CALFREST_2G
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  | Dec max cumltv zone impact - cumltv zone share | 0.02249
|  |  | Dec max cumltv zone impact - cumltv zone share pt | 87
Step 5 | Enter Dennis' file name into cell K27 |  | Dec max cumltv zone impact - cumltv zone share unit | NTHLK3_G
|  |  | North Zonal weighted AWGSF | 0.13101
Step 6 | click the step one button |  | Houston Zonal weighted AWGSF | -0.16396
|  |  | Inc PTDF cutoff point | 391
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  | Inc PTDF cutoff unit | FTR_CN4_5095
| X6:X30, or to the end of the selected list. |  | Inc 10% unit | CBY_GN1_1
|  |  | Inc max cumltv zone impact - cumltv zone share | 0.13835
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  | Inc max cumltv zone impact - cumltv zone share pt | 167
| of the formulas in columns L:V (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  | Inc max cumltv zone impact - cumltv zone share unit | CBE_ST34
| If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct leng |  | North Zonal weighted AWGSF | 0.13101
| It is only necessary to match the Distributed Slack - Dec worksheet. |  | Houston Zonal weighted AWGSF | -0.16396
|  |  | Min of zone correlation | -0.06115
Step 9 | Click the step 2 button |  | Bounary gen in Houston Zone | 52.0513
| The last file saved will still be open, yopu will need to close this file. |  | Bounary gen in soucre zone as % of line | 3.783%
| This sheet willno longer be open. |  | Bounary gen in North Zone | 0
|  |  | Bounary gen in soucre zone as % of line | 0
|  |  | OL element line rating | 1376
|  |  | North Zonal weighted AWGSF | 0.13101
|  | NH_043009automation.xls | Houston Zonal weighted AWGSF | -0.16396
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ Jewett to Singleton and Jewett to Singleton OL_ Gibbons to Singleton_ckt_75 |  | i_PTDF_DEC_pt | 254 |  | NTHLK3_G | Unit at max
990 | GIBN_CREK_G1 | 1 | North | YES | 0.25699 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.42094 | 0 | 463 | 118.9841 | 463 |  |  | 0.42094 | 194.8964 | 0.011219 | 0.015767 |  |  | i_10pctunit | 18 |  | 87 | # units @ max
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.23292 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.39688 | 32 | 32 | 7.4535 | 32 |  |  | 0.39688 | 12.7001 | 0.011994 | 0.016794 |  |  | # units | 645 |  | 0.02249 | delta max
32886 | BRYN_ATKINS3 | MB | North | YES | 0.22931 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0 | 0.011994 | 0.016794 | [5 empty] | Delta
32887 | BRYN_ATKINS6 | MB | North | YES | 0.22931 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0 | 0.011994 | 0.016794 | Weighted Shift Factors |  |  |  | 1 | 0.0045482
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.22931 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.39327 | 17 | 17 | 3.8983 | 17 |  |  | 0.39327 | 6.6856 | 0.012406 | 0.017335 | North | 0.13101 |  |  | 2 | 0.0048003
32890 | BRYN_ATKINS4 | MB | North | YES | 0.22931 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0 | 0.012406 | 0.017335 | Houston | -0.16396 |  |  | 3 | 0.0048003
32891 | BRYN_ATKINS5 | MB | North | YES | 0.22931 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0 | 0.012406 | 0.017335 |  |  |  |  | 4 | 0.0048003
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.22242 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.38638 | 48 | 48 | 10.6764 | 48 |  |  | 0.38638 | 18.5463 | 0.013569 | 0.018835 |  |  |  |  | 5 | 0.0049292
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.22242 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.38638 | 46 | 46 | 10.2315 | 46 |  |  | 0.38638 | 17.7735 | 0.014683 | 0.020273 |  |  |  |  | 6 | 0.0049292
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.22242 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.38638 | 105 | 105 | 23.3545 | 105 |  |  | 0.38638 | 40.5701 | 0.017228 | 0.023555 |  |  |  |  | 7 | 0.0049292
39960 | TNTNPONE_18 | 1 | North | YES | 0.1953 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.35926 | 0 | 152.3 | 29.7448 | 152.3 |  |  | 0.35926 | 54.7155 | 0.020918 | 0.027982 |  |  |  |  | 8 | 0.0052665
39970 | TNTNPONE_28 | 1 | North | YES | 0.1953 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.35926 | 0 | 153 | 29.8815 | 153 |  |  | 0.35926 | 54.967 | 0.024625 | 0.032428 |  |  |  |  | 9 | 0.0055898
48721 | LEG_1___1 | 1 | North | YES | 0.17253 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.33648 | 0 | 827 | 142.6798 | 827 |  |  | 0.33648 | 278.2727 | 0.044663 | 0.05494 |  |  |  |  | 10 | 0.0063277
48722 | LEG_2___2 | 2 | North | YES | 0.17253 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.33648 | 0 | 819 | 141.2996 | 819 |  |  | 0.33648 | 275.5808 | 0.064508 | 0.077234 |  |  |  |  | 11 | 0.0070638
3381 | BBRN_1G | 1 | North | YES | 0.15256 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.31652 | 0 | 618 | 94.2839 | 618 |  |  | 0.31652 | 195.6097 | 0.079482 | 0.093059 |  |  |  |  | 12 | 0.0078033
3382 | BBRN_2G | 2 | North | YES | 0.15256 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.31652 | 0 | 589 | 89.8596 | 589 |  |  | 0.31652 | 186.4306 | 0.093754 | 0.10814 |  |  |  |  | 13 | 0.010277
13131 | CALFREST_1G | 1 | North | YES | 0.15145 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.31541 | 150.7 | 150.7 | 22.8232 | 150.7 |  |  | 0.31541 | 47.5316 | 0.097405 | 0.11199 |  |  |  |  | 14 | 0.012726
13132 | CALFREST_2G | 2 | North | YES | 0.15145 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.31541 | 151 | 151 | 22.8686 | 151 |  |  | 0.31541 | 47.6262 | 0.10106 | 0.11584 |  |  |  |  | 15 | 0.013577
13133 | CALFREST_3G | 3 | North | YES | 0.15145 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.31541 | 177.4 | 177.4 | 26.8669 | 177.4 |  |  | 0.31541 | 55.9529 | 0.10536 | 0.12037 |  |  |  |  | 16 | 0.014387
13134 | CALFREST_4G | 4 | North | YES | 0.15119 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.31515 | 151.5 | 151.5 | 22.9053 | 151.5 |  |  | 0.31515 | 47.7448 | 0.10903 | 0.12423 |  |  |  |  | 17 | 0.014581
13135 | CALFREST_5G | 5 | North | YES | 0.15119 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.31515 | 152.3 | 152.3 | 23.0262 | 152.3 |  |  | 0.31515 | 47.997 | 0.11272 | 0.12811 |  |  |  |  | 18 | 0.014775
13136 | CALFREST_6G | 6 | North | YES | 0.15119 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.31515 | 177.5 | 177.5 | 26.8362 | 177.5 |  |  | 0.31515 | 55.9387 | 0.11702 | 0.13264 |  |  |  |  | 19 | 0.015003
3107 | STRYKER_1G | 1 | North | YES | 0.14652 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.31048 | 182 | 182 | 26.6668 | 182 |  |  | 0.31048 | 56.5071 | 0.12143 | 0.13721 |  |  |  |  | 20 | 0.015194
3108 | STRYKER_2G | 2 | North | YES | 0.14652 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.31048 | 484 | 484 | 70.9162 | 484 |  |  | 0.31048 | 150.2716 | 0.13316 | 0.14936 |  |  |  |  | 21 | 0.015387
3309 | ASPN_G | 1 | North | YES | 0.1463 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.31026 | 50 | 50 | 7.3151 | 50 |  |  | 0.31026 | 15.5129 | 0.13437 | 0.15062 |  |  |  |  | 22 | 0.015612
3348 | CHAMPION_1G | MB | North | YES | 0.14625 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0 | 0.13437 | 0.15062 |  |  |  |  | 23 | 0.015773
13116 | TGATEWAY_1G | 1 | North | YES | 0.14572 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.30967 | 151 | 151 | 22.003 | 151 |  |  | 0.30967 | 46.7605 | 0.13803 | 0.1544 |  |  |  |  | 24 | 0.016202
13117 | TGATEWAY_2G | 2 | North | YES | 0.14572 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.30967 | 130 | 130 | 18.9429 | 130 |  |  | 0.30967 | 40.2574 | 0.14118 | 0.15766 |  |  |  |  | 25 | 0.016246
13118 | TGATEWAY_3G | 3 | North | YES | 0.14572 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.30967 | 148 | 148 | 21.5658 | 148 |  |  | 0.30967 | 45.8315 | 0.14477 | 0.16137 |  |  |  |  | 26 | 0.016246
13119 | TGATEWAY_4G | 4 | North | YES | 0.14572 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.30967 | 399 | 399 | 58.1403 | 399 |  |  | 0.30967 | 123.5593 | 0.15444 | 0.17136 |  |  |  |  | 27 | 0.01637
3097 | MARTLAKE_1G | 1 | North | YES | 0.14521 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 790 | 114.7167 | 790 |  |  | 0.30917 | 244.2431 | 0.17358 | 0.19112 |  |  |  |  | 28 | 0.016477
3098 | MARTLAKE_2G | 2 | North | YES | 0.14521 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 795 | 115.4427 | 795 |  |  | 0.30917 | 245.789 | 0.19284 | 0.211 |  |  |  |  | 29 | 0.016598
3099 | MARTLAKE_3G | 3 | North | YES | 0.14521 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 804 | 116.7496 | 804 |  |  | 0.30917 | 248.5715 | 0.21232 | 0.23111 |  |  |  |  | 30 | 0.016926
3126 | TRINIDAD_6G | 1 | North | YES | 0.14175 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.30571 | 224 | 224 | 31.7531 | 224 |  |  | 0.30571 | 68.4796 | 0.21775 | 0.23665 |  |  |  |  | 31 | 0.017543
12411 | FPLEFR1A_G | 1 | North | YES | 0.14146 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.30542 | 161 | 161 | 22.7747 | 161 |  |  | 0.30542 | 49.1719 | 0.22165 | 0.24063 |  |  |  |  | 32 | 0.018164
12412 | FPLEFR1B_G | 2 | North | YES | 0.14146 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.30542 | 164 | 164 | 23.1991 | 164 |  |  | 0.30542 | 50.0881 | 0.22562 | 0.24468 |  |  |  |  | 33 | 0.018792
12413 | FPLEFR1C_G | 3 | North | YES | 0.14146 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.30542 | 164 | 164 | 23.1991 | 164 |  |  | 0.30542 | 50.0881 | 0.2296 | 0.24874 |  |  |  |  | 34 | 0.018905
12414 | FPLEFR1S_G | 4 | North | YES | 0.14146 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.30542 | 414 | 414 | 58.5636 | 414 |  |  | 0.30542 | 126.442 | 0.23963 | 0.25896 |  |  |  |  | 35 | 0.018981
12421 | FPLEFR2A_G | 1 | North | YES | 0.14146 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.30542 | 162 | 162 | 22.9162 | 162 |  |  | 0.30542 | 49.4773 | 0.24355 | 0.26297 |  |  |  |  | 36 | 0.01906
12422 | FPLEFR2B_G | 2 | North | YES | 0.14146 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.30542 | 161 | 161 | 22.7747 | 161 |  |  | 0.30542 | 49.1719 | 0.24746 | 0.26695 |  |  |  |  | 37 | 0.019138
12423 | FPLEFR2C_G | 3 | North | YES | 0.14146 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.30542 | 163 | 163 | 23.0577 | 163 |  |  | 0.30542 | 49.7827 | 0.2514 | 0.27097 |  |  |  |  | 38 | 0.019336
12424 | FPLEFR2S_G | 4 | North | YES | 0.14146 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.30542 | 415 | 415 | 58.7051 | 415 |  |  | 0.30542 | 126.7474 | 0.26146 | 0.28123 |  |  |  |  | 39 | 0.019413
2451 | LKHB1_G | 1 | North | YES | 0.14076 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.30471 | 391 | 391 | 55.036 | 391 |  |  | 0.30471 | 119.1434 | 0.27093 | 0.29086 |  |  |  |  | 40 | 0.01949
2452 | LKHB2_G | 2 | North | YES | 0.14076 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.30471 | 516 | 516 | 72.6306 | 516 |  |  | 0.30471 | 157.2327 | 0.28344 | 0.30358 |  |  |  |  | 41 | 0.019568
12440 | PARKD_1SVC8 | 1 | North | YES | 0.14071 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30467 | 0 | 0 | 0 | 0 |  |  | 0.30467 | 0 | 0.28344 | 0.30358 |  |  |  |  | 42 | 0.019766
12449 | PARKD_2SVC8 | 1 | North | YES | 0.14071 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30467 | 0 | 0 | 0 | 0 |  |  | 0.30467 | 0 | 0.28344 | 0.30358 |  |  |  |  | 43 | 0.01993
948 | STEAM1 | 1 | North | YES | 0.14031 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.30427 | 20 | 20 | 2.8063 | 20 |  |  | 0.30427 | 6.0855 | 0.28392 | 0.30408 |  |  |  |  | 44 | 0.020147
949 | STEAM2 | 1 | North | YES | 0.14031 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.30427 | 26 | 26 | 3.6482 | 26 |  |  | 0.30427 | 7.9111 | 0.28455 | 0.30472 |  |  |  |  | 45 | 0.020147
950 | STEAM3 | 1 | North | YES | 0.14031 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.30427 | 42 | 42 | 5.8932 | 42 |  |  | 0.30427 | 12.7794 | 0.28557 | 0.30575 |  |  |  |  | 46 | 0.020147
837 | NEWMAN_G5 | 1 | North | YES | 0.14016 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.30412 | 40 | 40 | 5.6063 | 40 |  |  | 0.30412 | 12.1646 | 0.28654 | 0.30673 |  |  |  |  | 47 | 0.020155
842 | OLINGER_G1 | 1 | North | YES | 0.14013 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.30409 | 79 | 79 | 11.0701 | 79 |  |  | 0.30409 | 24.0228 | 0.28845 | 0.30868 |  |  |  |  | 48 | 0.020165
843 | OLINGER_G2 | 1 | North | YES | 0.14013 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.30409 | 110 | 110 | 15.4141 | 110 |  |  | 0.30409 | 33.4494 | 0.29112 | 0.31138 |  |  |  |  | 49 | 0.020181
844 | OLINGER_G3 | 1 | North | YES | 0.14013 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.30409 | 150 | 150 | 21.0192 | 150 |  |  | 0.30409 | 45.6128 | 0.29475 | 0.31507 |  |  |  |  | 50 | 0.020196
845 | OLINGER_G4 | 1 | North | YES | 0.14013 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.30409 | 76 | 76 | 10.6497 | 76 |  |  | 0.30409 | 23.1105 | 0.29659 | 0.31694 |  |  |  |  | 51 | 0.020225
1701 | MOSES_1G | 1 | North | YES | 0.13983 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 558 | 78.0279 | 558 |  |  | 0.30379 | 169.5162 | 0.31011 | 0.33066 |  |  |  |  | 52 | 0.020266
1702 | MOSES_2G | 2 | North | YES | 0.13983 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 579 | 80.9645 | 579 |  |  | 0.30379 | 175.8959 | 0.32414 | 0.34489 |  |  |  |  | 53 | 0.020322
1703 | MOSES_3G | 3 | North | YES | 0.13983 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 808 | 112.9867 | 808 |  |  | 0.30379 | 245.4643 | 0.34372 | 0.36474 |  |  |  |  | 54 | 0.02035
5925 | DCEAST | EQ | North | YES | 0.13983 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.30379 | 0 | 0 | 0 | 0 |  |  | 0.30379 | 0 | 0.34372 | 0.36474 |  |  |  |  | 55 | 0.020543
1675 | PEC_1G | 1 | North | YES | 0.13969 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0 | 0.34372 | 0.36474 |  |  |  |  | 56 | 0.020743
1676 | PEC_2G | 2 | North | YES | 0.13969 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0 | 0.34372 | 0.36474 |  |  |  |  | 57 | 0.021023
1677 | PEC_3G | 3 | North | YES | 0.13969 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0 | 0.34372 | 0.36474 |  |  |  |  | 58 | 0.021023
1678 | LAMARPWR_1G | 1 | North | YES | 0.1396 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.30356 | 160 | 160 | 22.3365 | 160 |  |  | 0.30356 | 48.5697 | 0.3476 | 0.36867 |  |  |  |  | 59 | 0.021023
1679 | LAMARPWR_2G | 2 | North | YES | 0.1396 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30356 | 156 | 156 | 21.7781 | 156 |  |  | 0.30356 | 47.3554 | 0.35138 | 0.3725 |  |  |  |  | 60 | 0.021023
1680 | LAMARPWR_3G | 3 | North | YES | 0.1396 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.30356 | 196 | 196 | 27.3622 | 196 |  |  | 0.30356 | 59.4979 | 0.35613 | 0.37732 |  |  |  |  | 61 | 0.021023
1681 | LAMARPWR_4G | 4 | North | YES | 0.1396 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30356 | 156 | 156 | 21.7781 | 156 |  |  | 0.30356 | 47.3554 | 0.35991 | 0.38115 |  |  |  |  | 62 | 0.021075
1682 | LAMARPWR_5G | 5 | North | YES | 0.1396 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.30356 | 157 | 157 | 21.9177 | 157 |  |  | 0.30356 | 47.659 | 0.36371 | 0.385 |  |  |  |  | 63 | 0.021126
1683 | LAMARPWR_6G | 6 | North | YES | 0.1396 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.30356 | 198 | 198 | 27.6414 | 198 |  |  | 0.30356 | 60.105 | 0.36851 | 0.38987 |  |  |  |  | 64 | 0.021191
1689 | VALLEY_3G | 3 | North | YES | 0.13947 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.30343 | 375 | 375 | 52.3028 | 375 |  |  | 0.30343 | 113.7868 | 0.3776 | 0.39907 |  |  |  |  | 65 | 0.021242
11691 | KMICHICT1_G | 1 | North | YES | 0.13947 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30343 | 144 | 144 | 20.0843 | 144 |  |  | 0.30343 | 43.6941 | 0.38108 | 0.40261 |  |  |  |  | 66 | 0.021293
11692 | KMICHICT2_G | 2 | North | YES | 0.13947 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.30343 | 146 | 146 | 20.3632 | 146 |  |  | 0.30343 | 44.301 | 0.38462 | 0.40619 |  |  |  |  | 67 | 0.021358
11693 | KMICHIST3_G | 3 | North | YES | 0.13947 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.30343 | 312 | 312 | 43.5159 | 312 |  |  | 0.30343 | 94.6706 | 0.39218 | 0.41385 |  |  |  |  | 68 | 0.021477
11694 | KMICHICT4_G | 4 | North | YES | 0.13947 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30343 | 144 | 144 | 20.0843 | 144 |  |  | 0.30343 | 43.6941 | 0.39567 | 0.41738 |  |  |  |  | 69 | 0.021522
11695 | KMICHICT5_G | 5 | North | YES | 0.13947 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.30343 | 148 | 148 | 20.6422 | 148 |  |  | 0.30343 | 44.9079 | 0.39926 | 0.42102 |  |  |  |  | 70 | 0.021569
11696 | KMICHIST6_G | 6 | North | YES | 0.13947 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.30343 | 310 | 310 | 43.2369 | 310 |  |  | 0.30343 | 94.0638 | 0.40677 | 0.42863 |  |  |  |  | 71 | 0.021667
2413 | MTCK6_G | 6 | North | YES | 0.13923 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.30319 | 118 | 118 | 16.4289 | 118 |  |  | 0.30319 | 35.7759 | 0.40963 | 0.43152 |  |  |  |  | 72 | 0.021713
2414 | MTCK7_G | 7 | North | YES | 0.13923 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.30319 | 115 | 115 | 16.0112 | 115 |  |  | 0.30319 | 34.8663 | 0.41241 | 0.43434 |  |  |  |  | 73 | 0.02176
2417 | MTCK8_G | 8 | North | YES | 0.13923 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.30319 | 556 | 556 | 77.4108 | 556 |  |  | 0.30319 | 168.5711 | 0.42589 | 0.44798 |  |  |  |  | 74 | 0.021858
1687 | VALLEY_1G | 1 | North | YES | 0.13918 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.30314 | 170 | 170 | 23.6606 | 170 |  |  | 0.30314 | 51.5334 | 0.43001 | 0.45215 |  |  |  |  | 75 | 0.021893
1688 | VALLEY_2G | 2 | North | YES | 0.13918 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.30314 | 527 | 527 | 73.3479 | 527 |  |  | 0.30314 | 159.7535 | 0.44277 | 0.46507 |  |  |  |  | 76 | 0.021927
6948 | DENISNDM | 1 | North | YES | 0.13895 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.30291 | 0 | 0 | 0 | 0 |  |  | 0.30291 | 0 | 0.44277 | 0.46507 |  |  |  |  | 77 | 0.022093
6948 | DENISNDM | 2 | North | YES | 0.13895 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.30291 | 0 | 0 | 0 | 0 |  |  | 0.30291 | 0 | 0.44277 | 0.46507 |  |  |  |  | 78 | 0.022142
2371 | COLLIN_1G | MB | North | YES | 0.13823 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.30219 | 0 | 0 | 0 | 0 |  |  | 0.30219 | 0 | 0.44277 | 0.46507 |  |  |  |  | 79 | 0.022297
12322 | ENNSTRAC_1G | 1 | North | YES | 0.13803 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.30199 | 196 | 196 | 27.0537 | 196 |  |  | 0.30199 | 59.1894 | 0.44752 | 0.46986 |  |  |  |  | 80 | 0.022297
12323 | ENNSTRAC_2G | 2 | North | YES | 0.13803 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.30199 | 116 | 116 | 16.0114 | 116 |  |  | 0.30199 | 35.0304 | 0.45033 | 0.47269 |  |  |  |  | 81 | 0.022297
2381 | NTHLK1_G | 1 | North | YES | 0.13798 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.30194 | 156 | 156 | 21.5257 | 156 |  |  | 0.30194 | 47.103 | 0.45411 | 0.4765 |  |  |  |  | 82 | 0.022297
2382 | NTHLK2_G | 2 | North | YES | 0.13798 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.30194 | 181 | 181 | 24.9753 | 181 |  |  | 0.30194 | 54.6516 | 0.4585 | 0.48093 |  |  |  |  | 83 | 0.022336
2383 | NTHLK3_G | 3 | North | YES | 0.13798 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.30194 | 329 | 329 | 45.3971 | 329 |  |  | 0.30194 | 99.3391 | 0.46647 | 0.48896 |  |  |  |  | 84 | 0.022359
923 | SPENCER_G4 | 1 | North | YES | 0.13553 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.29948 | 61 | 61 | 8.267 | 61 |  |  | 0.29948 | 18.2684 | 0.46795 | 0.49044 |  |  |  |  | 85 | 0.02239
924 | SPENCER_G5 | 1 | North | YES | 0.13553 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.29948 | 66 | 66 | 8.9446 | 66 |  |  | 0.29948 | 19.7658 | 0.46955 | 0.49204 |  |  |  |  | 86 | 0.022426
1948 | HANDLEY_4G | 4 | North | YES | 0.13446 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.29842 | 435 | 435 | 58.4914 | 435 |  |  | 0.29842 | 129.8129 | 0.48009 | 0.50254 |  |  |  |  | 87 | 0.02249
728 | WOLFRIDGE801 | 1 | North | YES | 0.13423 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.29819 | 0 | 112.5 | 15.1009 | 112.5 |  |  | 0.29819 | 33.5461 | 0.48281 | 0.50525 |  |  |  |  | 88 | 0.02249
1947 | HANDLEY_3G | 3 | North | YES | 0.13422 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.29818 | 395 | 395 | 53.0173 | 395 |  |  | 0.29818 | 117.7805 | 0.49239 | 0.51478 |  |  |  |  | 89 | 0.02249
1949 | HANDLEY_5G | 5 | North | YES | 0.13422 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.29818 | 435 | 435 | 58.3861 | 435 |  |  | 0.29818 | 129.7077 | 0.50293 | 0.52528 |  |  |  |  | 90 | 0.022451
1941 | MDLTHELP_1G | 1 | North | YES | 0.13411 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.29807 | 216.4 | 216.4 | 29.0221 | 216.4 |  |  | 0.29807 | 64.5025 | 0.50817 | 0.53049 |  |  |  |  | 91 | 0.022439
1942 | MDLTHELP_2G | 2 | North | YES | 0.13411 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.29807 | 216.1 | 216.1 | 28.9818 | 216.1 |  |  | 0.29807 | 64.413 | 0.51341 | 0.5357 |  |  |  |  | 92 | 0.022397
1861 | EAGLEMNT_1G | MB | North | YES | 0.13366 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0 | 0.51341 | 0.5357 |  |  |  |  | 93 | 0.02235
1862 | EAGLEMNT_2G | MB | North | YES | 0.13366 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0 | 0.51341 | 0.5357 |  |  |  |  | 94 | 0.022324
1863 | EAGLEMNT_3G | MB | North | YES | 0.13366 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0 | 0.51341 | 0.5357 |  |  |  |  | 95 | 0.022299
1937 | MDLTHELP_5G | 5 | North | YES | 0.13269 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.29665 | 224 | 224 | 29.723 | 224 |  |  | 0.29665 | 66.4495 | 0.51883 | 0.54108 |  |  |  |  | 96 | 0.022299
1938 | MDLTHELP_6G | 6 | North | YES | 0.13269 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.29665 | 226 | 226 | 29.9884 | 226 |  |  | 0.29665 | 67.0428 | 0.52431 | 0.5465 |  |  |  |  | 97 | 0.022299
1943 | MDLTHELP_3G | 3 | North | YES | 0.13269 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.29665 | 212 | 212 | 28.1307 | 212 |  |  | 0.29665 | 62.8897 | 0.52945 | 0.55159 |  |  |  |  | 98 | 0.022299
1944 | MDLTHELP_4G | 4 | North | YES | 0.13269 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.29665 | 211 | 211 | 27.998 | 211 |  |  | 0.29665 | 62.593 | 0.53456 | 0.55666 |  |  |  |  | 99 | 0.022247
580 | JCKCNTY801 | 1 | North | YES | 0.1323 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.29626 | 288 | 288 | 38.1024 | 288 |  |  | 0.29626 | 85.3222 | 0.54154 | 0.56356 |  |  |  |  | 100 | 0.022195
581 | JCKCNTY802 | 2 | North | YES | 0.1323 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.29626 | 147 | 147 | 19.4481 | 147 |  |  | 0.29626 | 43.5499 | 0.5451 | 0.56708 |  |  |  |  | 101 | 0.022146
582 | JCKCNTY803 | 3 | North | YES | 0.1323 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.29626 | 147 | 147 | 19.4481 | 147 |  |  | 0.29626 | 43.5499 | 0.54866 | 0.5706 |  |  |  |  | 102 | 0.022097
1889 | DECRDOVA_1G | 1 | North | YES | 0.13182 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.29578 | 779 | 779 | 102.6917 | 779 |  |  | 0.29578 | 230.4146 | 0.56754 | 0.58924 |  |  |  |  | 103 | 0.022021
1877 | WLFHOLW_1G | 1 | North | YES | 0.13156 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.29552 | 217.3 | 217.3 | 28.5884 | 217.3 |  |  | 0.29552 | 64.2164 | 0.5728 | 0.59444 |  |  |  |  | 104 | 0.021982
1878 | WLFHOLW_2G | 2 | North | YES | 0.13156 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.29552 | 215.7 | 215.7 | 28.3779 | 215.7 |  |  | 0.29552 | 63.7436 | 0.57803 | 0.5996 |  |  |  |  | 105 | 0.021944
1879 | WLFHOLW_3G | 3 | North | YES | 0.13156 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.29552 | 272.4 | 272.4 | 35.8375 | 272.4 |  |  | 0.29552 | 80.4995 | 0.58463 | 0.60611 |  |  |  |  | 106 | 0.021708
1453 | WCPWRCO_1G | 1 | North | YES | 0.13141 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.29537 | 204 | 204 | 26.808 | 204 |  |  | 0.29537 | 60.2554 | 0.58957 | 0.61098 |  |  |  |  | 107 | 0.021638
1454 | WCPWRCO_2G | 2 | North | YES | 0.13141 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.29537 | 204 | 204 | 26.808 | 204 |  |  | 0.29537 | 60.2554 | 0.59451 | 0.61586 |  |  |  |  | 108 | 0.021569
1455 | WCPWRCO_3G | 3 | North | YES | 0.13141 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.29537 | 242 | 242 | 31.8017 | 242 |  |  | 0.29537 | 71.4794 | 0.60038 | 0.62164 |  |  |  |  | 109 | 0.02148
1898 | COMCHEPK_1G | 1 | North | YES | 0.1312 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.29515 | 0 | 0 | 0 | 0 |  |  | 0.29515 | 0 | 0.60038 | 0.62164 |  |  |  |  | 110 | 0.021412
1899 | COMCHEPK_2G | 2 | North | YES | 0.1312 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.29515 | 0 | 0 | 0 | 0 |  |  | 0.29515 | 0 | 0.60038 | 0.62164 |  |  |  |  | 111 | 0.021344
503 | NTHTEXAS01 | 1 | North | YES | 0.13058 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.29454 | 18 | 18 | 2.3505 | 18 |  |  | 0.29454 | 5.3017 | 0.60081 | 0.62207 |  |  |  |  | 112 | 0.021263
504 | NTHTEXAS02 | 2 | North | YES | 0.13058 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.29454 | 18 | 18 | 2.3505 | 18 |  |  | 0.29454 | 5.3017 | 0.60125 | 0.6225 |  |  |  |  | 113 | 0.021263
505 | NTHTEXAS03 | 3 | North | YES | 0.13058 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.29454 | 38 | 38 | 4.9622 | 38 |  |  | 0.29454 | 11.1925 | 0.60217 | 0.6234 |  |  |  |  | 114 | 0.021263
1892 | DECRDOVA_2G | A | North | YES | 0.13052 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.29448 | 70 | 70 | 9.1363 | 70 |  |  | 0.29448 | 20.6133 | 0.60387 | 0.62507 |  |  |  |  | 115 | 0.021255
1893 | DECRDOVA_3G | B | North | YES | 0.13052 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.29448 | 69 | 69 | 9.0057 | 69 |  |  | 0.29448 | 20.3188 | 0.60554 | 0.62671 |  |  |  |  | 116 | 0.021248
1894 | DECRDOVA_4G | C | North | YES | 0.13052 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.29448 | 69 | 69 | 9.0057 | 69 |  |  | 0.29448 | 20.3188 | 0.60721 | 0.62836 |  |  |  |  | 117 | 0.021233
1895 | DECRDOVA_5G | D | North | YES | 0.13052 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.29448 | 68 | 68 | 8.8752 | 68 |  |  | 0.29448 | 20.0243 | 0.60886 | 0.62998 |  |  |  |  | 118 | 0.021204
366 | JNSNCNTY802 | 1 | North | YES | 0.12969 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.29365 | 0 | 0 | 0 | 0 |  |  | 0.29365 | 0 | 0.60886 | 0.62998 |  |  |  |  | 119 | 0.021176
367 | JNSNCNTY802 | 2 | North | YES | 0.12969 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.29365 | 0 | 0 | 0 | 0 |  |  | 0.29365 | 0 | 0.60886 | 0.62998 |  |  |  |  | 120 | 0.021148
344 | MRSSHPRD | 1 | North | YES | 0.12934 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.2933 | 0 | 0 | 0 | 0 |  |  | 0.2933 | 0 | 0.60886 | 0.62998 |  |  |  |  | 121 | 0.02112
345 | MRSSHPRD01 | 2 | North | YES | 0.12934 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.2933 | 0 | 0 | 0 | 0 |  |  | 0.2933 | 0 | 0.60886 | 0.62998 |  |  |  |  | 122 | 0.02112
1600 | BARTNWND_1G | 1 | North | YES | 0.12915 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.29311 | 0 | 120 | 15.4984 | 120 |  |  | 0.29311 | 35.1733 | 0.61177 | 0.63282 |  |  |  |  | 123 | 0.02112
1479 | WFCOGEN_1G | 1 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0 | 0.61177 | 0.63282 |  |  |  |  | 124 | 0.02112
1479 | WFCOGEN_1G | 2 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0 | 0.61177 | 0.63282 |  |  |  |  | 125 | 0.02112
1482 | WFCOGEN_2G | 2 | North | YES | 0.12897 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0 | 0.61177 | 0.63282 |  |  |  |  | 126 | 0.021058
1482 | WFCOGEN_2G | 1 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0 | 0.61177 | 0.63282 |  |  |  |  | 127 | 0.021058
1432 | GRHAMSES_2G | 2 | North | YES | 0.12886 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.29281 | 366 | 366 | 47.1617 | 366 |  |  | 0.29281 | 107.1701 | 0.62063 | 0.64149 |  |  |  |  | 128 | 0.021058
332 | RWMILLER01 | 1 | North | YES | 0.12818 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.29214 | 73 | 73 | 9.3571 | 73 |  |  | 0.29214 | 21.326 | 0.6224 | 0.64322 |  |  |  |  | 129 | 0.021058
333 | RWMILLER02 | 2 | North | YES | 0.12818 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.29214 | 119 | 119 | 15.2534 | 119 |  |  | 0.29214 | 34.7644 | 0.62529 | 0.64603 |  |  |  |  | 130 | 0.021058
334 | RWMILLER03 | 3 | North | YES | 0.12818 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.29214 | 208 | 208 | 26.6614 | 208 |  |  | 0.29214 | 60.7646 | 0.63033 | 0.65095 |  |  |  |  | 131 | 0.02086
335 | RWMILLER04 | 4 | North | YES | 0.12818 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.29214 | 102 | 102 | 13.0744 | 102 |  |  | 0.29214 | 29.798 | 0.6328 | 0.65336 |  |  |  |  | 132 | 0.020816
336 | RWMILLER05 | 5 | North | YES | 0.12818 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.29214 | 101 | 101 | 12.9462 | 101 |  |  | 0.29214 | 29.5059 | 0.63524 | 0.65574 |  |  |  |  | 133 | 0.020745
1433 | GRHAMSES_1G | 1 | North | YES | 0.12811 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.29207 | 242 | 242 | 31.0024 | 242 |  |  | 0.29207 | 70.6801 | 0.64111 | 0.66146 |  |  |  |  | 134 | 0.020621
6100 | OKLA7A | EQ | West | YES | 0.12691 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.29087 | 0 | 0 |  |  |  |  | 0.29087 | 0 | 0.64111 | 0.66146 |  |  |  |  | 135 | 0.02056
6752 | OKLA0A | 1 | West | YES | 0.12691 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.29087 | 0 | 649.7 |  |  |  |  | 0.29087 | 188.9753 | 0.65685 | 0.67675 |  |  |  |  | 136 | 0.0205
1442 | COKFIELD_5 | 1 | North | YES | 0.12625 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.29021 | 0 | 165 | 20.8311 | 165 |  |  | 0.29021 | 47.8841 | 0.66085 | 0.68062 |  |  |  |  | 137 | 0.020354
1438 | MESQUITW_2G | 1 | North | YES | 0.12543 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.28938 | 0 | 236 | 29.6005 | 236 |  |  | 0.28938 | 68.2945 | 0.66657 | 0.68615 |  |  |  |  | 138 | 0.020354
1437 | MESQUITW_1G | 1 | North | YES | 0.12542 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.28938 | 0 | 400 | 50.1684 | 400 |  |  | 0.28938 | 115.7514 | 0.67626 | 0.69551 |  |  |  |  | 139 | 0.0199
60081 | WHRLWIND1A | 1 | West | YES | 0.12384 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.2878 | 0 | 60 |  |  |  |  | 0.2878 | 17.2679 | 0.67771 | 0.69691 |  |  |  |  | 140 | 0.019775
1416 | SWETWATR_1G | 1 | West | YES | 0.12334 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.28729 | 30 | 30 |  |  |  |  | 0.28729 | 8.6188 | 0.67844 | 0.69761 |  |  |  |  | 141 | 0.019582
1417 | SWETWATR_2G | 2 | West | YES | 0.12334 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.28729 | 72 | 72 |  |  |  |  | 0.28729 | 20.6852 | 0.68018 | 0.69928 |  |  |  |  | 142 | 0.019254
1418 | SWETWATR_3G | 3 | West | YES | 0.12334 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.28729 | 68 | 68 |  |  |  |  | 0.28729 | 19.536 | 0.68183 | 0.70086 |  |  |  |  | 143 | 0.019197
1419 | SWETWATR_4G | 4 | West | YES | 0.12334 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.28729 | 61 | 61 |  |  |  |  | 0.28729 | 17.525 | 0.68331 | 0.70228 |  |  |  |  | 144 | 0.019167
1643 | SLSTR1PP_1G | 1 | North | YES | 0.12319 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.28714 | 0 | 60 | 7.3912 | 60 |  |  | 0.28714 | 17.2287 | 0.68476 | 0.70367 |  |  |  |  | 145 | 0.019096
11056 | ROSCOE_1G | 1 | West | YES | 0.12289 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.28685 | 0 | 209 |  |  |  |  | 0.28685 | 59.9507 | 0.68983 | 0.70852 |  |  |  |  | 146 | 0.019029
11057 | CHAMPION_1G | 1 | West | YES | 0.12289 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.28685 | 0 | 126.5 |  |  |  |  | 0.28685 | 36.286 | 0.69289 | 0.71146 |  |  |  |  | 147 | 0.018969
11058 | PYRON_1G | 1 | West | YES | 0.12289 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.28685 | 0 | 249 |  |  |  |  | 0.28685 | 71.4245 | 0.69893 | 0.71724 |  |  |  |  | 148 | 0.018909
11059 | INADALE_1G | 1 | West | YES | 0.12289 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.28685 | 0 | 197 |  |  |  |  | 0.28685 | 56.5086 | 0.7037 | 0.72181 |  |  |  |  | 149 | 0.018695
6144 | MCADOO1A | 1 | West | YES | 0.12286 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.28682 | 0 | 150 |  |  |  |  | 0.28682 | 43.0231 | 0.70733 | 0.72529 |  |  |  |  | 150 | 0.018565
71051 | L_BITTCR1_1N | W1 | West | YES | 0.12284 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 37.5 |  |  |  |  | 0.2868 | 10.7549 | 0.70824 | 0.72616 |  |  |  |  | 151 | 0.01831
71054 | L_SWEETW1_1N | W1 | West | YES | 0.12284 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 107.5 |  |  |  |  | 0.2868 | 30.8306 | 0.71085 | 0.72865 |  |  |  |  | 152 | 0.018108
71057 | L_SWEETW1_2N | W1 | West | YES | 0.12284 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 135 |  |  |  |  | 0.2868 | 38.7175 | 0.71412 | 0.73178 |  |  |  |  | 153 | 0.017954
71059 | L_SWEETW1_3N | W1 | West | YES | 0.12284 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 119 |  |  |  |  | 0.2868 | 34.1288 | 0.717 | 0.73454 |  |  |  |  | 154 | 0.017915
71060 | L_SWEETW1_4N | W1 | West | YES | 0.12284 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 105 |  |  |  |  | 0.2868 | 30.1136 | 0.71955 | 0.73698 |  |  |  |  | 155 | 0.017805
71061 | L_SWEETW1_5N | W1 | West | YES | 0.12284 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 80.5 |  |  |  |  | 0.2868 | 23.0871 | 0.7215 | 0.73885 |  |  |  |  | 156 | 0.017666
6407 | TURKTRAK1A | 1 | West | YES | 0.12241 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.28637 | 0 | 169.5 |  |  |  |  | 0.28637 | 48.5393 | 0.7256 | 0.74278 |  |  |  |  | 157 | 0.017543
1343 | TRENTIPP_8 | 1 | West | YES | 0.12222 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.28618 | 0 | 150 |  |  |  |  | 0.28618 | 42.9268 | 0.72924 | 0.74625 |  |  |  |  | 158 | 0.017435
1354 | AEPWIND_8 | 1 | West | YES | 0.12222 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.28618 | 0 | 101 |  |  |  |  | 0.28618 | 28.904 | 0.73169 | 0.74859 |  |  |  |  | 159 | 0.017352
36998 | RDCNYNG1 | 1 | West | YES | 0.12212 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.28608 | 0 | 84 |  |  |  |  | 0.28608 | 24.0306 | 0.73372 | 0.75053 |  |  |  |  | 160 | 0.017172
1061 | CIELOGEN_1G | 1 | West | YES | 0.12195 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.28591 | 0 | 99 |  |  |  |  | 0.28591 | 28.305 | 0.73612 | 0.75282 |  |  |  |  | 161 | 0.01701
1062 | CIELOGEN_2G | 1 | West | YES | 0.12195 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.28591 | 0 | 61 |  |  |  |  | 0.28591 | 17.4405 | 0.7376 | 0.75423 |  |  |  |  | 162 | 0.016901
1069 | KINDERMG_1G | 1 | West | YES | 0.12195 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0 | 0.7376 | 0.75423 |  |  |  |  | 163 | 0.01681
1070 | KINDERMG_2G | 1 | West | YES | 0.12195 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0 | 0.7376 | 0.75423 |  |  |  |  | 164 | 0.016701
1071 | KINDERMG_3G | 1 | West | YES | 0.12195 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0 | 0.7376 | 0.75423 |  |  |  |  | 165 | 0.016634
1068 | SCURRYCW_1G | 1 | West | YES | 0.12194 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.2859 | 0 | 141 |  |  |  |  | 0.2859 | 40.3118 | 0.74101 | 0.75749 |  |  |  |  | 166 | 0.016634
1073 | SCURRYCW_2G | 2 | West | YES | 0.12194 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.2859 | 0 | 120 |  |  |  |  | 0.2859 | 34.3079 | 0.74392 | 0.76027 |  |  |  |  | 167 | 0.016634
6637 | SNYDERW1A | 1 | West | YES | 0.12188 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.28583 | 0 | 63 |  |  |  |  | 0.28583 | 18.0076 | 0.74545 | 0.76172 |  |  |  |  | 168 | 0.016634
1037 | MORGAN5G_5G | 5 | West | YES | 0.12184 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.2858 | 137 | 137 |  |  |  |  | 0.2858 | 39.1545 | 0.74877 | 0.76489 |  |  |  |  | 169 | 0.016479
1039 | MRGNAG_1G | A | West | YES | 0.12184 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.2858 | 69 | 69 |  |  |  |  | 0.2858 | 19.7202 | 0.75044 | 0.76649 |  |  |  |  | 170 | 0.016347
1040 | MRGNBG_2G | B | West | YES | 0.12184 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.2858 | 71 | 71 |  |  |  |  | 0.2858 | 20.2918 | 0.75216 | 0.76813 |  |  |  |  | 171 | 0.016277
1041 | MRGNCG_3G | C | West | YES | 0.12184 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.2858 | 70 | 70 |  |  |  |  | 0.2858 | 20.006 | 0.75386 | 0.76975 |  |  |  |  | 172 | 0.016125
1042 | MRGNDG_4G | D | West | YES | 0.12184 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.2858 | 68 | 68 |  |  |  |  | 0.2858 | 19.4344 | 0.7555 | 0.77132 |  |  |  |  | 173 | 0.016048
1043 | MRGNEG_5G | E | West | YES | 0.12184 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.2858 | 70 | 70 |  |  |  |  | 0.2858 | 20.006 | 0.7572 | 0.77294 |  |  |  |  | 174 | 0.01597
1044 | MRGNFG_6G | F | West | YES | 0.12184 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.2858 | 66 | 66 |  |  |  |  | 0.2858 | 18.8628 | 0.7588 | 0.77446 |  |  |  |  | 175 | 0.015892
60058 | BUFF_GAP1A | 1 | West | YES | 0.12179 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.28574 | 0 | 120 |  |  |  |  | 0.28574 | 34.2893 | 0.76171 | 0.77724 |  |  |  |  | 176 | 0.015816
60060 | CIRELLO | 1 | West | YES | 0.12179 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.28574 | 0 | 233 |  |  |  |  | 0.28574 | 66.5785 | 0.76735 | 0.78262 |  |  |  |  | 177 | 0.015739
60063 | BUFF_GAP1B | 1 | West | YES | 0.12179 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.28574 | 0 | 170.2 |  |  |  |  | 0.28574 | 48.6337 | 0.77148 | 0.78656 |  |  |  |  | 178 | 0.015666
60066 | H_HOLLOW1A | 1 | West | YES | 0.12179 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.28574 | 0 | 222 |  |  |  |  | 0.28574 | 63.4353 | 0.77685 | 0.79169 |  |  |  |  | 179 | 0.015532
60068 | HHOLLOW21A | 1 | West | YES | 0.12179 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 184 |  |  |  |  | 0.28574 | 52.577 | 0.78131 | 0.79594 |  |  |  |  | 180 | 0.015272
60070 | HHOLLOW31A | 1 | West | YES | 0.12179 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 224 |  |  |  |  | 0.28574 | 64.0068 | 0.78674 | 0.80112 |  |  |  |  | 181 | 0.015083
60072 | HHOLLOW41A | 1 | West | YES | 0.12179 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 115 |  |  |  |  | 0.28574 | 32.8606 | 0.78953 | 0.80378 |  |  |  |  | 182 | 0.014835
1058 | LONGSHORE_5 | 1 | West | YES | 0.12173 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.28568 | 0 | 150 |  |  |  |  | 0.28568 | 42.8525 | 0.79316 | 0.80725 |  |  |  |  | 183 | 0.01463
1058 | LONGSHORE_5 | 2 | West | YES | 0.12173 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.28568 | 0 | 220 |  |  |  |  | 0.28568 | 62.8504 | 0.79849 | 0.81233 |  |  |  |  | 184 | 0.014381
11065 | ELBOWCK_1G | 1 | West | YES | 0.12173 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.28568 | 0 | 121.9 |  |  |  |  | 0.28568 | 34.8248 | 0.80145 | 0.81515 |  |  |  |  | 185 | 0.014253
1045 | CALENG1G_1G | 1 | West | YES | 0.12154 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0 | 0.80145 | 0.81515 |  |  |  |  | 186 | 0.014085
1046 | CALENG2G_2G | 2 | West | YES | 0.12154 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0 | 0.80145 | 0.81515 |  |  |  |  | 187 | 0.013839
1047 | CALENG3G_3G | 3 | West | YES | 0.12154 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0 | 0.80145 | 0.81515 |  |  |  |  | 188 | 0.013702
11309 | BULLCREK_2G | 1 | West | YES | 0.12152 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.28548 | 0 | 180 |  |  |  |  | 0.28548 | 51.386 | 0.80581 | 0.81931 |  |  |  |  | 189 | 0.013702
11310 | BULLCREK_1G | 1 | West | YES | 0.12152 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.28548 | 0 | 180 |  |  |  |  | 0.28548 | 51.386 | 0.81017 | 0.82346 |  |  |  |  | 190 | 0.013702
11320 | COYOTE_1G | 1 | West | YES | 0.12146 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.28541 | 0 | 225 |  |  |  |  | 0.28541 | 64.2183 | 0.81562 | 0.82866 |  |  |  |  | 191 | 0.013702
1360 | GUNSIGHT_8 | 1 | West | YES | 0.1212 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.28515 | 0 | 120 |  |  |  |  | 0.28515 | 34.2185 | 0.81853 | 0.83143 |  |  |  |  | 192 | 0.013498
1327 | WILDHRSE_1G | 1 | West | YES | 0.12116 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.28512 | 0 | 120 |  |  |  |  | 0.28512 | 34.2145 | 0.82144 | 0.83419 |  |  |  |  | 193 | 0.013294
1333 | MCDDONAL_8 | 1 | West | YES | 0.12095 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.28491 | 0 | 214.2 |  |  |  |  | 0.28491 | 61.028 | 0.82663 | 0.83913 |  |  |  |  | 194 | 0.013037
1328 | OCOTILLO_1G | 1 | West | YES | 0.12078 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.28474 | 0 | 58 |  |  |  |  | 0.28474 | 16.515 | 0.82803 | 0.84047 |  |  |  |  | 195 | 0.012898
11001 | NAV1CT | 1 | West | YES | 0.12072 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.28468 | 70.4 | 70.4 |  |  |  |  | 0.28468 | 20.0416 | 0.82974 | 0.84209 |  |  |  |  | 196 | 0.012758
11009 | NAV2CT | 1 | West | YES | 0.12072 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.28468 | 71.4 | 71.4 |  |  |  |  | 0.28468 | 20.3263 | 0.83147 | 0.84373 |  |  |  |  | 197 | 0.012505
11011 | NAV3ST | 1 | West | YES | 0.12072 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.28468 | 92.8 | 92.8 |  |  |  |  | 0.28468 | 26.4184 | 0.83372 | 0.84587 |  |  |  |  | 198 | 0.012436
11012 | NAV4CT | 1 | West | YES | 0.12072 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28468 | 80 | 80 |  |  |  |  | 0.28468 | 22.7745 | 0.83565 | 0.84771 |  |  |  |  | 199 | 0.012351
11013 | NAV5CT | 1 | West | YES | 0.12072 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28468 | 80 | 80 |  |  |  |  | 0.28468 | 22.7745 | 0.83759 | 0.84955 |  |  |  |  | 200 | 0.012265
11014 | NAV6ST | 1 | West | YES | 0.12072 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.28468 | 115 | 115 |  |  |  |  | 0.28468 | 32.7384 | 0.84038 | 0.8522 |  |  |  |  | 201 | 0.012154
11020 | TIEHVSG_1G | 1 | West | YES | 0.12071 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.28467 | 208.2 | 208.2 |  |  |  |  | 0.28467 | 59.2684 | 0.84542 | 0.857 |  |  |  |  | 202 | 0.012058
11021 | TIEHVCG_1G | 1 | West | YES | 0.12071 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.28467 | 142.1 | 142.1 |  |  |  |  | 0.28467 | 40.4517 | 0.84887 | 0.86027 |  |  |  |  | 203 | 0.011962
11022 | TIEHVCG_2G | 1 | West | YES | 0.12071 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.28467 | 132.4 | 132.4 |  |  |  |  | 0.28467 | 37.6904 | 0.85207 | 0.86332 |  |  |  |  | 204 | 0.011824
11023 | TIEHVCG_3G | 1 | West | YES | 0.12071 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.28467 | 137.4 | 137.4 |  |  |  |  | 0.28467 | 39.1137 | 0.8554 | 0.86648 |  |  |  |  | 205 | 0.011574
11024 | TIEHVCG_4G | 1 | West | YES | 0.12071 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.28467 | 147 | 147 |  |  |  |  | 0.28467 | 41.8466 | 0.85897 | 0.86987 |  |  |  |  | 206 | 0.011403
11025 | TIEHVSG_2G | 1 | West | YES | 0.12071 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.28467 | 213.2 | 213.2 |  |  |  |  | 0.28467 | 60.6918 | 0.86413 | 0.87478 |  |  |  |  | 207 | 0.011245
1326 | STANTONW_8 | 1 | West | YES | 0.12067 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.28463 | 0 | 100.5 |  |  |  |  | 0.28463 | 28.6051 | 0.86657 | 0.87709 |  |  |  |  | 208 | 0.01108
1320 | BSP 1 | 1 | West | YES | 0.12055 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.28451 | 0 | 0 |  |  |  |  | 0.28451 | 0 | 0.86657 | 0.87709 |  |  |  |  | 209 | 0.010903
76031 | L_GASCCR1_1N | W1 | West | YES | 0.12027 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.28423 | 0 | 150 |  |  |  |  | 0.28423 | 42.634 | 0.8702 | 0.88054 |  |  |  |  | 210 | 0.010647
11147 | NOTREES_1G | 1 | West | YES | 0.11994 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.28389 | 0 | 149 |  |  |  |  | 0.28389 | 42.3001 | 0.87381 | 0.88396 |  |  |  |  | 211 | 0.010526
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.11993 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.28389 | 0 | 112.5 |  |  |  |  | 0.28389 | 31.9377 | 0.87654 | 0.88655 |  |  |  |  | 212 | 0.010526
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.11993 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 149.5 |  |  |  |  | 0.28389 | 42.4416 | 0.88016 | 0.88998 |  |  |  |  | 213 | 0.01034
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.11993 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 186 |  |  |  |  | 0.28389 | 52.8036 | 0.88467 | 0.89425 |  |  |  |  | 214 | 0.010152
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.11993 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 214.5 |  |  |  |  | 0.28389 | 60.8945 | 0.88986 | 0.89918 |  |  |  |  | 215 | 0.01001
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.11981 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.28376 | 0 | 35 |  |  |  |  | 0.28376 | 9.9318 | 0.89071 | 0.89998 |  |  |  |  | 216 | 0.009821
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.11981 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.28376 | 0 | 30 |  |  |  |  | 0.28376 | 8.5129 | 0.89144 | 0.90067 |  |  |  |  | 217 | 0.0095859
1002 | PBCTAGE_1G | A | West | YES | 0.11974 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.2837 | 66 | 66 |  |  |  |  | 0.2837 | 18.724 | 0.89304 | 0.90219 |  |  |  |  | 218 | 0.0093148
1003 | PBCTBGE_2G | B | West | YES | 0.11974 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.2837 | 66 | 66 |  |  |  |  | 0.2837 | 18.724 | 0.89464 | 0.9037 |  |  |  |  | 219 | 0.0092702
1004 | PBCTCGE_3G | C | West | YES | 0.11974 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.2837 | 67 | 67 |  |  |  |  | 0.2837 | 19.0077 | 0.89626 | 0.90524 |  |  |  |  | 220 | 0.009232
1005 | PBCTDGE_4G | D | West | YES | 0.11974 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.2837 | 68 | 68 |  |  |  |  | 0.2837 | 19.2914 | 0.89791 | 0.9068 |  |  |  |  | 221 | 0.0091476
1006 | PBCTEGE_5G | E | West | YES | 0.11974 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.2837 | 67 | 67 |  |  |  |  | 0.2837 | 19.0077 | 0.89953 | 0.90834 |  |  |  |  | 222 | 0.0090631
1007 | PB5GEN_6G | 5 | West | YES | 0.11974 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.2837 | 114 | 114 |  |  |  |  | 0.2837 | 32.3415 | 0.90229 | 0.91095 |  |  |  |  | 223 | 0.0089774
1008 | PB6GEN_7G | 6 | West | YES | 0.11974 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.2837 | 515 | 515 |  |  |  |  | 0.2837 | 146.1042 | 0.91477 | 0.92277 |  |  |  |  | 224 | 0.0088904
60057 | CALLAHAN1A | 1 | West | YES | 0.11964 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.2836 | 0 | 114 |  |  |  |  | 0.2836 | 32.33 | 0.91754 | 0.92539 |  |  |  |  | 225 | 0.0088047
1349 | WESTXWIN_1G | 1 | West | YES | 0.11931 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.28326 | 0 | 6.6 |  |  |  |  | 0.28326 | 1.8695 | 0.9177 | 0.92554 |  |  |  |  | 226 | 0.0086588
1350 | NWPWRG1_1G | 1 | West | YES | 0.11931 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.28326 | 0 | 34.3 |  |  |  |  | 0.28326 | 9.716 | 0.91853 | 0.92633 |  |  |  |  | 227 | 0.0079998
244 | WHITNYDM01 | 1 | North | YES | 0.11339 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.27735 | 0 | 0 | 0 | 0 |  |  | 0.27735 | 0 | 0.91853 | 0.92633 |  |  |  |  | 228 | 0.0078531
245 | WHITNYDM02 | 2 | North | YES | 0.11339 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.27735 | 0 | 0 | 0 | 0 |  |  | 0.27735 | 0 | 0.91853 | 0.92633 |  |  |  |  | 229 | 0.0078444
60007 | KING_SW1A | 1 | West | YES | 0.11331 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27726 | 0 | 80 |  |  |  |  | 0.27726 | 22.181 | 0.92046 | 0.92812 |  |  |  |  | 230 | 0.0077993
60019 | KING_NW1A | 1 | West | YES | 0.11331 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27726 | 0 | 80 |  |  |  |  | 0.27726 | 22.181 | 0.9224 | 0.92991 |  |  |  |  | 231 | 0.0077993
60201 | RIO DRCS | F | West | YES | 0.11301 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.27696 | 0 | 0 |  |  |  |  | 0.27696 | 0 | 0.9224 | 0.92991 |  |  |  |  | 232 | 0.0077993
6016 | SWMESA | 1 | West | YES | 0.11289 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.27685 | 0 | 75 |  |  |  |  | 0.27685 | 20.7634 | 0.92422 | 0.93159 |  |  |  |  | 233 | 0.0076553
60003 | KING_NE1A | 1 | West | YES | 0.11289 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27685 | 0 | 80 |  |  |  |  | 0.27685 | 22.1476 | 0.92616 | 0.93339 |  |  |  |  | 234 | 0.0075113
60005 | KING_SE1A | 1 | West | YES | 0.11289 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.27685 | 0 | 40 |  |  |  |  | 0.27685 | 11.0738 | 0.92713 | 0.93428 |  |  |  |  | 235 | 0.0075113
60016 | WOODWRD11A | 1 | West | YES | 0.11281 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.27677 | 0 | 80 |  |  |  |  | 0.27677 | 22.1414 | 0.92907 | 0.93607 |  |  |  |  | 236 | 0.0073737
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.1128 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.27675 | 0 | 80 |  |  |  |  | 0.27675 | 22.1403 | 0.931 | 0.93786 |  |  |  |  | 237 | 0.007227
38437 | TNSRBNMESA9 | 1 | West | YES | 0.11273 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.27669 | 0 | 150 |  |  |  |  | 0.27669 | 41.5034 | 0.93464 | 0.94122 |  |  |  |  | 238 | 0.0071537
60017 | ORNNWP1 | 1 | West | YES | 0.11052 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.27447 | 0 | 80 |  |  |  |  | 0.27447 | 21.958 | 0.93658 | 0.943 |  |  |  |  | 239 | 0.0070065
60000 | DSKY2 | 1 | West | YES | 0.10996 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.27392 | 0 | 76.5 |  |  |  |  | 0.27392 | 20.9551 | 0.93843 | 0.94469 |  |  |  |  | 240 | 0.0068592
60018 | DSKY1 | 1 | West | YES | 0.10977 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.27373 | 0 | 84 |  |  |  |  | 0.27373 | 22.9931 | 0.94047 | 0.94655 |  |  |  |  | 241 | 0.0065822
251 | BOSQUESW803 | 2 | North | YES | 0.10903 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.27299 | 150 | 150 | 16.3548 | 150 |  |  | 0.27299 | 40.9484 | 0.9441 | 0.94987 |  |  |  |  | 242 | 0.0064201
253 | BOSQUESW804 | 2 | North | YES | 0.10903 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.27299 | 80 | 80 | 8.7226 | 80 |  |  | 0.27299 | 21.8392 | 0.94604 | 0.95163 |  |  |  |  | 243 | 0.0062618
238 | BOSQUESW505 | 1 | North | YES | 0.10599 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.26995 | 255 | 255 | 27.0277 | 255 |  |  | 0.26995 | 68.8369 | 0.95222 | 0.9572 |  |  |  |  | 244 | 0.0060865
239 | BOSQUESW502 | 1 | North | YES | 0.10599 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.26995 | 149 | 149 | 15.7927 | 149 |  |  | 0.26995 | 40.2223 | 0.95583 | 0.96046 |  |  |  |  | 245 | 0.0057647
247 | BOSQUESW501 | 2 | North | YES | 0.10599 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.26995 | 156 | 156 | 16.5346 | 156 |  |  | 0.26995 | 42.112 | 0.95961 | 0.96386 |  |  |  |  | 246 | 0.005593
3403 | THOUSE_1G | 1 | North | YES | 0.1042 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.26815 | 563 | 563 | 58.6629 | 563 |  |  | 0.26815 | 150.971 | 0.97325 | 0.97608 |  |  |  |  | 247 | 0.0049831
3404 | THOUSE_2G | 2 | North | YES | 0.1042 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.26815 | 807 | 807 | 84.087 | 807 |  |  | 0.26815 | 216.4007 | 0.9928 | 0.99358 |  |  |  |  | 248 | 0.0046267
3416 | LAKE_CRK1_G | 1 | North | YES | 0.10317 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.26713 | 75 | 75 | 7.7381 | 75 |  |  | 0.26713 | 20.0349 | 0.99462 | 0.9952 |  |  |  |  | 249 | 0.0042536
3417 | LAKE_CRK2_G | 2 | North | YES | 0.10317 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.26713 | 222 | 222 | 22.9046 | 222 |  |  | 0.26713 | 59.3032 | 1 | 1 |  |  |  |  | 250 | 0.0028253
60202 | FRNDDRCS | F | West | YES | 0.0982 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.26216 | 0 | 0 |  |  |  |  | 0.26216 | 0 | 1 | 1 |  |  |  |  | 251 | 0.00077804
48671 | FTR_GT1_5105 | 1 | North | YES | -0.22511 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | -0.06115 | 154.2 | 154.2 | -34.7117 | 154.2 |  |  | -0.06115 | -9.4294 | [6 empty] | 252 | 0.00058157
48672 | FTR_GT2_5110 | 2 | North | YES | -0.22511 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | -0.06115 | 159 | 159 | -35.7922 | 159 |  |  | -0.06115 | -9.7229 | [6 empty] | 253 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | -0.22511 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | -0.06115 | 158 | 158 | -35.5671 | 158 |  |  | -0.06115 | -9.6618 | [6 empty] | 254 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | -0.22511 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | -0.06115 | 380 | 380 | -85.541 | 380 |  |  | -0.06115 | -23.2372 | [6 empty] | 255 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.044052 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.086954 | 0 | 581 |  |  |  |  | -0.086954 | 0 | [6 empty] | 256 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.02338 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.10763 | 0 | 580 |  |  |  |  | -0.10763 | 0 | [6 empty] | 257 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.007923 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 | [6 empty] | 258 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.007923 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 | [6 empty] | 259 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.007923 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 | [6 empty] | 260 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.007267 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.12374 | 0 | 0 |  |  |  |  | -0.12374 | 0 | [6 empty] | 261 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.000602 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 | [6 empty] | 262 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.000602 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 | [6 empty] | 263 | 0
88253 | HAMILTON | F | South | YES | 0.000602 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 | [6 empty] | 264 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.13101 | 15 | 15 |  |  |  |  | -0.13101 | -1.9651 | [6 empty] | 265 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | [6 empty] | 266 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | [6 empty] | 267 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | [6 empty] | 268 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | [6 empty] | 269 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | [6 empty] | 270 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | [6 empty] | 271 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | [6 empty] | 272 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | [6 empty] | 273 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.13101 | 0 | 0 |  |  | 0 | 0 | -0.13101 | 0 | [6 empty] | 274 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.00102 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.13203 | 0 | 0 |  |  |  |  | -0.13203 | 0 | [6 empty] | 275 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.00102 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.13203 | 0 | 0 |  |  |  |  | -0.13203 | 0 | [6 empty] | 276 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.001256 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.13226 | 423.3 | 423.3 |  |  |  |  | -0.13226 | -55.9867 | [6 empty] | 277 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.003738 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.13474 | 0 | 0 |  |  |  |  | -0.13474 | 0 | [6 empty] | 278 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.003738 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.13474 | 0 | 0 |  |  |  |  | -0.13474 | 0 | [6 empty] | 279 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.008874 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 | [6 empty] | 280 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.008874 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 | [6 empty] | 281 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.008874 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 | [6 empty] | 282 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.01061 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.14162 | 42 | 42 |  |  |  |  | -0.14162 | -5.9479 | [6 empty] | 283 | 0
9003 | DECKR_G4 | 4 | South | YES | -0.01061 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.14162 | 44 | 44 |  |  |  |  | -0.14162 | -6.2311 | [6 empty] | 284 | 0
9004 | DECKR_G5 | 5 | South | YES | -0.01061 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.14162 | 44 | 44 |  |  |  |  | -0.14162 | -6.2311 | [6 empty] | 285 | 0
9005 | DECKR_G6 | 6 | South | YES | -0.01061 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.14162 | 47 | 47 |  |  |  |  | -0.14162 | -6.656 | [6 empty] | 286 | 0
9000 | DECKR_G1 | 1 | South | YES | -0.01167 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.14268 | 321 | 321 |  |  |  |  | -0.14268 | -45.7991 | [6 empty] | 287 | 0
9001 | DECKR_G2 | 2 | South | YES | -0.01167 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.14268 | 426 | 426 |  |  |  |  | -0.14268 | -60.7801 | [6 empty] | 288 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.011802 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.14281 | 0 | 0 |  |  |  |  | -0.14281 | 0 | [6 empty] | 289 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.011802 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.14281 | 0 | 0 |  |  |  |  | -0.14281 | 0 | [6 empty] | 290 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.013106 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.14411 | 49 | 49 |  |  |  |  | -0.14411 | -7.0615 | [6 empty] | 291 | 0
9017 | SANDH_G2 | 2 | South | YES | -0.013106 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.14411 | 46 | 46 |  |  |  |  | -0.14411 | -6.6292 | [6 empty] | 292 | 0
9018 | SANDH_G3 | 3 | South | YES | -0.013106 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.14411 | 46 | 46 |  |  |  |  | -0.14411 | -6.6292 | [6 empty] | 293 | 0
9019 | SANDH_G4 | 4 | South | YES | -0.013106 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.14411 | 47 | 47 |  |  |  |  | -0.14411 | -6.7733 | [6 empty] | 294 | 0
9020 | SANDHG5A | 5A | South | YES | -0.013106 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.14411 | 155 | 155 |  |  |  |  | -0.14411 | -22.3374 | [6 empty] | 295 | 0
9021 | SANDHG5C | 5C | South | YES | -0.013106 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.14411 | 148 | 148 |  |  |  |  | -0.14411 | -21.3286 | [6 empty] | 296 | 0
8262 | ELPS | 1 | South | YES | -0.014943 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.14595 | 0 | 0 |  |  |  |  | -0.14595 | 0 | [6 empty] | 297 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.016728 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.14773 | 152.5 | 152.5 |  |  |  |  | -0.14773 | -22.5295 | [6 empty] | 298 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.016728 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.14773 | 149.5 | 149.5 |  |  |  |  | -0.14773 | -22.0863 | [6 empty] | 299 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.016728 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.14773 | 232.6 | 232.6 |  |  |  |  | -0.14773 | -34.363 | [6 empty] | 300 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.018765 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.14977 | 158 | 158 |  |  |  |  | -0.14977 | -23.6639 | [6 empty] | 301 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.018765 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.14977 | 160 | 160 |  |  |  |  | -0.14977 | -23.9634 | [6 empty] | 302 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.018765 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.14977 | 175 | 175 |  |  |  |  | -0.14977 | -26.21 | [6 empty] | 303 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.020362 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.15137 | 132 | 132 |  |  |  |  | -0.15137 | -19.9806 | [6 empty] | 304 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.020362 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.15137 | 139 | 139 |  |  |  |  | -0.15137 | -21.0402 | [6 empty] | 305 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.020362 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.15137 | 329 | 329 |  |  |  |  | -0.15137 | -49.8002 | [6 empty] | 306 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.030613 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.16162 | 0 | 0 |  |  |  |  | -0.16162 | 0 | [6 empty] | 307 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 | [6 empty] | 308 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 | [6 empty] | 309 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 | [6 empty] | 310 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 | [6 empty] | 311 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.035416 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.16642 | 223.9 | 223.9 |  |  |  |  | -0.16642 | -37.262 | [6 empty] | 312 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.035416 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.16642 | 225 | 225 |  |  |  |  | -0.16642 | -37.445 | [6 empty] | 313 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.035416 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.16642 | 224.6 | 224.6 |  |  |  |  | -0.16642 | -37.3785 | [6 empty] | 314 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.035416 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.16642 | 226.7 | 226.7 |  |  |  |  | -0.16642 | -37.728 | [6 empty] | 315 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.036911 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.16792 | 0 | 606 |  |  |  |  | -0.16792 | 0 | [6 empty] | 316 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.036911 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.16792 | 0 | 598 |  |  |  |  | -0.16792 | 0 | [6 empty] | 317 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.037052 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.16806 | 0 | 436 |  |  |  |  | -0.16806 | 0 | [6 empty] | 318 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.039626 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 | [6 empty] | 319 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.039626 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 | [6 empty] | 320 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.039626 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 | [6 empty] | 321 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.040116 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.17112 | 148 | 148 |  |  |  |  | -0.17112 | -25.3261 | [6 empty] | 322 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.040116 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.17112 | 148 | 148 |  |  |  |  | -0.17112 | -25.3261 | [6 empty] | 323 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.040116 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.17112 | 154 | 154 |  |  |  |  | -0.17112 | -26.3529 | [6 empty] | 324 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.040116 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.17112 | 293 | 293 |  |  |  |  | -0.17112 | -50.1389 | [6 empty] | 325 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.040794 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.1718 | 0 | 0 |  |  |  |  | -0.1718 | 0 | [6 empty] | 326 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.042542 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.17355 | 0 | 0 |  |  |  |  | -0.17355 | 0 | [6 empty] | 327 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.042542 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.17355 | 0 | 0 |  |  |  |  | -0.17355 | 0 | [6 empty] | 328 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 329 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 330 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 331 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 332 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 333 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 334 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 335 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 336 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 337 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 338 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 339 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 340 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 341 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 342 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 343 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 344 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 345 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 346 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 347 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 348 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 349 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 350 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 351 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | [6 empty] | 352 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.044531 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.17554 | 147 | 147 |  |  |  |  | -0.17554 | -25.804 | [6 empty] | 353 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.044531 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.17554 | 138 | 138 |  |  |  |  | -0.17554 | -24.2242 | [6 empty] | 354 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.044531 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.17554 | 146 | 146 |  |  |  |  | -0.17554 | -25.6285 | [6 empty] | 355 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.044531 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.17554 | 149 | 149 |  |  |  |  | -0.17554 | -26.1551 | [6 empty] | 356 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.044531 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.17554 | 182 | 182 |  |  |  |  | -0.17554 | -31.9478 | [6 empty] | 357 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.044531 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.17554 | 203 | 203 |  |  |  |  | -0.17554 | -35.6341 | [6 empty] | 358 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.045528 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.17653 | 407 | 407 |  |  |  |  | -0.17653 | -71.8495 | [6 empty] | 359 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.045555 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.17656 | 418 | 418 |  |  |  |  | -0.17656 | -73.8027 | [6 empty] | 360 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | -0.045555 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.17656 | 400 | 400 |  |  |  |  | -0.17656 | -70.6246 | [6 empty] | 361 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | -0.04556 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.17657 | 0 | 430 |  |  |  |  | -0.17657 | 0 | [6 empty] | 362 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.04556 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.17657 | 0 | 430 |  |  |  |  | -0.17657 | 0 | [6 empty] | 363 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.045592 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.1766 | 58 | 58 |  |  |  |  | -0.1766 | -10.2427 | [6 empty] | 364 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | -0.045592 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.1766 | 89 | 89 |  |  |  |  | -0.1766 | -15.7173 | [6 empty] | 365 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | -0.045592 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.1766 | 44 | 44 |  |  |  |  | -0.1766 | -7.7703 | [6 empty] | 366 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | -0.045592 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.1766 | 44 | 44 |  |  |  |  | -0.1766 | -7.7703 | [6 empty] | 367 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | -0.045592 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.1766 | 43 | 43 |  |  |  |  | -0.1766 | -7.5937 | [6 empty] | 368 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | -0.045592 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.1766 | 45 | 45 |  |  |  |  | -0.1766 | -7.9469 | [6 empty] | 369 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.045597 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.1766 | 61 | 61 |  |  |  |  | -0.1766 | -10.7728 | [6 empty] | 370 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.045597 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.1766 | 95 | 95 |  |  |  |  | -0.1766 | -16.7773 | [6 empty] | 371 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.045597 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.1766 | 151 | 151 |  |  |  |  | -0.1766 | -26.6671 | [6 empty] | 372 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.045713 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.17672 | 215 | 215 |  |  |  |  | -0.17672 | -37.9947 | [6 empty] | 373 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.045713 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.17672 | 216 | 216 |  |  |  |  | -0.17672 | -38.1714 | [6 empty] | 374 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.045752 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.17676 | 24 | 24 |  |  |  |  | -0.17676 | -4.2422 | [6 empty] | 375 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.045752 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.17676 | 24.3 | 24.3 |  |  |  |  | -0.17676 | -4.2952 | [6 empty] | 376 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.045752 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.17676 | 23.9 | 23.9 |  |  |  |  | -0.17676 | -4.2245 | [6 empty] | 377 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.047164 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.17817 | 155 | 155 |  |  |  |  | -0.17817 | -27.6164 | [6 empty] | 378 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | -0.047164 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.17817 | 174 | 174 |  |  |  |  | -0.17817 | -31.0017 | [6 empty] | 379 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.047164 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.17817 | 155 | 155 |  |  |  |  | -0.17817 | -27.6164 | [6 empty] | 380 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.048248 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.17925 | 0 | 562 |  |  |  |  | -0.17925 | 0 | [6 empty] | 381 | 0
8189 | CUECPL2A | 1 | South | YES | -0.050999 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.18201 | 0 | 0 |  |  |  |  | -0.18201 | 0 | [6 empty] | 382 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.053842 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.18485 | 0 | 396.3 |  |  |  |  | -0.18485 | 0 | [6 empty] | 383 | 0
80265 | LARECU40A | 4 | South | YES | -0.054415 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.18542 | 100 | 100 |  |  |  |  | -0.18542 | -18.5421 | [6 empty] | 384 | 0
80266 | LARECU50A | 5 | South | YES | -0.054415 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.18542 | 100 | 100 |  |  |  |  | -0.18542 | -18.5421 | [6 empty] | 385 | 0
80012 | LAR | F | South | YES | -0.054418 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.18542 | 0 | 0 |  |  |  |  | -0.18542 | 0 | [6 empty] | 386 | 0
88299 | ZAPATA | F | South | YES | -0.060485 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.19149 | 0 | 0 |  |  |  |  | -0.19149 | 0 | [6 empty] | 387 | 0
88198 | BEEVILLE | F | South | YES | -0.063278 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.19428 | 0 | 0 |  |  |  |  | -0.19428 | 0 | [6 empty] | 388 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.064599 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0 | [6 empty] | 389 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.064599 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0 | [6 empty] | 390 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.064599 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0
88508 | FALFURRI | F | South | YES | -0.065356 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.19636 | 0 | 0 |  |  |  |  | -0.19636 | 0
8161 | COLETO0A | 1 | South | YES | -0.066648 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.19765 | 0 | 633 |  |  |  |  | -0.19765 | 0
8933 | FGNTS001 | 1 | South | YES | -0.0689 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.19991 | 146.5 | 146.5 |  |  |  |  | -0.19991 | -29.2863
8934 | FGNTS101 | 2 | South | YES | -0.0689 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.19991 | 147.9 | 147.9 |  |  |  |  | -0.19991 | -29.5662
8935 | FGNTS201 | 3 | South | YES | -0.0689 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.19991 | 173 | 173 |  |  |  |  | -0.19991 | -34.5838
8981 | HECN1 | 1 | South | YES | -0.069623 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.20063 | 144.8 | 144.8 |  |  |  |  | -0.20063 | -29.0511
8982 | HECN2 | 2 | South | YES | -0.069623 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.20063 | 144.1 | 144.1 |  |  |  |  | -0.20063 | -28.9107
8983 | HECN3 | 3 | South | YES | -0.069623 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.20063 | 171.9 | 171.9 |  |  |  |  | -0.20063 | -34.4882
8936 | MVGN#1 | 1 | South | YES | -0.069624 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.20063 | 216.6 | 216.6 |  |  |  |  | -0.20063 | -43.4565
8937 | MVGN#2 | 2 | South | YES | -0.069624 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.20063 | 216.7 | 216.7 |  |  |  |  | -0.20063 | -43.4766
8938 | MVGN#3 | 3 | South | YES | -0.069624 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.20063 | 250.9 | 250.9 |  |  |  |  | -0.20063 | -50.3382
5932 | SI_RAY9 | 9 | South | YES | -0.069941 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.20095 | 38 | 38 |  |  |  |  | -0.20095 | -7.636
5933 | SI_RAY6 | 6 | South | YES | -0.069941 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.20095 | 19.3 | 19.3 |  |  |  |  | -0.20095 | -3.8783
5935 | SI_RAY10 | 10 | South | YES | -0.069941 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.20095 | 47 | 47 |  |  |  |  | -0.20095 | -9.4445
80003 | MILHWYS | F | South | YES | -0.069941 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.20095 | 0 | 0 |  |  |  |  | -0.20095 | 0
80080 | GWINDT11A | 3 | South | YES | -0.070135 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 38 |  |  |  |  | -0.20114 | 0
80080 | GWINDT11A | 4 | South | YES | -0.070135 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 19 |  |  |  |  | -0.20114 | 0
80080 | GWINDT11A | 2 | South | YES | -0.070135 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 41 |  |  |  |  | -0.20114 | 0
80080 | GWINDT11A | 1 | South | YES | -0.070135 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 94 |  |  |  |  | -0.20114 | 0
80081 | GWINDT21A | 4 | South | YES | -0.070135 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 22 |  |  |  |  | -0.20114 | 0
80081 | GWINDT21A | 1 | South | YES | -0.070135 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 94 |  |  |  |  | -0.20114 | 0
80081 | GWINDT21A | 3 | South | YES | -0.070135 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 43 |  |  |  |  | -0.20114 | 0
80081 | GWINDT21A | 2 | South | YES | -0.070135 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 36 |  |  |  |  | -0.20114 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.070135 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 50 |  |  |  |  | -0.20114 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.070135 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 148 |  |  |  |  | -0.20114 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.070135 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 50 |  |  |  |  | -0.20114 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.070135 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 55 |  |  |  |  | -0.20114 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.070221 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.20123 | 0 | 0 |  |  |  |  | -0.20123 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.070784 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.20179 | 0 | 0 |  |  |  |  | -0.20179 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.070843 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.20185 | 0 | 0 |  |  |  |  | -0.20185 | 0
8506 | VAL #1 | 1 | South | YES | -0.070946 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.20195 | 0 | 0 |  |  |  |  | -0.20195 | 0
8507 | VAL #2 | 2 | South | YES | -0.070946 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.20195 | 0 | 0 |  |  |  |  | -0.20195 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.07109 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.2021 | 0 | 0 |  |  |  |  | -0.2021 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.07109 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.2021 | 0 | 0 |  |  |  |  | -0.2021 | 0
80263 | B_DAVIS31A | 3 | South | YES | -0.07109 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.2021 | 180 | 180 |  |  |  |  | -0.2021 | -36.3774
80264 | B_DAVIS41A | 4 | South | YES | -0.07109 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.2021 | 180 | 180 |  |  |  |  | -0.2021 | -36.3774
8456 | COSW#1 | 1 | South | YES | -0.07125 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.20226 | 0 | 0 |  |  |  |  | -0.20226 | 0
8457 | COSW#2 | 2 | South | YES | -0.07125 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.20226 | 0 | 0 |  |  |  |  | -0.20226 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.071328 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.071328 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0
8562 | CNOPST1 | 3 | South | YES | -0.071328 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0
8442 | NBEC7 | 7 | South | YES | -0.071344 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.20235 | 367 | 367 |  |  |  |  | -0.20235 | -74.2626
8442 | NBEC7 | MB | South | YES | -0.071344 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.20235 | 0 | 0 |  |  |  |  | -0.20235 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.072739 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.072739 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.072739 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0
8930 | ICPGN10A | 1 | South | YES | -0.072739 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0
8931 | ICPGN20A | 2 | South | YES | -0.072739 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0
8932 | ICPGN30A | 3 | South | YES | -0.072739 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0
80223 | REYSHR G | 1 | South | YES | -0.072739 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0
8173 | VICEC51A | 5 | South | YES | -0.073157 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.20416 | 144 | 144 |  |  |  |  | -0.20416 | -29.3995
8174 | VICEC61A | 6 | South | YES | -0.073157 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.20416 | 188 | 188 |  |  |  |  | -0.20416 | -38.3827
5508 | RAYBURNCC9 | 1 | South | YES | -0.07442 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.20543 | 47.7 | 47.7 |  |  |  |  | -0.20543 | -9.7988
5509 | RAYBURNCC10 | 1 | South | YES | -0.07442 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.20543 | 37.3 | 37.3 |  |  |  |  | -0.20543 | -7.6624
5511 | RAYBURNCC7 | 1 | South | YES | -0.07442 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.20543 | 47.5 | 47.5 |  |  |  |  | -0.20543 | -9.7578
5512 | RAYBURNCC8 | 1 | South | YES | -0.07442 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.20543 | 49.3 | 49.3 |  |  |  |  | -0.20543 | -10.1275
8066 | DUP1V#1 | 1 | South | YES | -0.074513 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.20552 | 0 | 0 |  |  |  |  | -0.20552 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.075068 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.20607 | 22 | 22 |  |  |  |  | -0.20607 | -4.5336
5505 | RAYBURNGEN1 | 1 | South | YES | -0.075068 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.20607 | 11 | 11 |  |  |  |  | -0.20607 | -2.2668
5506 | RAYBURNGEN2 | 1 | South | YES | -0.075068 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.20607 | 11 | 11 |  |  |  |  | -0.20607 | -2.2668
80224 | VISTRONG1 | 1 | South | YES | -0.07682 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.20783 | 0 | 0 |  |  |  |  | -0.20783 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.07682 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.20783 | 0 | 0 |  |  |  |  | -0.20783 | 0
80227 | AIRCO G | 1 | South | YES | -0.077635 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.20864 | 0 | 0 |  |  |  |  | -0.20864 | 0
8147 | UCAR #2 | 10 | South | YES | -0.078169 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0
8148 | UCAR #1 | 2 | South | YES | -0.078169 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0
80137 | CSDR89 | 9 | South | YES | -0.078169 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0
80137 | CSDR89 | 8 | South | YES | -0.078169 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0
80138 | CSDR7 | 7 | South | YES | -0.078169 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0
80139 | CSDR56 | 6 | South | YES | -0.078169 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0
80139 | CSDR56 | 5 | South | YES | -0.078169 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0
80140 | CSDR11 | 11 | South | YES | -0.078169 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0
80226 | ALCOA G | 1 | South | YES | -0.081585 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.21259 | 0 | 0 |  |  |  |  | -0.21259 | 0
8134 | FOR #1 | 1 | South | YES | -0.082615 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
8138 | FOR #2 | 2 | South | YES | -0.082615 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
8153 | FOR #3 | 3 | South | YES | -0.082615 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
8154 | FOR #4 | 4 | South | YES | -0.082615 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
8155 | FOR #5 | 5 | South | YES | -0.082615 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
8156 | FOR #6 | 6 | South | YES | -0.082615 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
8157 | FOR #7 | 7 | South | YES | -0.082615 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
80051 | FOR #8 | 8 | South | YES | -0.082615 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
80052 | FOR #9 | 9 | South | YES | -0.082615 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
80053 | FOR #10 | 10 | South | YES | -0.082615 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.11917 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.25018 | 0 | 0 |  |  | 0 | 0 | -0.25018 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.11917 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.25018 | 0 | 0 |  |  | 0 | 0 | -0.25018 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753
48732 | CBE_GT2 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753
48733 | CBE_ST12 | 1 | Houston | YES | -0.11998 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.25099 | 105 | 105 |  |  | -12.5983 | 105 | -0.25099 | -26.354
48734 | CBE_GT3 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753
48735 | CBE_GT4 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753
48736 | CBE_ST34 | 1 | Houston | YES | -0.11998 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.25099 | 105 | 105 |  |  | -12.5983 | 105 | -0.25099 | -26.354
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.12405 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.25505 | 0 | 0 |  |  | 0 | 0 | -0.25505 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.13719 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.13719 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.13719 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.13719 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.13719 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.13719 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.13719 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.13719 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.13719 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.13719 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.13719 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.13719 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.13719 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.13719 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.13719 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.13719 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.13719 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.13719 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.13719 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.13719 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.1405 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.2715 | 0 | 0 |  |  | 0 | 0 | -0.2715 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.1405 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.2715 | 0 | 0 |  |  | 0 | 0 | -0.2715 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.14314 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.14314 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.14314 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.14314 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.15253 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.28354 | 0 | 0 |  |  | 0 | 0 | -0.28354 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.15264 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 651 |  |  | 0 | 0 | -0.28365 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.15264 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 564 |  |  | 0 | 0 | -0.28365 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.15264 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 603 |  |  | 0 | 0 | -0.28365 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.15272 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.28372 | 167.7 | 167.7 |  |  | -25.6108 | 167.7 | -0.28372 | -47.5806
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.15272 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.28372 | 166.4 | 166.4 |  |  | -25.4123 | 166.4 | -0.28372 | -47.2117
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.15272 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.28372 | 252.4 | 252.4 |  |  | -38.546 | 252.4 | -0.28372 | -71.612
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.15395 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.28495 | 0 | 0 |  |  | 0 | 0 | -0.28495 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.15422 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.28523 | 166 | 166 |  |  | -25.601 | 166 | -0.28523 | -47.3481
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.15422 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.28523 | 166 | 166 |  |  | -25.601 | 166 | -0.28523 | -47.3481
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.15422 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.28523 | 248 | 248 |  |  | -38.2473 | 248 | -0.28523 | -70.7369
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.15422 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.28523 | 546 | 546 |  |  | -84.2058 | 546 | -0.28523 | -155.7353
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.15422 | 591.2 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.28523 | 0 | 654 |  |  | 0 | 0 | -0.28523 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.15422 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.28523 | 13 | 13 |  |  | -2.0049 | 13 | -0.28523 | -3.708
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.16023 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.16023 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.16023 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.16023 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.16023 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.16023 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.16023 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.16023 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.16023 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.16023 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.16023 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.16023 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.16023 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.16023 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.16023 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.16281 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.29382 | 0 | 0 |  |  | 0 | 0 | -0.29382 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.16462 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.16462 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.16462 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.16462 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.16462 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.16531 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.16531 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.16531 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.16531 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687
48691 | GBY_73741085 | A | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687
48692 | GBY_81821075 | D | Houston | YES | -0.1662 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.29721 | 55 | 55 |  |  | -9.141 | 55 | -0.29721 | -16.3464
48692 | GBY_81821075 | C | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687
48693 | GBY_83841065 | F | Houston | YES | -0.1662 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.29721 | 54 | 54 |  |  | -8.9748 | 54 | -0.29721 | -16.0491
48693 | GBY_83841065 | E | Houston | YES | -0.1662 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.29721 | 57 | 57 |  |  | -9.4734 | 57 | -0.29721 | -16.9408
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.1666 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.29761 | 0 | 0 |  |  | 0 | 0 | -0.29761 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.1666 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.29761 | 0 | 0 |  |  | 0 | 0 | -0.29761 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.16693 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.29794 | 163.2 | 163.2 |  |  | -27.243 | 163.2 | -0.29794 | -48.6232
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.16693 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.29794 | 157.1 | 157.1 |  |  | -26.2247 | 157.1 | -0.29794 | -46.8058
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.16693 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.29794 | 157.5 | 157.5 |  |  | -26.2915 | 157.5 | -0.29794 | -46.925
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.16693 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.29794 | 157 | 157 |  |  | -26.208 | 157 | -0.29794 | -46.776
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.16693 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.29794 | 282 | 282 |  |  | -47.0743 | 282 | -0.29794 | -84.0181
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.16726 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.29827 | 0 | 0 |  |  | 0 | 0 | -0.29827 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.16758 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.29859 | 18 | 18 |  |  | -3.0164 | 18 | -0.29859 | -5.3745
48855 | SRB_GT211035 | B2 | Houston | YES | -0.16758 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.29859 | 12 | 12 |  |  | -2.0109 | 12 | -0.29859 | -3.583
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.1676 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.2986 | 176 | 176 |  |  | -29.4971 | 176 | -0.2986 | -52.5542
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.16762 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.29863 | 165 | 165 |  |  | -27.6575 | 165 | -0.29863 | -49.2735
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.16763 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.29864 | 0 | 0 |  |  | 0 | 0 | -0.29864 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.16763 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.29864 | 0 | 0 |  |  | 0 | 0 | -0.29864 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.16771 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.29871 | 213 | 213 |  |  | -35.7214 | 213 | -0.29871 | -63.6257
48845 | SOL_GT1 | 1 | Houston | YES | -0.16771 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.29872 | 16.2 | 16.2 |  |  | -2.7169 | 16.2 | -0.29872 | -4.8392
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.16772 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.16772 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.16772 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.16772 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.16773 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.29873 | 228 | 228 |  |  | -38.2413 | 228 | -0.29873 | -68.1108
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.16773 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.16773 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.16773 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.16818 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.16818 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.16818 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.16818 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.16881 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.29982 | 0 | 0 |  |  | 0 | 0 | -0.29982 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.16895 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.29995 | 42 | 42 |  |  | -7.0957 | 42 | -0.29995 | -12.598
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.16895 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.29995 | 42 | 42 |  |  | -7.0957 | 42 | -0.29995 | -12.598
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.16895 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.29995 | 39 | 39 |  |  | -6.5889 | 39 | -0.29995 | -11.6981
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.16895 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.29995 | 39 | 39 |  |  | -6.5889 | 39 | -0.29995 | -11.6981
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.16905 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.30005 | 0 | 0 |  |  | 0 | 0 | -0.30005 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.16905 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.30005 | 0 | 0 |  |  | 0 | 0 | -0.30005 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.16998 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.30099 | 107 | 107 |  |  | -18.188 | 107 | -0.30099 | -32.2057
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.16998 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.30099 | 108 | 108 |  |  | -18.3579 | 108 | -0.30099 | -32.5066
48875 | THW_3132 | A | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543
48875 | THW_3132 | B | Houston | YES | -0.16998 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.30099 | 53 | 53 |  |  | -9.009 | 53 | -0.30099 | -15.9523
48877 | THW_3334 | C | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543
48877 | THW_3334 | D | Houston | YES | -0.16998 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.30099 | 57 | 57 |  |  | -9.6889 | 57 | -0.30099 | -17.1563
48879 | THW_4142 | E | Houston | YES | -0.16998 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.30099 | 56 | 56 |  |  | -9.5189 | 56 | -0.30099 | -16.8553
48879 | THW_4142 | F | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543
48881 | THW_4344 | G | Houston | YES | -0.16998 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.30099 | 58 | 58 |  |  | -9.8589 | 58 | -0.30099 | -17.4573
48881 | THW_4344 | H | Houston | YES | -0.16998 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.30099 | 58 | 58 |  |  | -9.8589 | 58 | -0.30099 | -17.4573
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.17071 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.30171 | 746 | 746 |  |  | -127.3467 | 746 | -0.30171 | -225.0775
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.1711 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.3021 | 12 | 12 |  |  | -2.0532 | 12 | -0.3021 | -3.6252
49803 | EXN_15GT | 1 | Houston | YES | -0.17121 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.17121 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.17121 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.17121 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.17121 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.17121 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.17121 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.17121 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.17121 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.17121 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.17121 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.17169 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.3027 | 0 | 0 |  |  | 0 | 0 | -0.3027 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.17169 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.3027 | 0 | 0 |  |  | 0 | 0 | -0.3027 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.17171 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.30271 | 0 | 0 |  |  | 0 | 0 | -0.30271 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.17172 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.30273 | 744 | 744 |  |  | -127.7619 | 744 | -0.30273 | -225.2307
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.17175 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.17175 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.17175 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.17175 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.17175 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.17175 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.17175 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.17201 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.30302 | 0 | 0 |  |  | 0 | 0 | -0.30302 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.17299 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.304 | 162.8 | 162.8 |  |  | -28.1634 | 162.8 | -0.304 | -49.4913
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.17299 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.304 | 161.4 | 161.4 |  |  | -27.9212 | 161.4 | -0.304 | -49.0657
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.17299 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.304 | 158.9 | 158.9 |  |  | -27.4887 | 158.9 | -0.304 | -48.3057
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.17299 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.304 | 269.2 | 269.2 |  |  | -46.57 | 269.2 | -0.304 | -81.8369
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.17327 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.30428 | 398 | 398 |  |  | -68.9619 | 398 | -0.30428 | -121.1024
48885 | THW_5152 | B | Houston | YES | -0.17364 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.30465 | 59 | 59 |  |  | -10.2449 | 59 | -0.30465 | -17.9743
48885 | THW_5152 | A | Houston | YES | -0.17364 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.30465 | 58 | 58 |  |  | -10.0713 | 58 | -0.30465 | -17.6697
48886 | THW_5354 | D | Houston | YES | -0.17364 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.30465 | 58 | 58 |  |  | -10.0713 | 58 | -0.30465 | -17.6697
48886 | THW_5354 | C | Houston | YES | -0.17364 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.30465 | 57 | 57 |  |  | -9.8977 | 57 | -0.30465 | -17.365
48887 | THW_5556 | E | Houston | YES | -0.17364 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.30465 | 59 | 59 |  |  | -10.2449 | 59 | -0.30465 | -17.9743
48887 | THW_5556 | F | Houston | YES | -0.17364 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.30465 | 57 | 57 |  |  | -9.8977 | 57 | -0.30465 | -17.365
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.17877 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.17877 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.17877 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.17877 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.17877 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ Jewett to Singleton and Jewett to Singleton OL_ Gibbons to Singleton_ckt_75 |  | i_PTDF_INC_pt | 391 |  | CBE_ST34 | Unit at max
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.17877 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 | 0 | 0 |  |  | i_10pctunit | 28 |  | 167 | # units @ max
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.17877 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 | 0 | 0 | [5 empty] | 0.13835 | delta max
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.17877 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 | 0 | 0 | [5 empty] | Delta
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.17877 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 | 0 | 0 | Weighted Shift Factors |  |  |  | 1 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.17877 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 | 0 | 0 | North | 0.13101 |  |  | 2 | 0
48885 | THW_5152 | B | Houston | YES | -0.17364 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.30465 | 59 | 59 |  |  | -10.2449 | 59 | -0.30465 | -17.9743 | 0.0027268 | 0.003793 | Houston | -0.16396 |  |  | 3 | 0
48885 | THW_5152 | A | Houston | YES | -0.17364 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.30465 | 58 | 58 |  |  | -10.0713 | 58 | -0.30465 | -17.6697 | 0.0054073 | 0.0075217 |  |  |  |  | 4 | 0
48886 | THW_5354 | D | Houston | YES | -0.17364 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.30465 | 58 | 58 |  |  | -10.0713 | 58 | -0.30465 | -17.6697 | 0.0080878 | 0.01125 |  |  |  |  | 5 | 0
48886 | THW_5354 | C | Houston | YES | -0.17364 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.30465 | 57 | 57 |  |  | -9.8977 | 57 | -0.30465 | -17.365 | 0.010722 | 0.014915 |  |  |  |  | 6 | 0.0010662
48887 | THW_5556 | E | Houston | YES | -0.17364 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.30465 | 59 | 59 |  |  | -10.2449 | 59 | -0.30465 | -17.9743 | 0.013449 | 0.018708 |  |  |  |  | 7 | 0.0021144
48887 | THW_5556 | F | Houston | YES | -0.17364 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.30465 | 57 | 57 |  |  | -9.8977 | 57 | -0.30465 | -17.365 | 0.016083 | 0.022372 |  |  |  |  | 8 | 0.0031626
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.17327 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.30428 | 398 | 398 |  |  | -68.9619 | 398 | -0.30428 | -121.1024 | 0.034477 | 0.047928 |  |  |  |  | 9 | 0.0041927
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.17299 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.304 | 162.8 | 162.8 |  |  | -28.1634 | 162.8 | -0.304 | -49.4913 | 0.042001 | 0.058372 |  |  |  |  | 10 | 0.005259
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.17299 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.304 | 161.4 | 161.4 |  |  | -27.9212 | 161.4 | -0.304 | -49.0657 | 0.049461 | 0.068726 |  |  |  |  | 11 | 0.0062891
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.17299 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.304 | 158.9 | 158.9 |  |  | -27.4887 | 158.9 | -0.304 | -48.3057 | 0.056804 | 0.078919 |  |  |  |  | 12 | 0.01345
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.17299 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.304 | 269.2 | 269.2 |  |  | -46.57 | 269.2 | -0.304 | -81.8369 | 0.069246 | 0.096189 |  |  |  |  | 13 | 0.01637
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431 | 0.077195 | 0.10719 |  |  |  |  | 14 | 0.019265
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431 | 0.085144 | 0.1182 |  |  |  |  | 15 | 0.022115
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431 | 0.093093 | 0.1292 |  |  |  |  | 16 | 0.026943
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.17201 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.30302 | 0 | 0 |  |  | 0 | 0 | -0.30302 | 0 | 0.093093 | 0.1292 |  |  |  |  | 17 | 0.029997
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.17175 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 | 0.093093 | 0.1292 |  |  |  |  | 18 | 0.033051
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.17175 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 | 0.093093 | 0.1292 |  |  |  |  | 19 | 0.036106
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.17175 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 | 0.093093 | 0.1292 |  |  |  |  | 20 | 0.036106
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.17175 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 | 0.093093 | 0.1292 |  |  |  |  | 21 | 0.036106
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.17175 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 | 0.093093 | 0.1292 |  |  |  |  | 22 | 0.036106
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.17175 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 | 0.093093 | 0.1292 |  |  |  |  | 23 | 0.036106
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.17175 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 | 0.093093 | 0.1292 |  |  |  |  | 24 | 0.036106
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.17172 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.30273 | 744 | 744 |  |  | -127.7619 | 744 | -0.30273 | -225.2307 | 0.12748 | 0.17673 |  |  |  |  | 25 | 0.036106
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.17171 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.30271 | 0 | 0 |  |  | 0 | 0 | -0.30271 | 0 | 0.12748 | 0.17673 |  |  |  |  | 26 | 0.036106
48651 | EP_1_2 | 1 | Houston | YES | -0.17169 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.3027 | 0 | 0 |  |  | 0 | 0 | -0.3027 | 0 | 0.12748 | 0.17673 |  |  |  |  | 27 | 0.036106
48651 | EP_1_2 | 2 | Houston | YES | -0.17169 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.3027 | 0 | 0 |  |  | 0 | 0 | -0.3027 | 0 | 0.12748 | 0.17673 |  |  |  |  | 28 | 0.04925
49803 | EXN_15GT | 1 | Houston | YES | -0.17121 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 29 | 0.04925
49804 | EXN_16GT | 2 | Houston | YES | -0.17121 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 30 | 0.04925
49805 | EXN_17GT | 3 | Houston | YES | -0.17121 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 31 | 0.04925
49826 | EXN938GT | 5 | Houston | YES | -0.17121 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 32 | 0.04925
49828 | EXN941GT | 10 | Houston | YES | -0.17121 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 33 | 0.04925
49829 | EXN942GT | 11 | Houston | YES | -0.17121 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 34 | 0.04925
49830 | EXN943GT | 12 | Houston | YES | -0.17121 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 35 | 0.04925
49831 | EXN944GT | 13 | Houston | YES | -0.17121 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 36 | 0.04925
49832 | EXN945GT | 9 | Houston | YES | -0.17121 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 37 | 0.04925
49837 | EXN_GT | 4 | Houston | YES | -0.17121 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 38 | 0.04925
49838 | EXN_14GT | 14 | Houston | YES | -0.17121 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 | 0.12748 | 0.17673 |  |  |  |  | 39 | 0.04925
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.1711 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.3021 | 12 | 12 |  |  | -2.0532 | 12 | -0.3021 | -3.6252 | 0.12803 | 0.17749 |  |  |  |  | 40 | 0.04925
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.17071 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.30171 | 746 | 746 |  |  | -127.3467 | 746 | -0.30171 | -225.0775 | 0.16251 | 0.22499 |  |  |  |  | 41 | 0.04925
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.16998 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.30099 | 107 | 107 |  |  | -18.188 | 107 | -0.30099 | -32.2057 | 0.16746 | 0.23179 |  |  |  |  | 42 | 0.04925
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.16998 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.30099 | 108 | 108 |  |  | -18.3579 | 108 | -0.30099 | -32.5066 | 0.17245 | 0.23865 |  |  |  |  | 43 | 0.04946
48875 | THW_3132 | A | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543 | 0.17499 | 0.24214 |  |  |  |  | 44 | 0.06248
48875 | THW_3132 | B | Houston | YES | -0.16998 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.30099 | 53 | 53 |  |  | -9.009 | 53 | -0.30099 | -15.9523 | 0.17744 | 0.24551 |  |  |  |  | 45 | 0.064331
48877 | THW_3334 | C | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543 | 0.17998 | 0.249 |  |  |  |  | 46 | 0.066199
48877 | THW_3334 | D | Houston | YES | -0.16998 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.30099 | 57 | 57 |  |  | -9.6889 | 57 | -0.30099 | -17.1563 | 0.18261 | 0.25262 |  |  |  |  | 47 | 0.06715
48879 | THW_4142 | E | Houston | YES | -0.16998 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.30099 | 56 | 56 |  |  | -9.5189 | 56 | -0.30099 | -16.8553 | 0.1852 | 0.25618 |  |  |  |  | 48 | 0.068067
48879 | THW_4142 | F | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543 | 0.18774 | 0.25967 |  |  |  |  | 49 | 0.069019
48881 | THW_4344 | G | Houston | YES | -0.16998 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.30099 | 58 | 58 |  |  | -9.8589 | 58 | -0.30099 | -17.4573 | 0.19042 | 0.26335 |  |  |  |  | 50 | 0.070005
48881 | THW_4344 | H | Houston | YES | -0.16998 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.30099 | 58 | 58 |  |  | -9.8589 | 58 | -0.30099 | -17.4573 | 0.19311 | 0.26704 |  |  |  |  | 51 | 0.070974
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.16905 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.30005 | 0 | 0 |  |  | 0 | 0 | -0.30005 | 0 | 0.19311 | 0.26704 |  |  |  |  | 52 | 0.071925
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.16905 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.30005 | 0 | 0 |  |  | 0 | 0 | -0.30005 | 0 | 0.19311 | 0.26704 |  |  |  |  | 53 | 0.072928
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.16895 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.29995 | 42 | 42 |  |  | -7.0957 | 42 | -0.29995 | -12.598 | 0.19505 | 0.2697 |  |  |  |  | 54 | 0.073932
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.16895 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.29995 | 42 | 42 |  |  | -7.0957 | 42 | -0.29995 | -12.598 | 0.19699 | 0.27235 |  |  |  |  | 55 | 0.073932
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.16895 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.29995 | 39 | 39 |  |  | -6.5889 | 39 | -0.29995 | -11.6981 | 0.19879 | 0.27482 |  |  |  |  | 56 | 0.073932
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.16895 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.29995 | 39 | 39 |  |  | -6.5889 | 39 | -0.29995 | -11.6981 | 0.20059 | 0.27729 |  |  |  |  | 57 | 0.074649
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.16881 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.29982 | 0 | 0 |  |  | 0 | 0 | -0.29982 | 0 | 0.20059 | 0.27729 |  |  |  |  | 58 | 0.075366
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.16818 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0 | 0.20059 | 0.27729 |  |  |  |  | 59 | 0.076033
48821 | SHELLG2 | 2 | Houston | YES | -0.16818 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0 | 0.20059 | 0.27729 |  |  |  |  | 60 | 0.076699
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.16818 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0 | 0.20059 | 0.27729 |  |  |  |  | 61 | 0.076699
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.16818 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0 | 0.20059 | 0.27729 |  |  |  |  | 62 | 0.076699
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.16773 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0 | 0.20059 | 0.27729 |  |  |  |  | 63 | 0.076699
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.16773 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0 | 0.20059 | 0.27729 |  |  |  |  | 64 | 0.076699
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.16773 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0 | 0.20059 | 0.27729 |  |  |  |  | 65 | 0.076699
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.16773 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.29873 | 228 | 228 |  |  | -38.2413 | 228 | -0.29873 | -68.1108 | 0.21113 | 0.29166 |  |  |  |  | 66 | 0.076699
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.16772 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0 | 0.21113 | 0.29166 |  |  |  |  | 67 | 0.076699
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.16772 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0 | 0.21113 | 0.29166 |  |  |  |  | 68 | 0.076699
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.16772 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0 | 0.21113 | 0.29166 |  |  |  |  | 69 | 0.080534
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.16772 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0 | 0.21113 | 0.29166 |  |  |  |  | 70 | 0.080534
48845 | SOL_GT1 | 1 | Houston | YES | -0.16771 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.29872 | 16.2 | 16.2 |  |  | -2.7169 | 16.2 | -0.29872 | -4.8392 | 0.21188 | 0.29269 |  |  |  |  | 71 | 0.080534
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.16771 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.29871 | 213 | 213 |  |  | -35.7214 | 213 | -0.29871 | -63.6257 | 0.22172 | 0.30611 |  |  |  |  | 72 | 0.080534
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.16763 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.29864 | 0 | 0 |  |  | 0 | 0 | -0.29864 | 0 | 0.22172 | 0.30611 |  |  |  |  | 73 | 0.080534
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.16763 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.29864 | 0 | 0 |  |  | 0 | 0 | -0.29864 | 0 | 0.22172 | 0.30611 |  |  |  |  | 74 | 0.080807
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.16762 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.29863 | 165 | 165 |  |  | -27.6575 | 165 | -0.29863 | -49.2735 | 0.22935 | 0.31651 |  |  |  |  | 75 | 0.084389
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.1676 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.2986 | 176 | 176 |  |  | -29.4971 | 176 | -0.2986 | -52.5542 | 0.23748 | 0.3276 |  |  |  |  | 76 | 0.084389
48855 | SRB_GT211035 | B1 | Houston | YES | -0.16758 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.29859 | 18 | 18 |  |  | -3.0164 | 18 | -0.29859 | -5.3745 | 0.23831 | 0.32873 |  |  |  |  | 77 | 0.084389
48855 | SRB_GT211035 | B2 | Houston | YES | -0.16758 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.29859 | 12 | 12 |  |  | -2.0109 | 12 | -0.29859 | -3.583 | 0.23887 | 0.32949 |  |  |  |  | 78 | 0.087162
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.16726 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.29827 | 0 | 0 |  |  | 0 | 0 | -0.29827 | 0 | 0.23887 | 0.32949 |  |  |  |  | 79 | 0.090118
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.16693 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.29794 | 163.2 | 163.2 |  |  | -27.243 | 163.2 | -0.29794 | -48.6232 | 0.24641 | 0.33975 |  |  |  |  | 80 | 0.09042
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.16693 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.29794 | 157.1 | 157.1 |  |  | -26.2247 | 157.1 | -0.29794 | -46.8058 | 0.25367 | 0.34963 |  |  |  |  | 81 | 0.090621
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.16693 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.29794 | 157.5 | 157.5 |  |  | -26.2915 | 157.5 | -0.29794 | -46.925 | 0.26095 | 0.35953 |  |  |  |  | 82 | 0.090621
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.16693 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.29794 | 157 | 157 |  |  | -26.208 | 157 | -0.29794 | -46.776 | 0.26821 | 0.3694 |  |  |  |  | 83 | 0.09334
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.16693 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.29794 | 282 | 282 |  |  | -47.0743 | 282 | -0.29794 | -84.0181 | 0.28124 | 0.38713 |  |  |  |  | 84 | 0.095956
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.1666 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.29761 | 0 | 0 |  |  | 0 | 0 | -0.29761 | 0 | 0.28124 | 0.38713 |  |  |  |  | 85 | 0.098579
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.1666 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.29761 | 0 | 0 |  |  | 0 | 0 | -0.29761 | 0 | 0.28124 | 0.38713 |  |  |  |  | 86 | 0.10119
48691 | GBY_73741085 | B | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687 | 0.28341 | 0.39008 |  |  |  |  | 87 | 0.10589
48691 | GBY_73741085 | A | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687 | 0.28558 | 0.39303 |  |  |  |  | 88 | 0.10589
48692 | GBY_81821075 | D | Houston | YES | -0.1662 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.29721 | 55 | 55 |  |  | -9.141 | 55 | -0.29721 | -16.3464 | 0.28813 | 0.39648 |  |  |  |  | 89 | 0.10589
48692 | GBY_81821075 | C | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687 | 0.2903 | 0.39942 |  |  |  |  | 90 | 0.10667
48693 | GBY_83841065 | F | Houston | YES | -0.1662 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.29721 | 54 | 54 |  |  | -8.9748 | 54 | -0.29721 | -16.0491 | 0.29279 | 0.40281 |  |  |  |  | 91 | 0.10744
48693 | GBY_83841065 | E | Houston | YES | -0.1662 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.29721 | 57 | 57 |  |  | -9.4734 | 57 | -0.29721 | -16.9408 | 0.29543 | 0.40639 |  |  |  |  | 92 | 0.10835
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.16531 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0 | 0.29543 | 0.40639 |  |  |  |  | 93 | 0.10913
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.16531 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0 | 0.29543 | 0.40639 |  |  |  |  | 94 | 0.11002
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.16531 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0 | 0.29543 | 0.40639 |  |  |  |  | 95 | 0.11096
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.16531 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0 | 0.29543 | 0.40639 |  |  |  |  | 96 | 0.11096
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.16462 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 | 0.29543 | 0.40639 |  |  |  |  | 97 | 0.11096
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.16462 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 | 0.29543 | 0.40639 |  |  |  |  | 98 | 0.11096
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.16462 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 | 0.29543 | 0.40639 |  |  |  |  | 99 | 0.11096
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.16462 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 | 0.29543 | 0.40639 |  |  |  |  | 100 | 0.11096
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.16462 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 | 0.29543 | 0.40639 |  |  |  |  | 101 | 0.11096
48772 | PHR_GN2_2 | MB | Houston | YES | -0.16281 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.29382 | 0 | 0 |  |  | 0 | 0 | -0.29382 | 0 | 0.29543 | 0.40639 |  |  |  |  | 102 | 0.11096
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.16023 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 103 | 0.11096
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.16023 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 104 | 0.11096
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.16023 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 105 | 0.11096
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.16023 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 106 | 0.11096
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.16023 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 107 | 0.11096
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.16023 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 108 | 0.11096
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.16023 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 109 | 0.11096
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.16023 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 110 | 0.11096
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.16023 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 111 | 0.11096
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.16023 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 112 | 0.11096
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.16023 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 113 | 0.11096
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.16023 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 114 | 0.11096
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.16023 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 115 | 0.11096
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.16023 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 116 | 0.11096
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.16023 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 | 0.29543 | 0.40639 |  |  |  |  | 117 | 0.11096
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.15422 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.28523 | 166 | 166 |  |  | -25.601 | 166 | -0.28523 | -47.3481 | 0.3031 | 0.41638 |  |  |  |  | 118 | 0.11096
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.15422 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.28523 | 166 | 166 |  |  | -25.601 | 166 | -0.28523 | -47.3481 | 0.31077 | 0.42637 |  |  |  |  | 119 | 0.11096
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.15422 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.28523 | 248 | 248 |  |  | -38.2473 | 248 | -0.28523 | -70.7369 | 0.32223 | 0.4413 |  |  |  |  | 120 | 0.11096
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.15422 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.28523 | 546 | 546 |  |  | -84.2058 | 546 | -0.28523 | -155.7353 | 0.34747 | 0.47416 |  |  |  |  | 121 | 0.11328
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.15422 | 591.2 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.28523 | 0 | 654 |  |  | 0 | 0 | -0.28523 | 0 | 0.34747 | 0.47416 |  |  |  |  | 122 | 0.1156
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.15422 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.28523 | 13 | 13 |  |  | -2.0049 | 13 | -0.28523 | -3.708 | 0.34807 | 0.47494 |  |  |  |  | 123 | 0.11906
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.15395 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.28495 | 0 | 0 |  |  | 0 | 0 | -0.28495 | 0 | 0.34807 | 0.47494 |  |  |  |  | 124 | 0.12669
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.15272 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.28372 | 167.7 | 167.7 |  |  | -25.6108 | 167.7 | -0.28372 | -47.5806 | 0.35582 | 0.48498 |  |  |  |  | 125 | 0.12669
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.15272 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.28372 | 166.4 | 166.4 |  |  | -25.4123 | 166.4 | -0.28372 | -47.2117 | 0.36351 | 0.49495 |  |  |  |  | 126 | 0.12687
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.15272 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.28372 | 252.4 | 252.4 |  |  | -38.546 | 252.4 | -0.28372 | -71.612 | 0.37517 | 0.51006 |  |  |  |  | 127 | 0.12687
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.15264 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 651 |  |  | 0 | 0 | -0.28365 | 0 | 0.37517 | 0.51006 |  |  |  |  | 128 | 0.12916
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.15264 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 564 |  |  | 0 | 0 | -0.28365 | 0 | 0.37517 | 0.51006 |  |  |  |  | 129 | 0.13144
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.15264 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 603 |  |  | 0 | 0 | -0.28365 | 0 | 0.37517 | 0.51006 |  |  |  |  | 130 | 0.13488
48730 | MNS_GT | 1 | Houston | YES | -0.15253 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.28354 | 0 | 0 |  |  | 0 | 0 | -0.28354 | 0 | 0.37517 | 0.51006 |  |  |  |  | 131 | 0.13488
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.14314 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0 | 0.37517 | 0.51006 |  |  |  |  | 132 | 0.13488
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.14314 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0 | 0.37517 | 0.51006 |  |  |  |  | 133 | 0.13488
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.14314 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0 | 0.37517 | 0.51006 |  |  |  |  | 134 | 0.13488
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.14314 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0 | 0.37517 | 0.51006 |  |  |  |  | 135 | 0.13488
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.1405 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.2715 | 0 | 0 |  |  | 0 | 0 | -0.2715 | 0 | 0.37517 | 0.51006 |  |  |  |  | 136 | 0.13488
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.1405 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.2715 | 0 | 0 |  |  | 0 | 0 | -0.2715 | 0 | 0.37517 | 0.51006 |  |  |  |  | 137 | 0.13488
49851 | DOW17000 | 37 | Houston | YES | -0.13719 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 138 | 0.13488
49858 | DOW38100 | 31 | Houston | YES | -0.13719 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 139 | 0.13488
49859 | DOW38200 | 33 | Houston | YES | -0.13719 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 140 | 0.13488
49860 | DOW38300 | 32 | Houston | YES | -0.13719 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 141 | 0.13488
49862 | DOW39100 | 36 | Houston | YES | -0.13719 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 142 | 0.13488
49863 | DOW39200 | 35 | Houston | YES | -0.13719 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 143 | 0.13488
49865 | DOW41000 | 41 | Houston | YES | -0.13719 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 144 | 0.13488
49866 | DOW42000 | 42 | Houston | YES | -0.13719 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 145 | 0.13488
49869 | DOW49000 | 45 | Houston | YES | -0.13719 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 146 | 0.13488
49870 | DOW61000 | 61 | Houston | YES | -0.13719 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 147 | 0.13488
49871 | DOW62000 | 62 | Houston | YES | -0.13719 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 148 | 0.13488
49872 | DOW63000 | 63 | Houston | YES | -0.13719 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 149 | 0.13488
49873 | DOW64000 | 64 | Houston | YES | -0.13719 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 150 | 0.13488
49876 | DOW65000 | 65 | Houston | YES | -0.13719 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 151 | 0.13488
49877 | DOW66000 | 66 | Houston | YES | -0.13719 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 152 | 0.13488
49878 | DOW67000 | 67 | Houston | YES | -0.13719 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 153 | 0.13488
49882 | DOW81000 | 81 | Houston | YES | -0.13719 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 154 | 0.13488
49884 | DOW82000 | 82 | Houston | YES | -0.13719 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 155 | 0.13488
49885 | DOW83000 | 83 | Houston | YES | -0.13719 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 156 | 0.13488
49886 | DOW84000 | 84 | Houston | YES | -0.13719 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 | 0.37517 | 0.51006 |  |  |  |  | 157 | 0.13488
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.12405 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.25505 | 0 | 0 |  |  | 0 | 0 | -0.25505 | 0 | 0.37517 | 0.51006 |  |  |  |  | 158 | 0.13488
48731 | CBE_GT1 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753 | 0.37869 | 0.51408 |  |  |  |  | 159 | 0.13488
48732 | CBE_GT2 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753 | 0.3822 | 0.51811 |  |  |  |  | 160 | 0.13488
48733 | CBE_ST12 | 1 | Houston | YES | -0.11998 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.25099 | 105 | 105 |  |  | -12.5983 | 105 | -0.25099 | -26.354 | 0.38705 | 0.52367 |  |  |  |  | 161 | 0.13488
48734 | CBE_GT3 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753 | 0.39056 | 0.52769 |  |  |  |  | 162 | 0.1354
48735 | CBE_GT4 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753 | 0.39408 | 0.53172 |  |  |  |  | 163 | 0.13591
48736 | CBE_ST34 | 1 | Houston | YES | -0.11998 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.25099 | 105 | 105 |  |  | -12.5983 | 105 | -0.25099 | -26.354 | 0.39893 | 0.53728 |  |  |  |  | 164 | 0.13662
5911 | STP_GN1___1 | 1 | Houston | YES | -0.11917 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.25018 | 0 | 0 |  |  | 0 | 0 | -0.25018 | 0 | 0.39893 | 0.53728 |  |  |  |  | 165 | 0.13713
5912 | STP_GN2___2 | 2 | Houston | YES | -0.11917 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.25018 | 0 | 0 |  |  | 0 | 0 | -0.25018 | 0 | 0.39893 | 0.53728 |  |  |  |  | 166 | 0.13764
8134 | FOR #1 | 1 | South | YES | -0.082615 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 167 | 0.13835
8138 | FOR #2 | 2 | South | YES | -0.082615 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 168 | 0.13835
8153 | FOR #3 | 3 | South | YES | -0.082615 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 169 | 0.13835
8154 | FOR #4 | 4 | South | YES | -0.082615 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 170 | 0.13835
8155 | FOR #5 | 5 | South | YES | -0.082615 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 171 | 0.13835
8156 | FOR #6 | 6 | South | YES | -0.082615 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 172 | 0.13835
8157 | FOR #7 | 7 | South | YES | -0.082615 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 173 | 0.13835
80051 | FOR #8 | 8 | South | YES | -0.082615 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 174 | 0.13835
80052 | FOR #9 | 9 | South | YES | -0.082615 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 175 | 0.13835
80053 | FOR #10 | 10 | South | YES | -0.082615 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 | 0.39893 | 0.53728 |  |  |  |  | 176 | 0.13835
80226 | ALCOA G | 1 | South | YES | -0.081585 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.21259 | 0 | 0 |  |  |  |  | -0.21259 | 0 | 0.39893 | 0.53728 |  |  |  |  | 177 | 0.13835
8147 | UCAR #2 | 10 | South | YES | -0.078169 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 | 0.39893 | 0.53728 |  |  |  |  | 178 | 0.13835
8148 | UCAR #1 | 2 | South | YES | -0.078169 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 | 0.39893 | 0.53728 |  |  |  |  | 179 | 0.13835
80137 | CSDR89 | 9 | South | YES | -0.078169 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 | 0.39893 | 0.53728 |  |  |  |  | 180 | 0.13835
80137 | CSDR89 | 8 | South | YES | -0.078169 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 | 0.39893 | 0.53728 |  |  |  |  | 181 | 0.13835
80138 | CSDR7 | 7 | South | YES | -0.078169 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 | 0.39893 | 0.53728 |  |  |  |  | 182 | 0.13835
80139 | CSDR56 | 6 | South | YES | -0.078169 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 | 0.39893 | 0.53728 |  |  |  |  | 183 | 0.13835
80139 | CSDR56 | 5 | South | YES | -0.078169 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 | 0.39893 | 0.53728 |  |  |  |  | 184 | 0.13835
80140 | CSDR11 | 11 | South | YES | -0.078169 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 | 0.39893 | 0.53728 |  |  |  |  | 185 | 0.13835
80227 | AIRCO G | 1 | South | YES | -0.077635 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.20864 | 0 | 0 |  |  |  |  | -0.20864 | 0 | 0.39893 | 0.53728 |  |  |  |  | 186 | 0.13835
80224 | VISTRONG1 | 1 | South | YES | -0.07682 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.20783 | 0 | 0 |  |  |  |  | -0.20783 | 0 | 0.39893 | 0.53728 |  |  |  |  | 187 | 0.13835
80225 | VISTRONG2 | 2 | South | YES | -0.07682 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.20783 | 0 | 0 |  |  |  |  | -0.20783 | 0 | 0.39893 | 0.53728 |  |  |  |  | 188 | 0.13835
5503 | RAYBURNGEN3 | 1 | South | YES | -0.075068 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.20607 | 22 | 22 |  |  |  |  | -0.20607 | -4.5336 | 0.39995 | 0.53824 |  |  |  |  | 189 | 0.13835
5505 | RAYBURNGEN1 | 1 | South | YES | -0.075068 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.20607 | 11 | 11 |  |  |  |  | -0.20607 | -2.2668 | 0.40045 | 0.53872 |  |  |  |  | 190 | 0.13835
5506 | RAYBURNGEN2 | 1 | South | YES | -0.075068 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.20607 | 11 | 11 |  |  |  |  | -0.20607 | -2.2668 | 0.40096 | 0.53919 |  |  |  |  | 191 | 0.13835
8066 | DUP1V#1 | 1 | South | YES | -0.074513 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.20552 | 0 | 0 |  |  |  |  | -0.20552 | 0 | 0.40096 | 0.53919 |  |  |  |  | 192 | 0.13829
5508 | RAYBURNCC9 | 1 | South | YES | -0.07442 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.20543 | 47.7 | 47.7 |  |  |  |  | -0.20543 | -9.7988 | 0.40317 | 0.54126 |  |  |  |  | 193 | 0.13826
5509 | RAYBURNCC10 | 1 | South | YES | -0.07442 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.20543 | 37.3 | 37.3 |  |  |  |  | -0.20543 | -7.6624 | 0.40489 | 0.54288 |  |  |  |  | 194 | 0.13823
5511 | RAYBURNCC7 | 1 | South | YES | -0.07442 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.20543 | 47.5 | 47.5 |  |  |  |  | -0.20543 | -9.7578 | 0.40709 | 0.54494 |  |  |  |  | 195 | 0.13823
5512 | RAYBURNCC8 | 1 | South | YES | -0.07442 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.20543 | 49.3 | 49.3 |  |  |  |  | -0.20543 | -10.1275 | 0.40937 | 0.54708 |  |  |  |  | 196 | 0.13809
8173 | VICEC51A | 5 | South | YES | -0.073157 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.20416 | 144 | 144 |  |  |  |  | -0.20416 | -29.3995 | 0.41602 | 0.55328 |  |  |  |  | 197 | 0.13799
8174 | VICEC61A | 6 | South | YES | -0.073157 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.20416 | 188 | 188 |  |  |  |  | -0.20416 | -38.3827 | 0.42471 | 0.56138 |  |  |  |  | 198 | 0.13785
8926 | LGE_GT10A | 1 | South | YES | -0.072739 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 | 0.42471 | 0.56138 |  |  |  |  | 199 | 0.13771
8927 | LGE_GT20A | 2 | South | YES | -0.072739 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 | 0.42471 | 0.56138 |  |  |  |  | 200 | 0.13726
8928 | LGE_STG0A | 3 | South | YES | -0.072739 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 | 0.42471 | 0.56138 |  |  |  |  | 201 | 0.13667
8930 | ICPGN10A | 1 | South | YES | -0.072739 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 | 0.42471 | 0.56138 |  |  |  |  | 202 | 0.13667
8931 | ICPGN20A | 2 | South | YES | -0.072739 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 | 0.42471 | 0.56138 |  |  |  |  | 203 | 0.13667
8932 | ICPGN30A | 3 | South | YES | -0.072739 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 | 0.42471 | 0.56138 |  |  |  |  | 204 | 0.13667
80223 | REYSHR G | 1 | South | YES | -0.072739 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 | 0.42471 | 0.56138 |  |  |  |  | 205 | 0.13667
8442 | NBEC7 | 7 | South | YES | -0.071344 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.20235 | 367 | 367 |  |  |  |  | -0.20235 | -74.2626 | 0.44167 | 0.57705 |  |  |  |  | 206 | 0.13667
8442 | NBEC7 | MB | South | YES | -0.071344 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.20235 | 0 | 0 |  |  |  |  | -0.20235 | 0 | 0.44167 | 0.57705 |  |  |  |  | 207 | 0.13667
8560 | CNOPGT1 | 1 | South | YES | -0.071328 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0 | 0.44167 | 0.57705 |  |  |  |  | 208 | 0.13667
8561 | CNOPGT2 | 2 | South | YES | -0.071328 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0 | 0.44167 | 0.57705 |  |  |  |  | 209 | 0.13538
8562 | CNOPST1 | 3 | South | YES | -0.071328 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0 | 0.44167 | 0.57705 |  |  |  |  | 210 | 0.13538
8456 | COSW#1 | 1 | South | YES | -0.07125 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.20226 | 0 | 0 |  |  |  |  | -0.20226 | 0 | 0.44167 | 0.57705 |  |  |  |  | 211 | 0.13538
8457 | COSW#2 | 2 | South | YES | -0.07125 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.20226 | 0 | 0 |  |  |  |  | -0.20226 | 0 | 0.44167 | 0.57705 |  |  |  |  | 212 | 0.13538
8459 | B_DAVIS0B | MB | South | YES | -0.07109 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.2021 | 0 | 0 |  |  |  |  | -0.2021 | 0 | 0.44167 | 0.57705 |  |  |  |  | 213 | 0.13538
8460 | B_DAVIS0A | MB | South | YES | -0.07109 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.2021 | 0 | 0 |  |  |  |  | -0.2021 | 0 | 0.44167 | 0.57705 |  |  |  |  | 214 | 0.13538
80263 | B_DAVIS31A | 3 | South | YES | -0.07109 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.2021 | 180 | 180 |  |  |  |  | -0.2021 | -36.3774 | 0.44999 | 0.58473 |  |  |  |  | 215 | 0.13538
80264 | B_DAVIS41A | 4 | South | YES | -0.07109 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.2021 | 180 | 180 |  |  |  |  | -0.2021 | -36.3774 | 0.45831 | 0.5924 |  |  |  |  | 216 | 0.13538
8506 | VAL #1 | 1 | South | YES | -0.070946 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.20195 | 0 | 0 |  |  |  |  | -0.20195 | 0 | 0.45831 | 0.5924 |  |  |  |  | 217 | 0.13538
8507 | VAL #2 | 2 | South | YES | -0.070946 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.20195 | 0 | 0 |  |  |  |  | -0.20195 | 0 | 0.45831 | 0.5924 |  |  |  |  | 218 | 0.13474
8511 | OXY_CC0A | 1 | South | YES | -0.070843 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.20185 | 0 | 0 |  |  |  |  | -0.20185 | 0 | 0.45831 | 0.5924 |  |  |  |  | 219 | 0.1341
8461 | KOCH_UP0A | 1 | South | YES | -0.070784 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.20179 | 0 | 0 |  |  |  |  | -0.20179 | 0 | 0.45831 | 0.5924 |  |  |  |  | 220 | 0.1341
8517 | CELANEBI0A | 1 | South | YES | -0.070221 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.20123 | 0 | 0 |  |  |  |  | -0.20123 | 0 | 0.45831 | 0.5924 |  |  |  |  | 221 | 0.1341
80080 | GWINDT11A | 3 | South | YES | -0.070135 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 38 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 222 | 0.1341
80080 | GWINDT11A | 4 | South | YES | -0.070135 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 19 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 223 | 0.1341
80080 | GWINDT11A | 2 | South | YES | -0.070135 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 41 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 224 | 0.1341
80080 | GWINDT11A | 1 | South | YES | -0.070135 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 94 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 225 | 0.1341
80081 | GWINDT21A | 4 | South | YES | -0.070135 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 22 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 226 | 0.1341
80081 | GWINDT21A | 1 | South | YES | -0.070135 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 94 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 227 | 0.1341
80081 | GWINDT21A | 3 | South | YES | -0.070135 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 43 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 228 | 0.1341
80081 | GWINDT21A | 2 | South | YES | -0.070135 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 36 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 229 | 0.1341
80180 | PNSCALT11A | 2 | South | YES | -0.070135 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 50 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 230 | 0.1341
80180 | PNSCALT11A | 1 | South | YES | -0.070135 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 148 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 231 | 0.1341
80181 | PNSCALT21A | 2 | South | YES | -0.070135 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 50 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 232 | 0.1341
80181 | PNSCALT21A | 1 | South | YES | -0.070135 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 55 |  |  |  |  | -0.20114 | 0 | 0.45831 | 0.5924 |  |  |  |  | 233 | 0.1341
5932 | SI_RAY9 | 9 | South | YES | -0.069941 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.20095 | 38 | 38 |  |  |  |  | -0.20095 | -7.636 | 0.46006 | 0.59401 |  |  |  |  | 234 | 0.1341
5933 | SI_RAY6 | 6 | South | YES | -0.069941 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.20095 | 19.3 | 19.3 |  |  |  |  | -0.20095 | -3.8783 | 0.46096 | 0.59483 |  |  |  |  | 235 | 0.1341
5935 | SI_RAY10 | 10 | South | YES | -0.069941 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.20095 | 47 | 47 |  |  |  |  | -0.20095 | -9.4445 | 0.46313 | 0.59683 |  |  |  |  | 236 | 0.1341
80003 | MILHWYS | F | South | YES | -0.069941 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.20095 | 0 | 0 |  |  |  |  | -0.20095 | 0 | 0.46313 | 0.59683 |  |  |  |  | 237 | 0.13395
8936 | MVGN#1 | 1 | South | YES | -0.069624 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.20063 | 216.6 | 216.6 |  |  |  |  | -0.20063 | -43.4565 | 0.47314 | 0.606 |  |  |  |  | 238 | 0.13388
8937 | MVGN#2 | 2 | South | YES | -0.069624 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.20063 | 216.7 | 216.7 |  |  |  |  | -0.20063 | -43.4766 | 0.48315 | 0.61517 |  |  |  |  | 239 | 0.1337
8938 | MVGN#3 | 3 | South | YES | -0.069624 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.20063 | 250.9 | 250.9 |  |  |  |  | -0.20063 | -50.3382 | 0.49475 | 0.62579 |  |  |  |  | 240 | 0.1337
8981 | HECN1 | 1 | South | YES | -0.069623 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.20063 | 144.8 | 144.8 |  |  |  |  | -0.20063 | -29.0511 | 0.50144 | 0.63192 |  |  |  |  | 241 | 0.13286
8982 | HECN2 | 2 | South | YES | -0.069623 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.20063 | 144.1 | 144.1 |  |  |  |  | -0.20063 | -28.9107 | 0.5081 | 0.63803 |  |  |  |  | 242 | 0.13202
8983 | HECN3 | 3 | South | YES | -0.069623 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.20063 | 171.9 | 171.9 |  |  |  |  | -0.20063 | -34.4882 | 0.51605 | 0.6453 |  |  |  |  | 243 | 0.13104
8933 | FGNTS001 | 1 | South | YES | -0.0689 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.19991 | 146.5 | 146.5 |  |  |  |  | -0.19991 | -29.2863 | 0.52282 | 0.65148 |  |  |  |  | 244 | 0.13048
8934 | FGNTS101 | 2 | South | YES | -0.0689 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.19991 | 147.9 | 147.9 |  |  |  |  | -0.19991 | -29.5662 | 0.52965 | 0.65772 |  |  |  |  | 245 | 0.12992
8935 | FGNTS201 | 3 | South | YES | -0.0689 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.19991 | 173 | 173 |  |  |  |  | -0.19991 | -34.5838 | 0.53765 | 0.66502 |  |  |  |  | 246 | 0.12926
8161 | COLETO0A | 1 | South | YES | -0.066648 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.19765 | 0 | 633 |  |  |  |  | -0.19765 | 0 | 0.53765 | 0.66502 |  |  |  |  | 247 | 0.12867
88508 | FALFURRI | F | South | YES | -0.065356 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.19636 | 0 | 0 |  |  |  |  | -0.19636 | 0 | 0.53765 | 0.66502 |  |  |  |  | 248 | 0.12807
5728 | FALCONHYDRO2 | 2 | South | YES | -0.064599 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0 | 0.53765 | 0.66502 |  |  |  |  | 249 | 0.12737
5729 | FALCONHYDRO3 | 3 | South | YES | -0.064599 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0 | 0.53765 | 0.66502 |  |  |  |  | 250 | 0.12737
8048 | FALCONHYDRO1 | 1 | South | YES | -0.064599 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0 | 0.53765 | 0.66502 |  |  |  |  | 251 | 0.12737
88198 | BEEVILLE | F | South | YES | -0.063278 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.19428 | 0 | 0 |  |  |  |  | -0.19428 | 0 | 0.53765 | 0.66502 |  |  |  |  | 252 | 0.12737
88299 | ZAPATA | F | South | YES | -0.060485 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.19149 | 0 | 0 |  |  |  |  | -0.19149 | 0 | 0.53765 | 0.66502 |  |  |  |  | 253 | 0.12737
80012 | LAR | F | South | YES | -0.054418 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.18542 | 0 | 0 |  |  |  |  | -0.18542 | 0 | 0.53765 | 0.66502 |  |  |  |  | 254 | 0.12737
80265 | LARECU40A | 4 | South | YES | -0.054415 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.18542 | 100 | 100 |  |  |  |  | -0.18542 | -18.5421 | 0.54227 | 0.66893 |  |  |  |  | 255 | 0.12737
80266 | LARECU50A | 5 | South | YES | -0.054415 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.18542 | 100 | 100 |  |  |  |  | -0.18542 | -18.5421 | 0.54689 | 0.67285 |  |  |  |  | 256 | 0.12737
5903 | SANMIGUELGEN | 1 | South | YES | -0.053842 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.18485 | 0 | 396.3 |  |  |  |  | -0.18485 | 0 | 0.54689 | 0.67285 |  |  |  |  | 257 | 0.12737
8189 | CUECPL2A | 1 | South | YES | -0.050999 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.18201 | 0 | 0 |  |  |  |  | -0.18201 | 0 | 0.54689 | 0.67285 |  |  |  |  | 258 | 0.12666
5401 | CALAVER_JKS1 | 1 | South | YES | -0.048248 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.17925 | 0 | 562 |  |  |  |  | -0.17925 | 0 | 0.54689 | 0.67285 |  |  |  |  | 259 | 0.12595
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.047164 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.17817 | 155 | 155 |  |  |  |  | -0.17817 | -27.6164 | 0.55405 | 0.67867 |  |  |  |  | 260 | 0.12595
5477 | BRA_AVR1_ST | 1 | South | YES | -0.047164 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.17817 | 174 | 174 |  |  |  |  | -0.17817 | -31.0017 | 0.5621 | 0.68522 |  |  |  |  | 261 | 0.12595
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.047164 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.17817 | 155 | 155 |  |  |  |  | -0.17817 | -27.6164 | 0.56926 | 0.69104 |  |  |  |  | 262 | 0.12595
5890 | PEARSALLGEN1 | 1 | South | YES | -0.045752 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.17676 | 24 | 24 |  |  |  |  | -0.17676 | -4.2422 | 0.57037 | 0.69194 |  |  |  |  | 263 | 0.12462
5891 | PEARSALLGEN2 | 1 | South | YES | -0.045752 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.17676 | 24.3 | 24.3 |  |  |  |  | -0.17676 | -4.2952 | 0.57149 | 0.69285 |  |  |  |  | 264 | 0.12312
5892 | PEARSALLGEN3 | 1 | South | YES | -0.045752 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.17676 | 23.9 | 23.9 |  |  |  |  | -0.17676 | -4.2245 | 0.5726 | 0.69374 |  |  |  |  | 265 | 0.12178
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.045713 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.17672 | 215 | 215 |  |  |  |  | -0.17672 | -37.9947 | 0.58253 | 0.70175 |  |  |  |  | 266 | 0.12157
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.045713 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.17672 | 216 | 216 |  |  |  |  | -0.17672 | -38.1714 | 0.59252 | 0.70981 |  |  |  |  | 267 | 0.12135
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.045597 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.1766 | 61 | 61 |  |  |  |  | -0.1766 | -10.7728 | 0.59533 | 0.71208 |  |  |  |  | 268 | 0.12114
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.045597 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.1766 | 95 | 95 |  |  |  |  | -0.1766 | -16.7773 | 0.59973 | 0.71562 |  |  |  |  | 269 | 0.11922
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.045597 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.1766 | 151 | 151 |  |  |  |  | -0.1766 | -26.6671 | 0.6067 | 0.72125 |  |  |  |  | 270 | 0.11729
5264 | LEON_LCP3G3 | 3 | South | YES | -0.045592 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.1766 | 58 | 58 |  |  |  |  | -0.1766 | -10.2427 | 0.60938 | 0.72341 |  |  |  |  | 271 | 0.11675
5265 | LEON_LCP4G4 | 4 | South | YES | -0.045592 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.1766 | 89 | 89 |  |  |  |  | -0.1766 | -15.7173 | 0.6135 | 0.72673 |  |  |  |  | 272 | 0.1159
5266 | LEON_LCPCT1 | 1 | South | YES | -0.045592 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.1766 | 44 | 44 |  |  |  |  | -0.1766 | -7.7703 | 0.61553 | 0.72837 |  |  |  |  | 273 | 0.11455
5267 | LEON_LCPCT2 | 2 | South | YES | -0.045592 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.1766 | 44 | 44 |  |  |  |  | -0.1766 | -7.7703 | 0.61756 | 0.73001 |  |  |  |  | 274 | 0.11403
5268 | LEON_LCPCT3 | 3 | South | YES | -0.045592 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.1766 | 43 | 43 |  |  |  |  | -0.1766 | -7.5937 | 0.61955 | 0.73161 |  |  |  |  | 275 | 0.11323
5269 | LEON_LCPCT4 | 4 | South | YES | -0.045592 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.1766 | 45 | 45 |  |  |  |  | -0.1766 | -7.9469 | 0.62163 | 0.73329 |  |  |  |  | 276 | 0.11284
5111 | CALAVER_JTD1 | 1 | South | YES | -0.04556 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.17657 | 0 | 430 |  |  |  |  | -0.17657 | 0 | 0.62163 | 0.73329 |  |  |  |  | 277 | 0.11244
5112 | CALAVER_JTD2 | 2 | South | YES | -0.04556 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.17657 | 0 | 430 |  |  |  |  | -0.17657 | 0 | 0.62163 | 0.73329 |  |  |  |  | 278 | 0.11206
5396 | CALAVER_OWS1 | 1 | South | YES | -0.045555 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.17656 | 418 | 418 |  |  |  |  | -0.17656 | -73.8027 | 0.64095 | 0.74886 |  |  |  |  | 279 | 0.11166
5397 | CALAVER_OWS2 | 2 | South | YES | -0.045555 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.17656 | 400 | 400 |  |  |  |  | -0.17656 | -70.6246 | 0.65944 | 0.76377 |  |  |  |  | 280 | 0.11166
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.045528 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.17653 | 407 | 407 |  |  |  |  | -0.17653 | -71.8495 | 0.67825 | 0.77893 |  |  |  |  | 281 | 0.11166
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.044531 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.17554 | 147 | 147 |  |  |  |  | -0.17554 | -25.804 | 0.68504 | 0.78437 |  |  |  |  | 282 | 0.10791
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.044531 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.17554 | 138 | 138 |  |  |  |  | -0.17554 | -24.2242 | 0.69142 | 0.78948 |  |  |  |  | 283 | 0.10433
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.044531 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.17554 | 146 | 146 |  |  |  |  | -0.17554 | -25.6285 | 0.69817 | 0.79489 |  |  |  |  | 284 | 0.10068
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.044531 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.17554 | 149 | 149 |  |  |  |  | -0.17554 | -26.1551 | 0.70505 | 0.80041 |  |  |  |  | 285 | 0.099332
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.044531 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.17554 | 182 | 182 |  |  |  |  | -0.17554 | -31.9478 | 0.71346 | 0.80715 |  |  |  |  | 286 | 0.098066
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.044531 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.17554 | 203 | 203 |  |  |  |  | -0.17554 | -35.6341 | 0.72285 | 0.81467 |  |  |  |  | 287 | 0.096726
58909 | PEARSALLSCG1 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72323 | 0.81498 |  |  |  |  | 288 | 0.095359
58909 | PEARSALLSCG1 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72362 | 0.81529 |  |  |  |  | 289 | 0.09369
58909 | PEARSALLSCG1 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72401 | 0.8156 |  |  |  |  | 290 | 0.091828
58909 | PEARSALLSCG1 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.7244 | 0.81591 |  |  |  |  | 291 | 0.091749
58909 | PEARSALLSCG1 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72479 | 0.81622 |  |  |  |  | 292 | 0.09167
58909 | PEARSALLSCG1 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72517 | 0.81653 |  |  |  |  | 293 | 0.091591
58919 | PEARSALLSCG2 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72556 | 0.81684 |  |  |  |  | 294 | 0.091512
58919 | PEARSALLSCG2 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72595 | 0.81715 |  |  |  |  | 295 | 0.091434
58919 | PEARSALLSCG2 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72634 | 0.81746 |  |  |  |  | 296 | 0.091355
58919 | PEARSALLSCG2 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72673 | 0.81777 |  |  |  |  | 297 | 0.091276
58919 | PEARSALLSCG2 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72712 | 0.81808 |  |  |  |  | 298 | 0.091197
58919 | PEARSALLSCG2 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.7275 | 0.81839 |  |  |  |  | 299 | 0.091118
58929 | PEARSALLSCG3 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72789 | 0.8187 |  |  |  |  | 300 | 0.09104
58929 | PEARSALLSCG3 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72828 | 0.81901 |  |  |  |  | 301 | 0.090961
58929 | PEARSALLSCG3 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72867 | 0.81931 |  |  |  |  | 302 | 0.090882
58929 | PEARSALLSCG3 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72906 | 0.81962 |  |  |  |  | 303 | 0.090803
58929 | PEARSALLSCG3 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72945 | 0.81993 |  |  |  |  | 304 | 0.090724
58929 | PEARSALLSCG3 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.72983 | 0.82024 |  |  |  |  | 305 | 0.090646
58949 | PEARSALLSCG4 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.73022 | 0.82055 |  |  |  |  | 306 | 0.090567
58949 | PEARSALLSCG4 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.73061 | 0.82086 |  |  |  |  | 307 | 0.090488
58949 | PEARSALLSCG4 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.731 | 0.82117 |  |  |  |  | 308 | 0.090409
58949 | PEARSALLSCG4 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.73139 | 0.82148 |  |  |  |  | 309 | 0.09033
58949 | PEARSALLSCG4 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.73177 | 0.82179 |  |  |  |  | 310 | 0.090252
58949 | PEARSALLSCG4 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 | 0.73216 | 0.8221 |  |  |  |  | 311 | 0.090173
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.042542 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.17355 | 0 | 0 |  |  |  |  | -0.17355 | 0 | 0.73216 | 0.8221 |  |  |  |  | 312 | 0.090094
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.042542 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.17355 | 0 | 0 |  |  |  |  | -0.17355 | 0 | 0.73216 | 0.8221 |  |  |  |  | 313 | 0.090015
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.040794 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.1718 | 0 | 0 |  |  |  |  | -0.1718 | 0 | 0.73216 | 0.8221 |  |  |  |  | 314 | 0.089936
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.040116 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.17112 | 148 | 148 |  |  |  |  | -0.17112 | -25.3261 | 0.739 | 0.82744 |  |  |  |  | 315 | 0.089936
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.040116 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.17112 | 148 | 148 |  |  |  |  | -0.17112 | -25.3261 | 0.74584 | 0.83279 |  |  |  |  | 316 | 0.089936
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.040116 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.17112 | 154 | 154 |  |  |  |  | -0.17112 | -26.3529 | 0.75296 | 0.83835 |  |  |  |  | 317 | 0.089936
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.040116 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.17112 | 293 | 293 |  |  |  |  | -0.17112 | -50.1389 | 0.7665 | 0.84893 |  |  |  |  | 318 | 0.088441
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.039626 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 | 0.7665 | 0.84893 |  |  |  |  | 319 | 0.086945
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.039626 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 | 0.7665 | 0.84893 |  |  |  |  | 320 | 0.085389
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.039626 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 | 0.7665 | 0.84893 |  |  |  |  | 321 | 0.082428
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.037052 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.16806 | 0 | 436 |  |  |  |  | -0.16806 | 0 | 0.7665 | 0.84893 |  |  |  |  | 322 | 0.082428
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.036911 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.16792 | 0 | 606 |  |  |  |  | -0.16792 | 0 | 0.7665 | 0.84893 |  |  |  |  | 323 | 0.082428
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.036911 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.16792 | 0 | 598 |  |  |  |  | -0.16792 | 0 | 0.7665 | 0.84893 |  |  |  |  | 324 | 0.082428
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.035416 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.16642 | 223.9 | 223.9 |  |  |  |  | -0.16642 | -37.262 | 0.77685 | 0.85679 |  |  |  |  | 325 | 0.082428
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.035416 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.16642 | 225 | 225 |  |  |  |  | -0.16642 | -37.445 | 0.78725 | 0.86469 |  |  |  |  | 326 | 0.082428
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.035416 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.16642 | 224.6 | 224.6 |  |  |  |  | -0.16642 | -37.3785 | 0.79763 | 0.87258 |  |  |  |  | 327 | 0.082428
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.035416 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.16642 | 226.7 | 226.7 |  |  |  |  | -0.16642 | -37.728 | 0.80811 | 0.88054 |  |  |  |  | 328 | 0.079943
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 | 0.81042 | 0.8823 |  |  |  |  | 329 | 0.077447
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 | 0.81273 | 0.88405 |  |  |  |  | 330 | 0.074954
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 | 0.81504 | 0.88581 |  |  |  |  | 331 | 0.072438
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 | 0.81735 | 0.88756 |  |  |  |  | 332 | 0.071883
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.030613 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.16162 | 0 | 0 |  |  |  |  | -0.16162 | 0 | 0.81735 | 0.88756 |  |  |  |  | 333 | 0.071327
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.020362 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.15137 | 132 | 132 |  |  |  |  | -0.15137 | -19.9806 | 0.82345 | 0.89178 |  |  |  |  | 334 | 0.070772
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.020362 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.15137 | 139 | 139 |  |  |  |  | -0.15137 | -21.0402 | 0.82987 | 0.89622 |  |  |  |  | 335 | 0.070216
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.020362 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.15137 | 329 | 329 |  |  |  |  | -0.15137 | -49.8002 | 0.84508 | 0.90673 |  |  |  |  | 336 | 0.070216
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.018765 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.14977 | 158 | 158 |  |  |  |  | -0.14977 | -23.6639 | 0.85238 | 0.91172 |  |  |  |  | 337 | 0.068332
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.018765 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.14977 | 160 | 160 |  |  |  |  | -0.14977 | -23.9634 | 0.85978 | 0.91678 |  |  |  |  | 338 | 0.066348
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.018765 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.14977 | 175 | 175 |  |  |  |  | -0.14977 | -26.21 | 0.86786 | 0.92231 |  |  |  |  | 339 | 0.061652
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.016728 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.14773 | 152.5 | 152.5 |  |  |  |  | -0.14773 | -22.5295 | 0.87491 | 0.92707 |  |  |  |  | 340 | 0.059343
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.016728 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.14773 | 149.5 | 149.5 |  |  |  |  | -0.14773 | -22.0863 | 0.88182 | 0.93173 |  |  |  |  | 341 | 0.057006
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.016728 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.14773 | 232.6 | 232.6 |  |  |  |  | -0.14773 | -34.363 | 0.89257 | 0.93898 |  |  |  |  | 342 | 0.054449
8262 | ELPS | 1 | South | YES | -0.014943 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.14595 | 0 | 0 |  |  |  |  | -0.14595 | 0 | 0.89257 | 0.93898 |  |  |  |  | 343 | 0.052155
9016 | SANDH_G1 | 1 | South | YES | -0.013106 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.14411 | 49 | 49 |  |  |  |  | -0.14411 | -7.0615 | 0.89483 | 0.94047 |  |  |  |  | 344 | 0.049906
9017 | SANDH_G2 | 2 | South | YES | -0.013106 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.14411 | 46 | 46 |  |  |  |  | -0.14411 | -6.6292 | 0.89696 | 0.94187 |  |  |  |  | 345 | 0.046408
9018 | SANDH_G3 | 3 | South | YES | -0.013106 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.14411 | 46 | 46 |  |  |  |  | -0.14411 | -6.6292 | 0.89909 | 0.94327 |  |  |  |  | 346 | 0.046408
9019 | SANDH_G4 | 4 | South | YES | -0.013106 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.14411 | 47 | 47 |  |  |  |  | -0.14411 | -6.7733 | 0.90126 | 0.9447 |  |  |  |  | 347 | 0.045633
9020 | SANDHG5A | 5A | South | YES | -0.013106 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.14411 | 155 | 155 |  |  |  |  | -0.14411 | -22.3374 | 0.90842 | 0.94941 |  |  |  |  | 348 | 0.044906
9021 | SANDHG5C | 5C | South | YES | -0.013106 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.14411 | 148 | 148 |  |  |  |  | -0.14411 | -21.3286 | 0.91526 | 0.95391 |  |  |  |  | 349 | 0.044179
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.011802 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.14281 | 0 | 0 |  |  |  |  | -0.14281 | 0 | 0.91526 | 0.95391 |  |  |  |  | 350 | 0.043437
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.011802 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.14281 | 0 | 0 |  |  |  |  | -0.14281 | 0 | 0.91526 | 0.95391 |  |  |  |  | 351 | 0.040987
9000 | DECKR_G1 | 1 | South | YES | -0.01167 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.14268 | 321 | 321 |  |  |  |  | -0.14268 | -45.7991 | 0.9301 | 0.96357 |  |  |  |  | 352 | 0.038648
9001 | DECKR_G2 | 2 | South | YES | -0.01167 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.14268 | 426 | 426 |  |  |  |  | -0.14268 | -60.7801 | 0.94979 | 0.9764 |  |  |  |  | 353 | 0.038648
9002 | DECKR_G3 | 3 | South | YES | -0.01061 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.14162 | 42 | 42 |  |  |  |  | -0.14162 | -5.9479 | 0.95173 | 0.97766 |  |  |  |  | 354 | 0.038648
9003 | DECKR_G4 | 4 | South | YES | -0.01061 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.14162 | 44 | 44 |  |  |  |  | -0.14162 | -6.2311 | 0.95376 | 0.97897 |  |  |  |  | 355 | 0.033477
9004 | DECKR_G5 | 5 | South | YES | -0.01061 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.14162 | 44 | 44 |  |  |  |  | -0.14162 | -6.2311 | 0.95579 | 0.98029 |  |  |  |  | 356 | 0.026615
9005 | DECKR_G6 | 6 | South | YES | -0.01061 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.14162 | 47 | 47 |  |  |  |  | -0.14162 | -6.656 | 0.95797 | 0.98169 |  |  |  |  | 357 | 0.025929
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.008874 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 | 0.95797 | 0.98169 |  |  |  |  | 358 | 0.02521
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.008874 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 | 0.95797 | 0.98169 |  |  |  |  | 359 | 0.024492
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.008874 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 | 0.95797 | 0.98169 |  |  |  |  | 360 | 0.023724
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.003738 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.13474 | 0 | 0 |  |  |  |  | -0.13474 | 0 | 0.95797 | 0.98169 |  |  |  |  | 361 | 0.023724
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.003738 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.13474 | 0 | 0 |  |  |  |  | -0.13474 | 0 | 0.95797 | 0.98169 |  |  |  |  | 362 | 0.023724
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.001256 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.13226 | 423.3 | 423.3 |  |  |  |  | -0.13226 | -55.9867 | 0.97753 | 0.9935 |  |  |  |  | 363 | 0.023724
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.00102 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.13203 | 0 | 0 |  |  |  |  | -0.13203 | 0 | 0.97753 | 0.9935 |  |  |  |  | 364 | 0.023724
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.00102 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.13203 | 0 | 0 |  |  |  |  | -0.13203 | 0 | 0.97753 | 0.9935 |  |  |  |  | 365 | 0.023724
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.13101 | 15 | 15 |  |  |  |  | -0.13101 | -1.9651 | 0.97822 | 0.99392 |  |  |  |  | 366 | 0.015975
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 367 | 0.015975
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 368 | 0.015975
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 369 | 0.015697
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 370 | 0.015697
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 371 | 0.015697
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 372 | 0.015697
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 373 | 0.015697
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 374 | 0.015697
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.13101 | 0 | 0 |  |  | 0 | 0 | -0.13101 | 0 | 0.97822 | 0.99392 |  |  |  |  | 375 | 0.015697
8032 | AMISTADHYD1 | 1 | South | YES | 0.000602 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 | 0.97822 | 0.99392 |  |  |  |  | 376 | 0.015697
8033 | AMISTADHYD2 | 2 | South | YES | 0.000602 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 | 0.97822 | 0.99392 |  |  |  |  | 377 | 0.015697
88253 | HAMILTON | F | South | YES | 0.000602 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 | 0.97822 | 0.99392 |  |  |  |  | 378 | 0.015697
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.007267 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.12374 | 0 | 0 |  |  |  |  | -0.12374 | 0 | 0.97822 | 0.99392 |  |  |  |  | 379 | 0.015697
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.007923 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 | 0.97822 | 0.99392 |  |  |  |  | 380 | 0.015697
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.007923 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 | 0.97822 | 0.99392 |  |  |  |  | 381 | 0.015697
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.007923 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 | 0.97822 | 0.99392 |  |  |  |  | 382 | 0.015697
3432 | SANDOW_4G | 4 | South | YES | 0.02338 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.10763 | 0 | 580 |  |  |  |  | -0.10763 | 0 | 0.97822 | 0.99392 |  |  |  |  | 383 | 0.015697
13432 | SANDOW_5G | 5 | South | YES | 0.044052 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.086954 | 0 | 581 |  |  |  |  | -0.086954 | 0 | 0.97822 | 0.99392 |  |  |  |  | 384 | 0.015697
48671 | FTR_GT1_5105 | 1 | North | YES | -0.22511 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | -0.06115 | 154.2 | 154.2 | -34.7117 | 154.2 |  |  | -0.06115 | -9.4294 | 0.98535 | 0.99591 |  |  |  |  | 385 | 0.015697
48672 | FTR_GT2_5110 | 2 | North | YES | -0.22511 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | -0.06115 | 159 | 159 | -35.7922 | 159 |  |  | -0.06115 | -9.7229 | 0.9927 | 0.99796 |  |  |  |  | 386 | 0.015697
48673 | FTR_GT3_5085 | 3 | North | YES | -0.22511 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | -0.06115 | 158 | 158 | -35.5671 | 158 |  |  | -0.06115 | -9.6618 | 1 | 1 |  |  |  |  | 387 | 0.015697
48674 | FTR_CN4_5095 | 4 | North | YES | -0.22511 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | -0.06115 | 380 | 380 | -85.541 | 380 |  |  | -0.06115 | -23.2372 | 1.0176 | 1.0049 |  |  |  |  | 388 | 0.01056
60202 | FRNDDRCS | F | West | YES | 0.0982 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.26216 | 0 | 0 |  |  |  |  | 0.26216 | 0 | [6 empty] | 389 | 0.0052633
3416 | LAKE_CRK1_G | 1 | North | YES | 0.10317 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.26713 | 75 | 75 | 7.7381 | 75 |  |  | 0.26713 | 20.0349 | [6 empty] | 390 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | 0.10317 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.26713 | 222 | 222 | 22.9046 | 222 |  |  | 0.26713 | 59.3032
3403 | THOUSE_1G | 1 | North | YES | 0.1042 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.26815 | 563 | 563 | 58.6629 | 563 |  |  | 0.26815 | 150.971
3404 | THOUSE_2G | 2 | North | YES | 0.1042 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.26815 | 807 | 807 | 84.087 | 807 |  |  | 0.26815 | 216.4007
238 | BOSQUESW505 | 1 | North | YES | 0.10599 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.26995 | 255 | 255 | 27.0277 | 255 |  |  | 0.26995 | 68.8369
239 | BOSQUESW502 | 1 | North | YES | 0.10599 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.26995 | 149 | 149 | 15.7927 | 149 |  |  | 0.26995 | 40.2223
247 | BOSQUESW501 | 2 | North | YES | 0.10599 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.26995 | 156 | 156 | 16.5346 | 156 |  |  | 0.26995 | 42.112
251 | BOSQUESW803 | 2 | North | YES | 0.10903 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.27299 | 150 | 150 | 16.3548 | 150 |  |  | 0.27299 | 40.9484
253 | BOSQUESW804 | 2 | North | YES | 0.10903 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.27299 | 80 | 80 | 8.7226 | 80 |  |  | 0.27299 | 21.8392
60018 | DSKY1 | 1 | West | YES | 0.10977 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.27373 | 0 | 84 |  |  |  |  | 0.27373 | 22.9931
60000 | DSKY2 | 1 | West | YES | 0.10996 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.27392 | 0 | 76.5 |  |  |  |  | 0.27392 | 20.9551
60017 | ORNNWP1 | 1 | West | YES | 0.11052 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.27447 | 0 | 80 |  |  |  |  | 0.27447 | 21.958
38437 | TNSRBNMESA9 | 1 | West | YES | 0.11273 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.27669 | 0 | 150 |  |  |  |  | 0.27669 | 41.5034
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.1128 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.27675 | 0 | 80 |  |  |  |  | 0.27675 | 22.1403
60016 | WOODWRD11A | 1 | West | YES | 0.11281 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.27677 | 0 | 80 |  |  |  |  | 0.27677 | 22.1414
6016 | SWMESA | 1 | West | YES | 0.11289 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.27685 | 0 | 75 |  |  |  |  | 0.27685 | 20.7634
60003 | KING_NE1A | 1 | West | YES | 0.11289 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27685 | 0 | 80 |  |  |  |  | 0.27685 | 22.1476
60005 | KING_SE1A | 1 | West | YES | 0.11289 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.27685 | 0 | 40 |  |  |  |  | 0.27685 | 11.0738
60201 | RIO DRCS | F | West | YES | 0.11301 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.27696 | 0 | 0 |  |  |  |  | 0.27696 | 0
60007 | KING_SW1A | 1 | West | YES | 0.11331 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27726 | 0 | 80 |  |  |  |  | 0.27726 | 22.181
60019 | KING_NW1A | 1 | West | YES | 0.11331 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27726 | 0 | 80 |  |  |  |  | 0.27726 | 22.181
244 | WHITNYDM01 | 1 | North | YES | 0.11339 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.27735 | 0 | 0 | 0 | 0 |  |  | 0.27735 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.11339 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.27735 | 0 | 0 | 0 | 0 |  |  | 0.27735 | 0
1349 | WESTXWIN_1G | 1 | West | YES | 0.11931 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.28326 | 0 | 6.6 |  |  |  |  | 0.28326 | 1.8695
1350 | NWPWRG1_1G | 1 | West | YES | 0.11931 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.28326 | 0 | 34.3 |  |  |  |  | 0.28326 | 9.716
60057 | CALLAHAN1A | 1 | West | YES | 0.11964 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.2836 | 0 | 114 |  |  |  |  | 0.2836 | 32.33
1002 | PBCTAGE_1G | A | West | YES | 0.11974 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.2837 | 66 | 66 |  |  |  |  | 0.2837 | 18.724
1003 | PBCTBGE_2G | B | West | YES | 0.11974 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.2837 | 66 | 66 |  |  |  |  | 0.2837 | 18.724
1004 | PBCTCGE_3G | C | West | YES | 0.11974 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.2837 | 67 | 67 |  |  |  |  | 0.2837 | 19.0077
1005 | PBCTDGE_4G | D | West | YES | 0.11974 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.2837 | 68 | 68 |  |  |  |  | 0.2837 | 19.2914
1006 | PBCTEGE_5G | E | West | YES | 0.11974 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.2837 | 67 | 67 |  |  |  |  | 0.2837 | 19.0077
1007 | PB5GEN_6G | 5 | West | YES | 0.11974 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.2837 | 114 | 114 |  |  |  |  | 0.2837 | 32.3415
1008 | PB6GEN_7G | 6 | West | YES | 0.11974 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.2837 | 515 | 515 |  |  |  |  | 0.2837 | 146.1042
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.11981 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.28376 | 0 | 35 |  |  |  |  | 0.28376 | 9.9318
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.11981 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.28376 | 0 | 30 |  |  |  |  | 0.28376 | 8.5129
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.11993 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.28389 | 0 | 112.5 |  |  |  |  | 0.28389 | 31.9377
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.11993 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 149.5 |  |  |  |  | 0.28389 | 42.4416
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.11993 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 186 |  |  |  |  | 0.28389 | 52.8036
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.11993 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 214.5 |  |  |  |  | 0.28389 | 60.8945
11147 | NOTREES_1G | 1 | West | YES | 0.11994 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.28389 | 0 | 149 |  |  |  |  | 0.28389 | 42.3001
76031 | L_GASCCR1_1N | W1 | West | YES | 0.12027 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.28423 | 0 | 150 |  |  |  |  | 0.28423 | 42.634
1320 | BSP 1 | 1 | West | YES | 0.12055 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.28451 | 0 | 0 |  |  |  |  | 0.28451 | 0
1326 | STANTONW_8 | 1 | West | YES | 0.12067 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.28463 | 0 | 100.5 |  |  |  |  | 0.28463 | 28.6051
11020 | TIEHVSG_1G | 1 | West | YES | 0.12071 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.28467 | 208.2 | 208.2 |  |  |  |  | 0.28467 | 59.2684
11021 | TIEHVCG_1G | 1 | West | YES | 0.12071 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.28467 | 142.1 | 142.1 |  |  |  |  | 0.28467 | 40.4517
11022 | TIEHVCG_2G | 1 | West | YES | 0.12071 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.28467 | 132.4 | 132.4 |  |  |  |  | 0.28467 | 37.6904
11023 | TIEHVCG_3G | 1 | West | YES | 0.12071 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.28467 | 137.4 | 137.4 |  |  |  |  | 0.28467 | 39.1137
11024 | TIEHVCG_4G | 1 | West | YES | 0.12071 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.28467 | 147 | 147 |  |  |  |  | 0.28467 | 41.8466
11025 | TIEHVSG_2G | 1 | West | YES | 0.12071 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.28467 | 213.2 | 213.2 |  |  |  |  | 0.28467 | 60.6918
11001 | NAV1CT | 1 | West | YES | 0.12072 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.28468 | 70.4 | 70.4 |  |  |  |  | 0.28468 | 20.0416
11009 | NAV2CT | 1 | West | YES | 0.12072 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.28468 | 71.4 | 71.4 |  |  |  |  | 0.28468 | 20.3263
11011 | NAV3ST | 1 | West | YES | 0.12072 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.28468 | 92.8 | 92.8 |  |  |  |  | 0.28468 | 26.4184
11012 | NAV4CT | 1 | West | YES | 0.12072 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28468 | 80 | 80 |  |  |  |  | 0.28468 | 22.7745
11013 | NAV5CT | 1 | West | YES | 0.12072 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28468 | 80 | 80 |  |  |  |  | 0.28468 | 22.7745
11014 | NAV6ST | 1 | West | YES | 0.12072 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.28468 | 115 | 115 |  |  |  |  | 0.28468 | 32.7384
1328 | OCOTILLO_1G | 1 | West | YES | 0.12078 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.28474 | 0 | 58 |  |  |  |  | 0.28474 | 16.515
1333 | MCDDONAL_8 | 1 | West | YES | 0.12095 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.28491 | 0 | 214.2 |  |  |  |  | 0.28491 | 61.028
1327 | WILDHRSE_1G | 1 | West | YES | 0.12116 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.28512 | 0 | 120 |  |  |  |  | 0.28512 | 34.2145
1360 | GUNSIGHT_8 | 1 | West | YES | 0.1212 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.28515 | 0 | 120 |  |  |  |  | 0.28515 | 34.2185
11320 | COYOTE_1G | 1 | West | YES | 0.12146 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.28541 | 0 | 225 |  |  |  |  | 0.28541 | 64.2183
11309 | BULLCREK_2G | 1 | West | YES | 0.12152 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.28548 | 0 | 180 |  |  |  |  | 0.28548 | 51.386
11310 | BULLCREK_1G | 1 | West | YES | 0.12152 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.28548 | 0 | 180 |  |  |  |  | 0.28548 | 51.386
1045 | CALENG1G_1G | 1 | West | YES | 0.12154 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.12154 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.12154 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0
1058 | LONGSHORE_5 | 1 | West | YES | 0.12173 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.28568 | 0 | 150 |  |  |  |  | 0.28568 | 42.8525
1058 | LONGSHORE_5 | 2 | West | YES | 0.12173 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.28568 | 0 | 220 |  |  |  |  | 0.28568 | 62.8504
11065 | ELBOWCK_1G | 1 | West | YES | 0.12173 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.28568 | 0 | 121.9 |  |  |  |  | 0.28568 | 34.8248
60058 | BUFF_GAP1A | 1 | West | YES | 0.12179 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.28574 | 0 | 120 |  |  |  |  | 0.28574 | 34.2893
60060 | CIRELLO | 1 | West | YES | 0.12179 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.28574 | 0 | 233 |  |  |  |  | 0.28574 | 66.5785
60063 | BUFF_GAP1B | 1 | West | YES | 0.12179 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.28574 | 0 | 170.2 |  |  |  |  | 0.28574 | 48.6337
60066 | H_HOLLOW1A | 1 | West | YES | 0.12179 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.28574 | 0 | 222 |  |  |  |  | 0.28574 | 63.4353
60068 | HHOLLOW21A | 1 | West | YES | 0.12179 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 184 |  |  |  |  | 0.28574 | 52.577
60070 | HHOLLOW31A | 1 | West | YES | 0.12179 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 224 |  |  |  |  | 0.28574 | 64.0068
60072 | HHOLLOW41A | 1 | West | YES | 0.12179 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 115 |  |  |  |  | 0.28574 | 32.8606
1037 | MORGAN5G_5G | 5 | West | YES | 0.12184 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.2858 | 137 | 137 |  |  |  |  | 0.2858 | 39.1545
1039 | MRGNAG_1G | A | West | YES | 0.12184 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.2858 | 69 | 69 |  |  |  |  | 0.2858 | 19.7202
1040 | MRGNBG_2G | B | West | YES | 0.12184 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.2858 | 71 | 71 |  |  |  |  | 0.2858 | 20.2918
1041 | MRGNCG_3G | C | West | YES | 0.12184 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.2858 | 70 | 70 |  |  |  |  | 0.2858 | 20.006
1042 | MRGNDG_4G | D | West | YES | 0.12184 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.2858 | 68 | 68 |  |  |  |  | 0.2858 | 19.4344
1043 | MRGNEG_5G | E | West | YES | 0.12184 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.2858 | 70 | 70 |  |  |  |  | 0.2858 | 20.006
1044 | MRGNFG_6G | F | West | YES | 0.12184 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.2858 | 66 | 66 |  |  |  |  | 0.2858 | 18.8628
6637 | SNYDERW1A | 1 | West | YES | 0.12188 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.28583 | 0 | 63 |  |  |  |  | 0.28583 | 18.0076
1068 | SCURRYCW_1G | 1 | West | YES | 0.12194 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.2859 | 0 | 141 |  |  |  |  | 0.2859 | 40.3118
1073 | SCURRYCW_2G | 2 | West | YES | 0.12194 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.2859 | 0 | 120 |  |  |  |  | 0.2859 | 34.3079
1061 | CIELOGEN_1G | 1 | West | YES | 0.12195 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.28591 | 0 | 99 |  |  |  |  | 0.28591 | 28.305
1062 | CIELOGEN_2G | 1 | West | YES | 0.12195 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.28591 | 0 | 61 |  |  |  |  | 0.28591 | 17.4405
1069 | KINDERMG_1G | 1 | West | YES | 0.12195 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.12195 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.12195 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0
36998 | RDCNYNG1 | 1 | West | YES | 0.12212 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.28608 | 0 | 84 |  |  |  |  | 0.28608 | 24.0306
1343 | TRENTIPP_8 | 1 | West | YES | 0.12222 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.28618 | 0 | 150 |  |  |  |  | 0.28618 | 42.9268
1354 | AEPWIND_8 | 1 | West | YES | 0.12222 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.28618 | 0 | 101 |  |  |  |  | 0.28618 | 28.904
6407 | TURKTRAK1A | 1 | West | YES | 0.12241 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.28637 | 0 | 169.5 |  |  |  |  | 0.28637 | 48.5393
71051 | L_BITTCR1_1N | W1 | West | YES | 0.12284 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 37.5 |  |  |  |  | 0.2868 | 10.7549
71054 | L_SWEETW1_1N | W1 | West | YES | 0.12284 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 107.5 |  |  |  |  | 0.2868 | 30.8306
71057 | L_SWEETW1_2N | W1 | West | YES | 0.12284 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 135 |  |  |  |  | 0.2868 | 38.7175
71059 | L_SWEETW1_3N | W1 | West | YES | 0.12284 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 119 |  |  |  |  | 0.2868 | 34.1288
71060 | L_SWEETW1_4N | W1 | West | YES | 0.12284 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 105 |  |  |  |  | 0.2868 | 30.1136
71061 | L_SWEETW1_5N | W1 | West | YES | 0.12284 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 80.5 |  |  |  |  | 0.2868 | 23.0871
6144 | MCADOO1A | 1 | West | YES | 0.12286 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.28682 | 0 | 150 |  |  |  |  | 0.28682 | 43.0231
11056 | ROSCOE_1G | 1 | West | YES | 0.12289 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.28685 | 0 | 209 |  |  |  |  | 0.28685 | 59.9507
11057 | CHAMPION_1G | 1 | West | YES | 0.12289 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.28685 | 0 | 126.5 |  |  |  |  | 0.28685 | 36.286
11058 | PYRON_1G | 1 | West | YES | 0.12289 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.28685 | 0 | 249 |  |  |  |  | 0.28685 | 71.4245
11059 | INADALE_1G | 1 | West | YES | 0.12289 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.28685 | 0 | 197 |  |  |  |  | 0.28685 | 56.5086
1643 | SLSTR1PP_1G | 1 | North | YES | 0.12319 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.28714 | 0 | 60 | 7.3912 | 60 |  |  | 0.28714 | 17.2287
1416 | SWETWATR_1G | 1 | West | YES | 0.12334 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.28729 | 30 | 30 |  |  |  |  | 0.28729 | 8.6188
1417 | SWETWATR_2G | 2 | West | YES | 0.12334 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.28729 | 72 | 72 |  |  |  |  | 0.28729 | 20.6852
1418 | SWETWATR_3G | 3 | West | YES | 0.12334 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.28729 | 68 | 68 |  |  |  |  | 0.28729 | 19.536
1419 | SWETWATR_4G | 4 | West | YES | 0.12334 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.28729 | 61 | 61 |  |  |  |  | 0.28729 | 17.525
60081 | WHRLWIND1A | 1 | West | YES | 0.12384 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.2878 | 0 | 60 |  |  |  |  | 0.2878 | 17.2679
1437 | MESQUITW_1G | 1 | North | YES | 0.12542 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.28938 | 0 | 400 | 50.1684 | 400 |  |  | 0.28938 | 115.7514
1438 | MESQUITW_2G | 1 | North | YES | 0.12543 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.28938 | 0 | 236 | 29.6005 | 236 |  |  | 0.28938 | 68.2945
1442 | COKFIELD_5 | 1 | North | YES | 0.12625 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.29021 | 0 | 165 | 20.8311 | 165 |  |  | 0.29021 | 47.8841
6100 | OKLA7A | EQ | West | YES | 0.12691 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.29087 | 0 | 0 |  |  |  |  | 0.29087 | 0
6752 | OKLA0A | 1 | West | YES | 0.12691 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.29087 | 0 | 649.7 |  |  |  |  | 0.29087 | 188.9753
1433 | GRHAMSES_1G | 1 | North | YES | 0.12811 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.29207 | 242 | 242 | 31.0024 | 242 |  |  | 0.29207 | 70.6801
332 | RWMILLER01 | 1 | North | YES | 0.12818 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.29214 | 73 | 73 | 9.3571 | 73 |  |  | 0.29214 | 21.326
333 | RWMILLER02 | 2 | North | YES | 0.12818 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.29214 | 119 | 119 | 15.2534 | 119 |  |  | 0.29214 | 34.7644
334 | RWMILLER03 | 3 | North | YES | 0.12818 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.29214 | 208 | 208 | 26.6614 | 208 |  |  | 0.29214 | 60.7646
335 | RWMILLER04 | 4 | North | YES | 0.12818 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.29214 | 102 | 102 | 13.0744 | 102 |  |  | 0.29214 | 29.798
336 | RWMILLER05 | 5 | North | YES | 0.12818 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.29214 | 101 | 101 | 12.9462 | 101 |  |  | 0.29214 | 29.5059
1432 | GRHAMSES_2G | 2 | North | YES | 0.12886 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.29281 | 366 | 366 | 47.1617 | 366 |  |  | 0.29281 | 107.1701
1479 | WFCOGEN_1G | 1 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.12897 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.12915 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.29311 | 0 | 120 | 15.4984 | 120 |  |  | 0.29311 | 35.1733
344 | MRSSHPRD | 1 | North | YES | 0.12934 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.2933 | 0 | 0 | 0 | 0 |  |  | 0.2933 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.12934 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.2933 | 0 | 0 | 0 | 0 |  |  | 0.2933 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.12969 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.29365 | 0 | 0 | 0 | 0 |  |  | 0.29365 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.12969 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.29365 | 0 | 0 | 0 | 0 |  |  | 0.29365 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.13052 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.29448 | 70 | 70 | 9.1363 | 70 |  |  | 0.29448 | 20.6133
1893 | DECRDOVA_3G | B | North | YES | 0.13052 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.29448 | 69 | 69 | 9.0057 | 69 |  |  | 0.29448 | 20.3188
1894 | DECRDOVA_4G | C | North | YES | 0.13052 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.29448 | 69 | 69 | 9.0057 | 69 |  |  | 0.29448 | 20.3188
1895 | DECRDOVA_5G | D | North | YES | 0.13052 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.29448 | 68 | 68 | 8.8752 | 68 |  |  | 0.29448 | 20.0243
503 | NTHTEXAS01 | 1 | North | YES | 0.13058 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.29454 | 18 | 18 | 2.3505 | 18 |  |  | 0.29454 | 5.3017
504 | NTHTEXAS02 | 2 | North | YES | 0.13058 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.29454 | 18 | 18 | 2.3505 | 18 |  |  | 0.29454 | 5.3017
505 | NTHTEXAS03 | 3 | North | YES | 0.13058 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.29454 | 38 | 38 | 4.9622 | 38 |  |  | 0.29454 | 11.1925
1898 | COMCHEPK_1G | 1 | North | YES | 0.1312 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.29515 | 0 | 0 | 0 | 0 |  |  | 0.29515 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.1312 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.29515 | 0 | 0 | 0 | 0 |  |  | 0.29515 | 0
1453 | WCPWRCO_1G | 1 | North | YES | 0.13141 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.29537 | 204 | 204 | 26.808 | 204 |  |  | 0.29537 | 60.2554
1454 | WCPWRCO_2G | 2 | North | YES | 0.13141 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.29537 | 204 | 204 | 26.808 | 204 |  |  | 0.29537 | 60.2554
1455 | WCPWRCO_3G | 3 | North | YES | 0.13141 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.29537 | 242 | 242 | 31.8017 | 242 |  |  | 0.29537 | 71.4794
1877 | WLFHOLW_1G | 1 | North | YES | 0.13156 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.29552 | 217.3 | 217.3 | 28.5884 | 217.3 |  |  | 0.29552 | 64.2164
1878 | WLFHOLW_2G | 2 | North | YES | 0.13156 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.29552 | 215.7 | 215.7 | 28.3779 | 215.7 |  |  | 0.29552 | 63.7436
1879 | WLFHOLW_3G | 3 | North | YES | 0.13156 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.29552 | 272.4 | 272.4 | 35.8375 | 272.4 |  |  | 0.29552 | 80.4995
1889 | DECRDOVA_1G | 1 | North | YES | 0.13182 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.29578 | 779 | 779 | 102.6917 | 779 |  |  | 0.29578 | 230.4146
580 | JCKCNTY801 | 1 | North | YES | 0.1323 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.29626 | 288 | 288 | 38.1024 | 288 |  |  | 0.29626 | 85.3222
581 | JCKCNTY802 | 2 | North | YES | 0.1323 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.29626 | 147 | 147 | 19.4481 | 147 |  |  | 0.29626 | 43.5499
582 | JCKCNTY803 | 3 | North | YES | 0.1323 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.29626 | 147 | 147 | 19.4481 | 147 |  |  | 0.29626 | 43.5499
1937 | MDLTHELP_5G | 5 | North | YES | 0.13269 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.29665 | 224 | 224 | 29.723 | 224 |  |  | 0.29665 | 66.4495
1938 | MDLTHELP_6G | 6 | North | YES | 0.13269 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.29665 | 226 | 226 | 29.9884 | 226 |  |  | 0.29665 | 67.0428
1943 | MDLTHELP_3G | 3 | North | YES | 0.13269 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.29665 | 212 | 212 | 28.1307 | 212 |  |  | 0.29665 | 62.8897
1944 | MDLTHELP_4G | 4 | North | YES | 0.13269 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.29665 | 211 | 211 | 27.998 | 211 |  |  | 0.29665 | 62.593
1861 | EAGLEMNT_1G | MB | North | YES | 0.13366 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.13366 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.13366 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0
1941 | MDLTHELP_1G | 1 | North | YES | 0.13411 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.29807 | 216.4 | 216.4 | 29.0221 | 216.4 |  |  | 0.29807 | 64.5025
1942 | MDLTHELP_2G | 2 | North | YES | 0.13411 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.29807 | 216.1 | 216.1 | 28.9818 | 216.1 |  |  | 0.29807 | 64.413
1947 | HANDLEY_3G | 3 | North | YES | 0.13422 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.29818 | 395 | 395 | 53.0173 | 395 |  |  | 0.29818 | 117.7805
1949 | HANDLEY_5G | 5 | North | YES | 0.13422 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.29818 | 435 | 435 | 58.3861 | 435 |  |  | 0.29818 | 129.7077
728 | WOLFRIDGE801 | 1 | North | YES | 0.13423 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.29819 | 0 | 112.5 | 15.1009 | 112.5 |  |  | 0.29819 | 33.5461
1948 | HANDLEY_4G | 4 | North | YES | 0.13446 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.29842 | 435 | 435 | 58.4914 | 435 |  |  | 0.29842 | 129.8129
923 | SPENCER_G4 | 1 | North | YES | 0.13553 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.29948 | 61 | 61 | 8.267 | 61 |  |  | 0.29948 | 18.2684
924 | SPENCER_G5 | 1 | North | YES | 0.13553 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.29948 | 66 | 66 | 8.9446 | 66 |  |  | 0.29948 | 19.7658
2381 | NTHLK1_G | 1 | North | YES | 0.13798 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.30194 | 156 | 156 | 21.5257 | 156 |  |  | 0.30194 | 47.103
2382 | NTHLK2_G | 2 | North | YES | 0.13798 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.30194 | 181 | 181 | 24.9753 | 181 |  |  | 0.30194 | 54.6516
2383 | NTHLK3_G | 3 | North | YES | 0.13798 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.30194 | 329 | 329 | 45.3971 | 329 |  |  | 0.30194 | 99.3391
12322 | ENNSTRAC_1G | 1 | North | YES | 0.13803 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.30199 | 196 | 196 | 27.0537 | 196 |  |  | 0.30199 | 59.1894
12323 | ENNSTRAC_2G | 2 | North | YES | 0.13803 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.30199 | 116 | 116 | 16.0114 | 116 |  |  | 0.30199 | 35.0304
2371 | COLLIN_1G | MB | North | YES | 0.13823 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.30219 | 0 | 0 | 0 | 0 |  |  | 0.30219 | 0
6948 | DENISNDM | 1 | North | YES | 0.13895 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.30291 | 0 | 0 | 0 | 0 |  |  | 0.30291 | 0
6948 | DENISNDM | 2 | North | YES | 0.13895 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.30291 | 0 | 0 | 0 | 0 |  |  | 0.30291 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.13918 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.30314 | 170 | 170 | 23.6606 | 170 |  |  | 0.30314 | 51.5334
1688 | VALLEY_2G | 2 | North | YES | 0.13918 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.30314 | 527 | 527 | 73.3479 | 527 |  |  | 0.30314 | 159.7535
2413 | MTCK6_G | 6 | North | YES | 0.13923 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.30319 | 118 | 118 | 16.4289 | 118 |  |  | 0.30319 | 35.7759
2414 | MTCK7_G | 7 | North | YES | 0.13923 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.30319 | 115 | 115 | 16.0112 | 115 |  |  | 0.30319 | 34.8663
2417 | MTCK8_G | 8 | North | YES | 0.13923 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.30319 | 556 | 556 | 77.4108 | 556 |  |  | 0.30319 | 168.5711
1689 | VALLEY_3G | 3 | North | YES | 0.13947 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.30343 | 375 | 375 | 52.3028 | 375 |  |  | 0.30343 | 113.7868
11691 | KMICHICT1_G | 1 | North | YES | 0.13947 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30343 | 144 | 144 | 20.0843 | 144 |  |  | 0.30343 | 43.6941
11692 | KMICHICT2_G | 2 | North | YES | 0.13947 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.30343 | 146 | 146 | 20.3632 | 146 |  |  | 0.30343 | 44.301
11693 | KMICHIST3_G | 3 | North | YES | 0.13947 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.30343 | 312 | 312 | 43.5159 | 312 |  |  | 0.30343 | 94.6706
11694 | KMICHICT4_G | 4 | North | YES | 0.13947 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30343 | 144 | 144 | 20.0843 | 144 |  |  | 0.30343 | 43.6941
11695 | KMICHICT5_G | 5 | North | YES | 0.13947 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.30343 | 148 | 148 | 20.6422 | 148 |  |  | 0.30343 | 44.9079
11696 | KMICHIST6_G | 6 | North | YES | 0.13947 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.30343 | 310 | 310 | 43.2369 | 310 |  |  | 0.30343 | 94.0638
1678 | LAMARPWR_1G | 1 | North | YES | 0.1396 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.30356 | 160 | 160 | 22.3365 | 160 |  |  | 0.30356 | 48.5697
1679 | LAMARPWR_2G | 2 | North | YES | 0.1396 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30356 | 156 | 156 | 21.7781 | 156 |  |  | 0.30356 | 47.3554
1680 | LAMARPWR_3G | 3 | North | YES | 0.1396 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.30356 | 196 | 196 | 27.3622 | 196 |  |  | 0.30356 | 59.4979
1681 | LAMARPWR_4G | 4 | North | YES | 0.1396 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30356 | 156 | 156 | 21.7781 | 156 |  |  | 0.30356 | 47.3554
1682 | LAMARPWR_5G | 5 | North | YES | 0.1396 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.30356 | 157 | 157 | 21.9177 | 157 |  |  | 0.30356 | 47.659
1683 | LAMARPWR_6G | 6 | North | YES | 0.1396 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.30356 | 198 | 198 | 27.6414 | 198 |  |  | 0.30356 | 60.105
1675 | PEC_1G | 1 | North | YES | 0.13969 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0
1676 | PEC_2G | 2 | North | YES | 0.13969 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0
1677 | PEC_3G | 3 | North | YES | 0.13969 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0
1701 | MOSES_1G | 1 | North | YES | 0.13983 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 558 | 78.0279 | 558 |  |  | 0.30379 | 169.5162
1702 | MOSES_2G | 2 | North | YES | 0.13983 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 579 | 80.9645 | 579 |  |  | 0.30379 | 175.8959
1703 | MOSES_3G | 3 | North | YES | 0.13983 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 808 | 112.9867 | 808 |  |  | 0.30379 | 245.4643
5925 | DCEAST | EQ | North | YES | 0.13983 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.30379 | 0 | 0 | 0 | 0 |  |  | 0.30379 | 0
842 | OLINGER_G1 | 1 | North | YES | 0.14013 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.30409 | 79 | 79 | 11.0701 | 79 |  |  | 0.30409 | 24.0228
843 | OLINGER_G2 | 1 | North | YES | 0.14013 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.30409 | 110 | 110 | 15.4141 | 110 |  |  | 0.30409 | 33.4494
844 | OLINGER_G3 | 1 | North | YES | 0.14013 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.30409 | 150 | 150 | 21.0192 | 150 |  |  | 0.30409 | 45.6128
845 | OLINGER_G4 | 1 | North | YES | 0.14013 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.30409 | 76 | 76 | 10.6497 | 76 |  |  | 0.30409 | 23.1105
837 | NEWMAN_G5 | 1 | North | YES | 0.14016 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.30412 | 40 | 40 | 5.6063 | 40 |  |  | 0.30412 | 12.1646
948 | STEAM1 | 1 | North | YES | 0.14031 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.30427 | 20 | 20 | 2.8063 | 20 |  |  | 0.30427 | 6.0855
949 | STEAM2 | 1 | North | YES | 0.14031 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.30427 | 26 | 26 | 3.6482 | 26 |  |  | 0.30427 | 7.9111
950 | STEAM3 | 1 | North | YES | 0.14031 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.30427 | 42 | 42 | 5.8932 | 42 |  |  | 0.30427 | 12.7794
12440 | PARKD_1SVC8 | 1 | North | YES | 0.14071 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30467 | 0 | 0 | 0 | 0 |  |  | 0.30467 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.14071 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30467 | 0 | 0 | 0 | 0 |  |  | 0.30467 | 0
2451 | LKHB1_G | 1 | North | YES | 0.14076 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.30471 | 391 | 391 | 55.036 | 391 |  |  | 0.30471 | 119.1434
2452 | LKHB2_G | 2 | North | YES | 0.14076 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.30471 | 516 | 516 | 72.6306 | 516 |  |  | 0.30471 | 157.2327
12411 | FPLEFR1A_G | 1 | North | YES | 0.14146 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.30542 | 161 | 161 | 22.7747 | 161 |  |  | 0.30542 | 49.1719
12412 | FPLEFR1B_G | 2 | North | YES | 0.14146 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.30542 | 164 | 164 | 23.1991 | 164 |  |  | 0.30542 | 50.0881
12413 | FPLEFR1C_G | 3 | North | YES | 0.14146 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.30542 | 164 | 164 | 23.1991 | 164 |  |  | 0.30542 | 50.0881
12414 | FPLEFR1S_G | 4 | North | YES | 0.14146 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.30542 | 414 | 414 | 58.5636 | 414 |  |  | 0.30542 | 126.442
12421 | FPLEFR2A_G | 1 | North | YES | 0.14146 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.30542 | 162 | 162 | 22.9162 | 162 |  |  | 0.30542 | 49.4773
12422 | FPLEFR2B_G | 2 | North | YES | 0.14146 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.30542 | 161 | 161 | 22.7747 | 161 |  |  | 0.30542 | 49.1719
12423 | FPLEFR2C_G | 3 | North | YES | 0.14146 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.30542 | 163 | 163 | 23.0577 | 163 |  |  | 0.30542 | 49.7827
12424 | FPLEFR2S_G | 4 | North | YES | 0.14146 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.30542 | 415 | 415 | 58.7051 | 415 |  |  | 0.30542 | 126.7474
3126 | TRINIDAD_6G | 1 | North | YES | 0.14175 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.30571 | 224 | 224 | 31.7531 | 224 |  |  | 0.30571 | 68.4796
3097 | MARTLAKE_1G | 1 | North | YES | 0.14521 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 790 | 114.7167 | 790 |  |  | 0.30917 | 244.2431
3098 | MARTLAKE_2G | 2 | North | YES | 0.14521 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 795 | 115.4427 | 795 |  |  | 0.30917 | 245.789
3099 | MARTLAKE_3G | 3 | North | YES | 0.14521 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 804 | 116.7496 | 804 |  |  | 0.30917 | 248.5715
13116 | TGATEWAY_1G | 1 | North | YES | 0.14572 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.30967 | 151 | 151 | 22.003 | 151 |  |  | 0.30967 | 46.7605
13117 | TGATEWAY_2G | 2 | North | YES | 0.14572 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.30967 | 130 | 130 | 18.9429 | 130 |  |  | 0.30967 | 40.2574
13118 | TGATEWAY_3G | 3 | North | YES | 0.14572 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.30967 | 148 | 148 | 21.5658 | 148 |  |  | 0.30967 | 45.8315
13119 | TGATEWAY_4G | 4 | North | YES | 0.14572 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.30967 | 399 | 399 | 58.1403 | 399 |  |  | 0.30967 | 123.5593
3348 | CHAMPION_1G | MB | North | YES | 0.14625 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0
3309 | ASPN_G | 1 | North | YES | 0.1463 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.31026 | 50 | 50 | 7.3151 | 50 |  |  | 0.31026 | 15.5129
3107 | STRYKER_1G | 1 | North | YES | 0.14652 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.31048 | 182 | 182 | 26.6668 | 182 |  |  | 0.31048 | 56.5071
3108 | STRYKER_2G | 2 | North | YES | 0.14652 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.31048 | 484 | 484 | 70.9162 | 484 |  |  | 0.31048 | 150.2716
13134 | CALFREST_4G | 4 | North | YES | 0.15119 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.31515 | 151.5 | 151.5 | 22.9053 | 151.5 |  |  | 0.31515 | 47.7448
13135 | CALFREST_5G | 5 | North | YES | 0.15119 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.31515 | 152.3 | 152.3 | 23.0262 | 152.3 |  |  | 0.31515 | 47.997
13136 | CALFREST_6G | 6 | North | YES | 0.15119 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.31515 | 177.5 | 177.5 | 26.8362 | 177.5 |  |  | 0.31515 | 55.9387
13131 | CALFREST_1G | 1 | North | YES | 0.15145 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.31541 | 150.7 | 150.7 | 22.8232 | 150.7 |  |  | 0.31541 | 47.5316
13132 | CALFREST_2G | 2 | North | YES | 0.15145 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.31541 | 151 | 151 | 22.8686 | 151 |  |  | 0.31541 | 47.6262
13133 | CALFREST_3G | 3 | North | YES | 0.15145 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.31541 | 177.4 | 177.4 | 26.8669 | 177.4 |  |  | 0.31541 | 55.9529
3381 | BBRN_1G | 1 | North | YES | 0.15256 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.31652 | 0 | 618 | 94.2839 | 618 |  |  | 0.31652 | 195.6097
3382 | BBRN_2G | 2 | North | YES | 0.15256 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.31652 | 0 | 589 | 89.8596 | 589 |  |  | 0.31652 | 186.4306
48721 | LEG_1___1 | 1 | North | YES | 0.17253 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.33648 | 0 | 827 | 142.6798 | 827 |  |  | 0.33648 | 278.2727
48722 | LEG_2___2 | 2 | North | YES | 0.17253 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.33648 | 0 | 819 | 141.2996 | 819 |  |  | 0.33648 | 275.5808
39960 | TNTNPONE_18 | 1 | North | YES | 0.1953 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.35926 | 0 | 152.3 | 29.7448 | 152.3 |  |  | 0.35926 | 54.7155
39970 | TNTNPONE_28 | 1 | North | YES | 0.1953 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.35926 | 0 | 153 | 29.8815 | 153 |  |  | 0.35926 | 54.967
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.22242 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.38638 | 48 | 48 | 10.6764 | 48 |  |  | 0.38638 | 18.5463
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.22242 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.38638 | 46 | 46 | 10.2315 | 46 |  |  | 0.38638 | 17.7735
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.22242 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.38638 | 105 | 105 | 23.3545 | 105 |  |  | 0.38638 | 40.5701
32886 | BRYN_ATKINS3 | MB | North | YES | 0.22931 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.22931 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.22931 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.39327 | 17 | 17 | 3.8983 | 17 |  |  | 0.39327 | 6.6856
32890 | BRYN_ATKINS4 | MB | North | YES | 0.22931 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.22931 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.23292 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.39688 | 32 | 32 | 7.4535 | 32 |  |  | 0.39688 | 12.7001
990 | GIBN_CREK_G1 | 1 | North | YES | 0.25699 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.42094 | 0 | 463 | 118.9841 | 463 |  |  | 0.42094 | 194.8964
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Bound Gen
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | max of zone correlation | -0.06115 |  |  | Neg PTDF weight | Pos PTDF weight
48674 | FTR_CN4_5095 | 4 | North | YES | -0.22511 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | -0.06115 | 380 | 380 | -85.541 | 380 |  |  | -0.06115 | -23.2372 |  |  |  |  | -23.2372 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | -0.22511 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | -0.06115 | 159 | 159 | -35.7922 | 159 |  |  | -0.06115 | -9.7229 |  |  |  |  | -9.7229 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | -0.22511 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | -0.06115 | 158 | 158 | -35.5671 | 158 |  |  | -0.06115 | -9.6618 |  |  |  |  | -9.6618 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | -0.22511 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | -0.06115 | 154.2 | 154.2 | -34.7117 | 154.2 |  |  | -0.06115 | -9.4294 |  |  | Weighted Shift Factors |  | -9.4294 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.044052 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.086954 | 0 | 581 |  |  |  |  | -0.086954 | 0 |  |  | North | 0.13101 | 0 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.02338 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.10763 | 0 | 580 |  |  |  |  | -0.10763 | 0 |  |  | Houston | -0.16396 | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.007923 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 |  |  |  |  | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.007923 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 | Houston |  |  |  | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.007923 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.12308 | 0 | 0 |  |  |  |  | -0.12308 | 0 | Line Rating |  | 1376 |  | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.007267 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.12374 | 0 | 0 |  |  |  |  | -0.12374 | 0 | Impact Counter to Zone: |  | 52.0513 |  | 0 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.000602 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 |  |  | 3.783% |  | 0 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.000602 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 |  |  |  |  | 0 | 0
88253 | HAMILTON | F | South | YES | 0.000602 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.1304 | 0 | 0 |  |  |  |  | -0.1304 | 0 | North |  |  |  | 0 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.13101 | 15 | 15 |  |  |  |  | -0.13101 | -1.9651 | Line Rating |  | 1376 |  | 0 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 | Impact Counter to Zone: |  | 0 |  | 0 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 |  |  | 0% |  | 0 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 |  |  |  |  | 0 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 |  |  |  |  | 0 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 |  |  |  |  | 0 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 |  |  |  |  | 0 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 |  |  |  |  | 0 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.13101 | 0 | 0 |  |  |  |  | -0.13101 | 0 |  |  |  |  | 0 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.13101 | 0 | 0 |  |  | 0 | 0 | -0.13101 | 0 |  |  |  |  | 0 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.00102 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.13203 | 0 | 0 |  |  |  |  | -0.13203 | 0 |  |  |  |  | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.00102 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.13203 | 0 | 0 |  |  |  |  | -0.13203 | 0 |  |  |  |  | 0 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.001256 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.13226 | 423.3 | 423.3 |  |  |  |  | -0.13226 | -55.9867 |  |  |  |  | 0 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.003738 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.13474 | 0 | 0 |  |  |  |  | -0.13474 | 0 |  |  |  |  | 0 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.003738 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.13474 | 0 | 0 |  |  |  |  | -0.13474 | 0 |  |  |  |  | 0 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.008874 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 |  |  |  |  | 0 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.008874 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 |  |  |  |  | 0 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.008874 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.13988 | 0 | 0 |  |  |  |  | -0.13988 | 0 |  |  |  |  | 0 | 0
9005 | DECKR_G6 | 6 | South | YES | -0.01061 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.14162 | 47 | 47 |  |  |  |  | -0.14162 | -6.656 |  |  |  |  | 0 | 0
9003 | DECKR_G4 | 4 | South | YES | -0.01061 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.14162 | 44 | 44 |  |  |  |  | -0.14162 | -6.2311 |  |  |  |  | 0 | 0
9004 | DECKR_G5 | 5 | South | YES | -0.01061 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.14162 | 44 | 44 |  |  |  |  | -0.14162 | -6.2311 |  |  |  |  | 0 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.01061 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.14162 | 42 | 42 |  |  |  |  | -0.14162 | -5.9479 |  |  |  |  | 0 | 0
9001 | DECKR_G2 | 2 | South | YES | -0.01167 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.14268 | 426 | 426 |  |  |  |  | -0.14268 | -60.7801 |  |  |  |  | 0 | 0
9000 | DECKR_G1 | 1 | South | YES | -0.01167 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.14268 | 321 | 321 |  |  |  |  | -0.14268 | -45.7991 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.011802 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.14281 | 0 | 0 |  |  |  |  | -0.14281 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.011802 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.14281 | 0 | 0 |  |  |  |  | -0.14281 | 0 |  |  |  |  | 0 | 0
9020 | SANDHG5A | 5A | South | YES | -0.013106 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.14411 | 155 | 155 |  |  |  |  | -0.14411 | -22.3374 |  |  |  |  | 0 | 0
9021 | SANDHG5C | 5C | South | YES | -0.013106 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.14411 | 148 | 148 |  |  |  |  | -0.14411 | -21.3286 |  |  |  |  | 0 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.013106 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.14411 | 49 | 49 |  |  |  |  | -0.14411 | -7.0615 |  |  |  |  | 0 | 0
9019 | SANDH_G4 | 4 | South | YES | -0.013106 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.14411 | 47 | 47 |  |  |  |  | -0.14411 | -6.7733 |  |  |  |  | 0 | 0
9017 | SANDH_G2 | 2 | South | YES | -0.013106 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.14411 | 46 | 46 |  |  |  |  | -0.14411 | -6.6292 |  |  |  |  | 0 | 0
9018 | SANDH_G3 | 3 | South | YES | -0.013106 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.14411 | 46 | 46 |  |  |  |  | -0.14411 | -6.6292 |  |  |  |  | 0 | 0
8262 | ELPS | 1 | South | YES | -0.014943 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.14595 | 0 | 0 |  |  |  |  | -0.14595 | 0 |  |  |  |  | 0 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.016728 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.14773 | 232.6 | 232.6 |  |  |  |  | -0.14773 | -34.363 |  |  |  |  | 0 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.016728 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.14773 | 152.5 | 152.5 |  |  |  |  | -0.14773 | -22.5295 |  |  |  |  | 0 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.016728 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.14773 | 149.5 | 149.5 |  |  |  |  | -0.14773 | -22.0863 |  |  |  |  | 0 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.018765 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.14977 | 175 | 175 |  |  |  |  | -0.14977 | -26.21 |  |  |  |  | 0 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.018765 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.14977 | 160 | 160 |  |  |  |  | -0.14977 | -23.9634 |  |  |  |  | 0 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.018765 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.14977 | 158 | 158 |  |  |  |  | -0.14977 | -23.6639 |  |  |  |  | 0 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.020362 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.15137 | 329 | 329 |  |  |  |  | -0.15137 | -49.8002 |  |  |  |  | 0 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.020362 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.15137 | 139 | 139 |  |  |  |  | -0.15137 | -21.0402 |  |  |  |  | 0 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.020362 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.15137 | 132 | 132 |  |  |  |  | -0.15137 | -19.9806 |  |  |  |  | 0 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.030613 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.16162 | 0 | 0 |  |  |  |  | -0.16162 | 0 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.035352 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.16636 | 50 | 50 |  |  |  |  | -0.16636 | -8.3179 |  |  |  |  | 0 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.035416 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.16642 | 226.7 | 226.7 |  |  |  |  | -0.16642 | -37.728 |  |  |  |  | 0 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.035416 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.16642 | 225 | 225 |  |  |  |  | -0.16642 | -37.445 |  |  |  |  | 0 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.035416 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.16642 | 224.6 | 224.6 |  |  |  |  | -0.16642 | -37.3785 |  |  |  |  | 0 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.035416 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.16642 | 223.9 | 223.9 |  |  |  |  | -0.16642 | -37.262 |  |  |  |  | 0 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.036911 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.16792 | 0 | 606 |  |  |  |  | -0.16792 | 0 |  |  |  |  | 0 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.036911 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.16792 | 0 | 598 |  |  |  |  | -0.16792 | 0 |  |  |  |  | 0 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.037052 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.16806 | 0 | 436 |  |  |  |  | -0.16806 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.039626 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.039626 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.039626 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.17063 | 0 | 0 |  |  |  |  | -0.17063 | 0 |  |  |  |  | 0 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.040116 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.17112 | 293 | 293 |  |  |  |  | -0.17112 | -50.1389 |  |  |  |  | 0 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.040116 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.17112 | 154 | 154 |  |  |  |  | -0.17112 | -26.3529 |  |  |  |  | 0 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.040116 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.17112 | 148 | 148 |  |  |  |  | -0.17112 | -25.3261 |  |  |  |  | 0 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.040116 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.17112 | 148 | 148 |  |  |  |  | -0.17112 | -25.3261 |  |  |  |  | 0 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.040794 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.1718 | 0 | 0 |  |  |  |  | -0.1718 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.042542 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.17355 | 0 | 0 |  |  |  |  | -0.17355 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.042542 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.17355 | 0 | 0 |  |  |  |  | -0.17355 | 0 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.043549 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.17456 | 8.4 | 8.4 |  |  |  |  | -0.17456 | -1.4663 |  |  |  |  | 0 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.044531 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.17554 | 203 | 203 |  |  |  |  | -0.17554 | -35.6341 |  |  |  |  | 0 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.044531 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.17554 | 182 | 182 |  |  |  |  | -0.17554 | -31.9478 |  |  |  |  | 0 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.044531 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.17554 | 149 | 149 |  |  |  |  | -0.17554 | -26.1551 |  |  |  |  | 0 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.044531 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.17554 | 147 | 147 |  |  |  |  | -0.17554 | -25.804 |  |  |  |  | 0 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.044531 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.17554 | 146 | 146 |  |  |  |  | -0.17554 | -25.6285 |  |  |  |  | 0 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.044531 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.17554 | 138 | 138 |  |  |  |  | -0.17554 | -24.2242 |  |  |  |  | 0 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.045528 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.17653 | 407 | 407 |  |  |  |  | -0.17653 | -71.8495 |  |  |  |  | 0 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.045555 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.17656 | 418 | 418 |  |  |  |  | -0.17656 | -73.8027 |  |  |  |  | 0 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | -0.045555 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.17656 | 400 | 400 |  |  |  |  | -0.17656 | -70.6246 |  |  |  |  | 0 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | -0.04556 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.17657 | 0 | 430 |  |  |  |  | -0.17657 | 0 |  |  |  |  | 0 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.04556 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.17657 | 0 | 430 |  |  |  |  | -0.17657 | 0 |  |  |  |  | 0 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | -0.045592 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.1766 | 89 | 89 |  |  |  |  | -0.1766 | -15.7173 |  |  |  |  | 0 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.045592 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.1766 | 58 | 58 |  |  |  |  | -0.1766 | -10.2427 |  |  |  |  | 0 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | -0.045592 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.1766 | 45 | 45 |  |  |  |  | -0.1766 | -7.9469 |  |  |  |  | 0 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | -0.045592 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.1766 | 44 | 44 |  |  |  |  | -0.1766 | -7.7703 |  |  |  |  | 0 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | -0.045592 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.1766 | 44 | 44 |  |  |  |  | -0.1766 | -7.7703 |  |  |  |  | 0 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | -0.045592 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.1766 | 43 | 43 |  |  |  |  | -0.1766 | -7.5937 |  |  |  |  | 0 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.045597 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.1766 | 151 | 151 |  |  |  |  | -0.1766 | -26.6671 |  |  |  |  | 0 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.045597 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.1766 | 95 | 95 |  |  |  |  | -0.1766 | -16.7773 |  |  |  |  | 0 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.045597 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.1766 | 61 | 61 |  |  |  |  | -0.1766 | -10.7728 |  |  |  |  | 0 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.045713 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.17672 | 216 | 216 |  |  |  |  | -0.17672 | -38.1714 |  |  |  |  | 0 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.045713 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.17672 | 215 | 215 |  |  |  |  | -0.17672 | -37.9947 |  |  |  |  | 0 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.045752 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.17676 | 24.3 | 24.3 |  |  |  |  | -0.17676 | -4.2952 |  |  |  |  | 0 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.045752 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.17676 | 24 | 24 |  |  |  |  | -0.17676 | -4.2422 |  |  |  |  | 0 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.045752 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.17676 | 23.9 | 23.9 |  |  |  |  | -0.17676 | -4.2245 |  |  |  |  | 0 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | -0.047164 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.17817 | 174 | 174 |  |  |  |  | -0.17817 | -31.0017 |  |  |  |  | 0 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.047164 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.17817 | 155 | 155 |  |  |  |  | -0.17817 | -27.6164 |  |  |  |  | 0 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.047164 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.17817 | 155 | 155 |  |  |  |  | -0.17817 | -27.6164 |  |  |  |  | 0 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.048248 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.17925 | 0 | 562 |  |  |  |  | -0.17925 | 0 |  |  |  |  | 0 | 0
8189 | CUECPL2A | 1 | South | YES | -0.050999 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.18201 | 0 | 0 |  |  |  |  | -0.18201 | 0 |  |  |  |  | 0 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.053842 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.18485 | 0 | 396.3 |  |  |  |  | -0.18485 | 0 |  |  |  |  | 0 | 0
80265 | LARECU40A | 4 | South | YES | -0.054415 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.18542 | 100 | 100 |  |  |  |  | -0.18542 | -18.5421 |  |  |  |  | 0 | 0
80266 | LARECU50A | 5 | South | YES | -0.054415 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.18542 | 100 | 100 |  |  |  |  | -0.18542 | -18.5421 |  |  |  |  | 0 | 0
80012 | LAR | F | South | YES | -0.054418 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.18542 | 0 | 0 |  |  |  |  | -0.18542 | 0 |  |  |  |  | 0 | 0
88299 | ZAPATA | F | South | YES | -0.060485 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.19149 | 0 | 0 |  |  |  |  | -0.19149 | 0 |  |  |  |  | 0 | 0
88198 | BEEVILLE | F | South | YES | -0.063278 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.19428 | 0 | 0 |  |  |  |  | -0.19428 | 0 |  |  |  |  | 0 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.064599 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0 |  |  |  |  | 0 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.064599 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0 |  |  |  |  | 0 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.064599 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.19561 | 0 | 0 |  |  |  |  | -0.19561 | 0 |  |  |  |  | 0 | 0
88508 | FALFURRI | F | South | YES | -0.065356 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.19636 | 0 | 0 |  |  |  |  | -0.19636 | 0 |  |  |  |  | 0 | 0
8161 | COLETO0A | 1 | South | YES | -0.066648 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.19765 | 0 | 633 |  |  |  |  | -0.19765 | 0 |  |  |  |  | 0 | 0
8935 | FGNTS201 | 3 | South | YES | -0.0689 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.19991 | 173 | 173 |  |  |  |  | -0.19991 | -34.5838 |  |  |  |  | 0 | 0
8934 | FGNTS101 | 2 | South | YES | -0.0689 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.19991 | 147.9 | 147.9 |  |  |  |  | -0.19991 | -29.5662 |  |  |  |  | 0 | 0
8933 | FGNTS001 | 1 | South | YES | -0.0689 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.19991 | 146.5 | 146.5 |  |  |  |  | -0.19991 | -29.2863 |  |  |  |  | 0 | 0
8983 | HECN3 | 3 | South | YES | -0.069623 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.20063 | 171.9 | 171.9 |  |  |  |  | -0.20063 | -34.4882 |  |  |  |  | 0 | 0
8981 | HECN1 | 1 | South | YES | -0.069623 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.20063 | 144.8 | 144.8 |  |  |  |  | -0.20063 | -29.0511 |  |  |  |  | 0 | 0
8982 | HECN2 | 2 | South | YES | -0.069623 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.20063 | 144.1 | 144.1 |  |  |  |  | -0.20063 | -28.9107 |  |  |  |  | 0 | 0
8938 | MVGN#3 | 3 | South | YES | -0.069624 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.20063 | 250.9 | 250.9 |  |  |  |  | -0.20063 | -50.3382 |  |  |  |  | 0 | 0
8937 | MVGN#2 | 2 | South | YES | -0.069624 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.20063 | 216.7 | 216.7 |  |  |  |  | -0.20063 | -43.4766 |  |  |  |  | 0 | 0
8936 | MVGN#1 | 1 | South | YES | -0.069624 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.20063 | 216.6 | 216.6 |  |  |  |  | -0.20063 | -43.4565 |  |  |  |  | 0 | 0
5935 | SI_RAY10 | 10 | South | YES | -0.069941 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.20095 | 47 | 47 |  |  |  |  | -0.20095 | -9.4445 |  |  |  |  | 0 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.069941 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.20095 | 38 | 38 |  |  |  |  | -0.20095 | -7.636 |  |  |  |  | 0 | 0
5933 | SI_RAY6 | 6 | South | YES | -0.069941 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.20095 | 19.3 | 19.3 |  |  |  |  | -0.20095 | -3.8783 |  |  |  |  | 0 | 0
80003 | MILHWYS | F | South | YES | -0.069941 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.20095 | 0 | 0 |  |  |  |  | -0.20095 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 3 | South | YES | -0.070135 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 38 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 4 | South | YES | -0.070135 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 19 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 2 | South | YES | -0.070135 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 41 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 1 | South | YES | -0.070135 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 94 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 4 | South | YES | -0.070135 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 22 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 1 | South | YES | -0.070135 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 94 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 3 | South | YES | -0.070135 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 43 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 2 | South | YES | -0.070135 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 36 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.070135 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 50 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.070135 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 148 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.070135 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 50 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.070135 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.20114 | 0 | 55 |  |  |  |  | -0.20114 | 0 |  |  |  |  | 0 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.070221 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.20123 | 0 | 0 |  |  |  |  | -0.20123 | 0 |  |  |  |  | 0 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.070784 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.20179 | 0 | 0 |  |  |  |  | -0.20179 | 0 |  |  |  |  | 0 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.070843 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.20185 | 0 | 0 |  |  |  |  | -0.20185 | 0 |  |  |  |  | 0 | 0
8506 | VAL #1 | 1 | South | YES | -0.070946 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.20195 | 0 | 0 |  |  |  |  | -0.20195 | 0 |  |  |  |  | 0 | 0
8507 | VAL #2 | 2 | South | YES | -0.070946 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.20195 | 0 | 0 |  |  |  |  | -0.20195 | 0 |  |  |  |  | 0 | 0
80263 | B_DAVIS31A | 3 | South | YES | -0.07109 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.2021 | 180 | 180 |  |  |  |  | -0.2021 | -36.3774 |  |  |  |  | 0 | 0
80264 | B_DAVIS41A | 4 | South | YES | -0.07109 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.2021 | 180 | 180 |  |  |  |  | -0.2021 | -36.3774 |  |  |  |  | 0 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.07109 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.2021 | 0 | 0 |  |  |  |  | -0.2021 | 0 |  |  |  |  | 0 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.07109 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.2021 | 0 | 0 |  |  |  |  | -0.2021 | 0 |  |  |  |  | 0 | 0
8456 | COSW#1 | 1 | South | YES | -0.07125 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.20226 | 0 | 0 |  |  |  |  | -0.20226 | 0 |  |  |  |  | 0 | 0
8457 | COSW#2 | 2 | South | YES | -0.07125 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.20226 | 0 | 0 |  |  |  |  | -0.20226 | 0 |  |  |  |  | 0 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.071328 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0 |  |  |  |  | 0 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.071328 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0 |  |  |  |  | 0 | 0
8562 | CNOPST1 | 3 | South | YES | -0.071328 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.20233 | 0 | 0 |  |  |  |  | -0.20233 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | 7 | South | YES | -0.071344 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.20235 | 367 | 367 |  |  |  |  | -0.20235 | -74.2626 |  |  |  |  | 0 | 0
8442 | NBEC7 | MB | South | YES | -0.071344 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.20235 | 0 | 0 |  |  |  |  | -0.20235 | 0 |  |  |  |  | 0 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.072739 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 |  |  |  |  | 0 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.072739 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 |  |  |  |  | 0 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.072739 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 |  |  |  |  | 0 | 0
8930 | ICPGN10A | 1 | South | YES | -0.072739 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 |  |  |  |  | 0 | 0
8931 | ICPGN20A | 2 | South | YES | -0.072739 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 |  |  |  |  | 0 | 0
8932 | ICPGN30A | 3 | South | YES | -0.072739 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 |  |  |  |  | 0 | 0
80223 | REYSHR G | 1 | South | YES | -0.072739 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.20375 | 0 | 0 |  |  |  |  | -0.20375 | 0 |  |  |  |  | 0 | 0
8174 | VICEC61A | 6 | South | YES | -0.073157 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.20416 | 188 | 188 |  |  |  |  | -0.20416 | -38.3827 |  |  |  |  | 0 | 0
8173 | VICEC51A | 5 | South | YES | -0.073157 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.20416 | 144 | 144 |  |  |  |  | -0.20416 | -29.3995 |  |  |  |  | 0 | 0
5512 | RAYBURNCC8 | 1 | South | YES | -0.07442 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.20543 | 49.3 | 49.3 |  |  |  |  | -0.20543 | -10.1275 |  |  |  |  | 0 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.07442 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.20543 | 47.7 | 47.7 |  |  |  |  | -0.20543 | -9.7988 |  |  |  |  | 0 | 0
5511 | RAYBURNCC7 | 1 | South | YES | -0.07442 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.20543 | 47.5 | 47.5 |  |  |  |  | -0.20543 | -9.7578 |  |  |  |  | 0 | 0
5509 | RAYBURNCC10 | 1 | South | YES | -0.07442 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.20543 | 37.3 | 37.3 |  |  |  |  | -0.20543 | -7.6624 |  |  |  |  | 0 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.074513 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.20552 | 0 | 0 |  |  |  |  | -0.20552 | 0 |  |  |  |  | 0 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.075068 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.20607 | 22 | 22 |  |  |  |  | -0.20607 | -4.5336 |  |  |  |  | 0 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | -0.075068 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.20607 | 11 | 11 |  |  |  |  | -0.20607 | -2.2668 |  |  |  |  | 0 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | -0.075068 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.20607 | 11 | 11 |  |  |  |  | -0.20607 | -2.2668 |  |  |  |  | 0 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.07682 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.20783 | 0 | 0 |  |  |  |  | -0.20783 | 0 |  |  |  |  | 0 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.07682 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.20783 | 0 | 0 |  |  |  |  | -0.20783 | 0 |  |  |  |  | 0 | 0
80227 | AIRCO G | 1 | South | YES | -0.077635 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.20864 | 0 | 0 |  |  |  |  | -0.20864 | 0 |  |  |  |  | 0 | 0
8147 | UCAR #2 | 10 | South | YES | -0.078169 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 |  |  |  |  | 0 | 0
8148 | UCAR #1 | 2 | South | YES | -0.078169 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 9 | South | YES | -0.078169 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 8 | South | YES | -0.078169 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 |  |  |  |  | 0 | 0
80138 | CSDR7 | 7 | South | YES | -0.078169 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 6 | South | YES | -0.078169 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 5 | South | YES | -0.078169 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 |  |  |  |  | 0 | 0
80140 | CSDR11 | 11 | South | YES | -0.078169 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.20918 | 0 | 0 |  |  |  |  | -0.20918 | 0 |  |  |  |  | 0 | 0
80226 | ALCOA G | 1 | South | YES | -0.081585 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.21259 | 0 | 0 |  |  |  |  | -0.21259 | 0 |  |  |  |  | 0 | 0
8134 | FOR #1 | 1 | South | YES | -0.082615 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
8138 | FOR #2 | 2 | South | YES | -0.082615 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
8153 | FOR #3 | 3 | South | YES | -0.082615 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
8154 | FOR #4 | 4 | South | YES | -0.082615 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
8155 | FOR #5 | 5 | South | YES | -0.082615 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
8156 | FOR #6 | 6 | South | YES | -0.082615 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
8157 | FOR #7 | 7 | South | YES | -0.082615 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
80051 | FOR #8 | 8 | South | YES | -0.082615 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
80052 | FOR #9 | 9 | South | YES | -0.082615 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
80053 | FOR #10 | 10 | South | YES | -0.082615 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.21362 | 0 | 0 |  |  |  |  | -0.21362 | 0 |  |  |  |  | 0 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.11917 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.25018 | 0 | 0 |  |  | 0 | 0 | -0.25018 | 0 |  |  |  |  | 0 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.11917 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.25018 | 0 | 0 |  |  | 0 | 0 | -0.25018 | 0 |  |  |  |  | 0 | 0
48733 | CBE_ST12 | 1 | Houston | YES | -0.11998 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.25099 | 105 | 105 |  |  | -12.5983 | 105 | -0.25099 | -26.354 |  |  |  |  | 0 | 0
48736 | CBE_ST34 | 1 | Houston | YES | -0.11998 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.25099 | 105 | 105 |  |  | -12.5983 | 105 | -0.25099 | -26.354 |  |  |  |  | 0 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753 |  |  |  |  | 0 | 0
48732 | CBE_GT2 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753 |  |  |  |  | 0 | 0
48734 | CBE_GT3 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753 |  |  |  |  | 0 | 0
48735 | CBE_GT4 | 1 | Houston | YES | -0.11998 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.25099 | 76 | 76 |  |  | -9.1188 | 76 | -0.25099 | -19.0753 |  |  |  |  | 0 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.12405 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.25505 | 0 | 0 |  |  | 0 | 0 | -0.25505 | 0 |  |  |  |  | 0 | 0
60202 | FRNDDRCS | F | West | YES | 0.0982 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.26216 | 0 | 0 |  |  |  |  | 0.26216 | 0 |  |  |  |  | 0 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | 0.10317 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.26713 | 75 | 75 | 7.7381 | 75 |  |  | 0.26713 | 20.0349 |  |  |  |  | 0 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | 0.10317 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.26713 | 222 | 222 | 22.9046 | 222 |  |  | 0.26713 | 59.3032 |  |  |  |  | 0 | 0
3403 | THOUSE_1G | 1 | North | YES | 0.1042 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.26815 | 563 | 563 | 58.6629 | 563 |  |  | 0.26815 | 150.971 |  |  |  |  | 0 | 0
3404 | THOUSE_2G | 2 | North | YES | 0.1042 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.26815 | 807 | 807 | 84.087 | 807 |  |  | 0.26815 | 216.4007 |  |  |  |  | 0 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.13719 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.13719 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.13719 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.13719 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.13719 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.13719 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.13719 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.13719 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.13719 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.13719 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.13719 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.13719 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.13719 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.13719 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.13719 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.13719 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.13719 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.13719 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.13719 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.13719 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.26819 | 0 | 0 |  |  | 0 | 0 | -0.26819 | 0 |  |  |  |  | 0 | 0
239 | BOSQUESW502 | 1 | North | YES | 0.10599 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.26995 | 149 | 149 | 15.7927 | 149 |  |  | 0.26995 | 40.2223 |  |  |  |  | 0 | 0
247 | BOSQUESW501 | 2 | North | YES | 0.10599 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.26995 | 156 | 156 | 16.5346 | 156 |  |  | 0.26995 | 42.112 |  |  |  |  | 0 | 0
238 | BOSQUESW505 | 1 | North | YES | 0.10599 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.26995 | 255 | 255 | 27.0277 | 255 |  |  | 0.26995 | 68.8369 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.1405 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.2715 | 0 | 0 |  |  | 0 | 0 | -0.2715 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.1405 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.2715 | 0 | 0 |  |  | 0 | 0 | -0.2715 | 0 |  |  |  |  | 0 | 0
253 | BOSQUESW804 | 2 | North | YES | 0.10903 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.27299 | 80 | 80 | 8.7226 | 80 |  |  | 0.27299 | 21.8392 |  |  |  |  | 0 | 0
251 | BOSQUESW803 | 2 | North | YES | 0.10903 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.27299 | 150 | 150 | 16.3548 | 150 |  |  | 0.27299 | 40.9484 |  |  |  |  | 0 | 0
60018 | DSKY1 | 1 | West | YES | 0.10977 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.27373 | 0 | 84 |  |  |  |  | 0.27373 | 22.9931 |  |  |  |  | 0 | 0
60000 | DSKY2 | 1 | West | YES | 0.10996 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.27392 | 0 | 76.5 |  |  |  |  | 0.27392 | 20.9551 |  |  |  |  | 0 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.14314 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0 |  |  |  |  | 0 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.14314 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0 |  |  |  |  | 0 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.14314 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0 |  |  |  |  | 0 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.14314 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.27414 | 0 | 0 |  |  | 0 | 0 | -0.27414 | 0 |  |  |  |  | 0 | 0
60017 | ORNNWP1 | 1 | West | YES | 0.11052 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.27447 | 0 | 80 |  |  |  |  | 0.27447 | 21.958 |  |  |  |  | 0 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | 0.11273 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.27669 | 0 | 150 |  |  |  |  | 0.27669 | 41.5034 |  |  |  |  | 0 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.1128 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.27675 | 0 | 80 |  |  |  |  | 0.27675 | 22.1403 |  |  |  |  | 0 | 0
60016 | WOODWRD11A | 1 | West | YES | 0.11281 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.27677 | 0 | 80 |  |  |  |  | 0.27677 | 22.1414 |  |  |  |  | 0 | 0
60005 | KING_SE1A | 1 | West | YES | 0.11289 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.27685 | 0 | 40 |  |  |  |  | 0.27685 | 11.0738 |  |  |  |  | 0 | 0
6016 | SWMESA | 1 | West | YES | 0.11289 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.27685 | 0 | 75 |  |  |  |  | 0.27685 | 20.7634 |  |  |  |  | 0 | 0
60003 | KING_NE1A | 1 | West | YES | 0.11289 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27685 | 0 | 80 |  |  |  |  | 0.27685 | 22.1476 |  |  |  |  | 0 | 0
60201 | RIO DRCS | F | West | YES | 0.11301 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.27696 | 0 | 0 |  |  |  |  | 0.27696 | 0 |  |  |  |  | 0 | 0
60007 | KING_SW1A | 1 | West | YES | 0.11331 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27726 | 0 | 80 |  |  |  |  | 0.27726 | 22.181 |  |  |  |  | 0 | 0
60019 | KING_NW1A | 1 | West | YES | 0.11331 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27726 | 0 | 80 |  |  |  |  | 0.27726 | 22.181 |  |  |  |  | 0 | 0
244 | WHITNYDM01 | 1 | North | YES | 0.11339 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.27735 | 0 | 0 | 0 | 0 |  |  | 0.27735 | 0 |  |  |  |  | 0 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.11339 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.27735 | 0 | 0 | 0 | 0 |  |  | 0.27735 | 0 |  |  |  |  | 0 | 0
1349 | WESTXWIN_1G | 1 | West | YES | 0.11931 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.28326 | 0 | 6.6 |  |  |  |  | 0.28326 | 1.8695 |  |  |  |  | 0 | 0
1350 | NWPWRG1_1G | 1 | West | YES | 0.11931 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.28326 | 0 | 34.3 |  |  |  |  | 0.28326 | 9.716 |  |  |  |  | 0 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.15253 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.28354 | 0 | 0 |  |  | 0 | 0 | -0.28354 | 0 |  |  |  |  | 0 | 0
60057 | CALLAHAN1A | 1 | West | YES | 0.11964 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.2836 | 0 | 114 |  |  |  |  | 0.2836 | 32.33 |  |  |  |  | 0 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.15264 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 651 |  |  | 0 | 0 | -0.28365 | 0 |  |  |  |  | 0 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.15264 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 564 |  |  | 0 | 0 | -0.28365 | 0 |  |  |  |  | 0 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.15264 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.28365 | 0 | 603 |  |  | 0 | 0 | -0.28365 | 0 |  |  |  |  | 0 | 0
1002 | PBCTAGE_1G | A | West | YES | 0.11974 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.2837 | 66 | 66 |  |  |  |  | 0.2837 | 18.724 |  |  |  |  | 0 | 0
1003 | PBCTBGE_2G | B | West | YES | 0.11974 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.2837 | 66 | 66 |  |  |  |  | 0.2837 | 18.724 |  |  |  |  | 0 | 0
1004 | PBCTCGE_3G | C | West | YES | 0.11974 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.2837 | 67 | 67 |  |  |  |  | 0.2837 | 19.0077 |  |  |  |  | 0 | 0
1006 | PBCTEGE_5G | E | West | YES | 0.11974 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.2837 | 67 | 67 |  |  |  |  | 0.2837 | 19.0077 |  |  |  |  | 0 | 0
1005 | PBCTDGE_4G | D | West | YES | 0.11974 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.2837 | 68 | 68 |  |  |  |  | 0.2837 | 19.2914 |  |  |  |  | 0 | 0
1007 | PB5GEN_6G | 5 | West | YES | 0.11974 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.2837 | 114 | 114 |  |  |  |  | 0.2837 | 32.3415 |  |  |  |  | 0 | 0
1008 | PB6GEN_7G | 6 | West | YES | 0.11974 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.2837 | 515 | 515 |  |  |  |  | 0.2837 | 146.1042 |  |  |  |  | 0 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.15272 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.28372 | 252.4 | 252.4 |  |  | -38.546 | 252.4 | -0.28372 | -71.612 |  |  |  |  | 0 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.15272 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.28372 | 167.7 | 167.7 |  |  | -25.6108 | 167.7 | -0.28372 | -47.5806 |  |  |  |  | 0 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.15272 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.28372 | 166.4 | 166.4 |  |  | -25.4123 | 166.4 | -0.28372 | -47.2117 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.11981 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.28376 | 0 | 30 |  |  |  |  | 0.28376 | 8.5129 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.11981 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.28376 | 0 | 35 |  |  |  |  | 0.28376 | 9.9318 |  |  |  |  | 0 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.11993 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.28389 | 0 | 112.5 |  |  |  |  | 0.28389 | 31.9377 |  |  |  |  | 0 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.11993 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 149.5 |  |  |  |  | 0.28389 | 42.4416 |  |  |  |  | 0 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.11993 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 186 |  |  |  |  | 0.28389 | 52.8036 |  |  |  |  | 0 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.11993 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.28389 | 0 | 214.5 |  |  |  |  | 0.28389 | 60.8945 |  |  |  |  | 0 | 0
11147 | NOTREES_1G | 1 | West | YES | 0.11994 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.28389 | 0 | 149 |  |  |  |  | 0.28389 | 42.3001 |  |  |  |  | 0 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | 0.12027 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.28423 | 0 | 150 |  |  |  |  | 0.28423 | 42.634 |  |  |  |  | 0 | 0
1320 | BSP 1 | 1 | West | YES | 0.12055 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.28451 | 0 | 0 |  |  |  |  | 0.28451 | 0 |  |  |  |  | 0 | 0
1326 | STANTONW_8 | 1 | West | YES | 0.12067 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.28463 | 0 | 100.5 |  |  |  |  | 0.28463 | 28.6051 |  |  |  |  | 0 | 0
11022 | TIEHVCG_2G | 1 | West | YES | 0.12071 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.28467 | 132.4 | 132.4 |  |  |  |  | 0.28467 | 37.6904 |  |  |  |  | 0 | 0
11023 | TIEHVCG_3G | 1 | West | YES | 0.12071 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.28467 | 137.4 | 137.4 |  |  |  |  | 0.28467 | 39.1137 |  |  |  |  | 0 | 0
11021 | TIEHVCG_1G | 1 | West | YES | 0.12071 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.28467 | 142.1 | 142.1 |  |  |  |  | 0.28467 | 40.4517 |  |  |  |  | 0 | 0
11024 | TIEHVCG_4G | 1 | West | YES | 0.12071 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.28467 | 147 | 147 |  |  |  |  | 0.28467 | 41.8466 |  |  |  |  | 0 | 0
11020 | TIEHVSG_1G | 1 | West | YES | 0.12071 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.28467 | 208.2 | 208.2 |  |  |  |  | 0.28467 | 59.2684 |  |  |  |  | 0 | 0
11025 | TIEHVSG_2G | 1 | West | YES | 0.12071 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.28467 | 213.2 | 213.2 |  |  |  |  | 0.28467 | 60.6918 |  |  |  |  | 0 | 0
11001 | NAV1CT | 1 | West | YES | 0.12072 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.28468 | 70.4 | 70.4 |  |  |  |  | 0.28468 | 20.0416 |  |  |  |  | 0 | 0
11009 | NAV2CT | 1 | West | YES | 0.12072 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.28468 | 71.4 | 71.4 |  |  |  |  | 0.28468 | 20.3263 |  |  |  |  | 0 | 0
11012 | NAV4CT | 1 | West | YES | 0.12072 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28468 | 80 | 80 |  |  |  |  | 0.28468 | 22.7745 |  |  |  |  | 0 | 0
11013 | NAV5CT | 1 | West | YES | 0.12072 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28468 | 80 | 80 |  |  |  |  | 0.28468 | 22.7745 |  |  |  |  | 0 | 0
11011 | NAV3ST | 1 | West | YES | 0.12072 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.28468 | 92.8 | 92.8 |  |  |  |  | 0.28468 | 26.4184 |  |  |  |  | 0 | 0
11014 | NAV6ST | 1 | West | YES | 0.12072 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.28468 | 115 | 115 |  |  |  |  | 0.28468 | 32.7384 |  |  |  |  | 0 | 0
1328 | OCOTILLO_1G | 1 | West | YES | 0.12078 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.28474 | 0 | 58 |  |  |  |  | 0.28474 | 16.515 |  |  |  |  | 0 | 0
1333 | MCDDONAL_8 | 1 | West | YES | 0.12095 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.28491 | 0 | 214.2 |  |  |  |  | 0.28491 | 61.028 |  |  |  |  | 0 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.15395 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.28495 | 0 | 0 |  |  | 0 | 0 | -0.28495 | 0 |  |  |  |  | 0 | 0
1327 | WILDHRSE_1G | 1 | West | YES | 0.12116 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.28512 | 0 | 120 |  |  |  |  | 0.28512 | 34.2145 |  |  |  |  | 0 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | 0.1212 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.28515 | 0 | 120 |  |  |  |  | 0.28515 | 34.2185 |  |  |  |  | 0 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.15422 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.28523 | 546 | 546 |  |  | -84.2058 | 546 | -0.28523 | -155.7353 |  |  |  |  | 0 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.15422 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.28523 | 248 | 248 |  |  | -38.2473 | 248 | -0.28523 | -70.7369 |  |  |  |  | 0 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.15422 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.28523 | 166 | 166 |  |  | -25.601 | 166 | -0.28523 | -47.3481 |  |  |  |  | 0 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.15422 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.28523 | 166 | 166 |  |  | -25.601 | 166 | -0.28523 | -47.3481 |  |  |  |  | 0 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.15422 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.28523 | 13 | 13 |  |  | -2.0049 | 13 | -0.28523 | -3.708 |  |  |  |  | 0 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.15422 | 591.2 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.28523 | 0 | 654 |  |  | 0 | 0 | -0.28523 | 0 |  |  |  |  | 0 | 0
11320 | COYOTE_1G | 1 | West | YES | 0.12146 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.28541 | 0 | 225 |  |  |  |  | 0.28541 | 64.2183 |  |  |  |  | 0 | 0
11309 | BULLCREK_2G | 1 | West | YES | 0.12152 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.28548 | 0 | 180 |  |  |  |  | 0.28548 | 51.386 |  |  |  |  | 0 | 0
11310 | BULLCREK_1G | 1 | West | YES | 0.12152 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.28548 | 0 | 180 |  |  |  |  | 0.28548 | 51.386 |  |  |  |  | 0 | 0
1045 | CALENG1G_1G | 1 | West | YES | 0.12154 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0 |  |  |  |  | 0 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.12154 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0 |  |  |  |  | 0 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.12154 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.28549 | 0 | 0 |  |  |  |  | 0.28549 | 0 |  |  |  |  | 0 | 0
11065 | ELBOWCK_1G | 1 | West | YES | 0.12173 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.28568 | 0 | 121.9 |  |  |  |  | 0.28568 | 34.8248 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 1 | West | YES | 0.12173 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.28568 | 0 | 150 |  |  |  |  | 0.28568 | 42.8525 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 2 | West | YES | 0.12173 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.28568 | 0 | 220 |  |  |  |  | 0.28568 | 62.8504 |  |  |  |  | 0 | 0
60072 | HHOLLOW41A | 1 | West | YES | 0.12179 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 115 |  |  |  |  | 0.28574 | 32.8606 |  |  |  |  | 0 | 0
60058 | BUFF_GAP1A | 1 | West | YES | 0.12179 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.28574 | 0 | 120 |  |  |  |  | 0.28574 | 34.2893 |  |  |  |  | 0 | 0
60063 | BUFF_GAP1B | 1 | West | YES | 0.12179 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.28574 | 0 | 170.2 |  |  |  |  | 0.28574 | 48.6337 |  |  |  |  | 0 | 0
60068 | HHOLLOW21A | 1 | West | YES | 0.12179 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 184 |  |  |  |  | 0.28574 | 52.577 |  |  |  |  | 0 | 0
60066 | H_HOLLOW1A | 1 | West | YES | 0.12179 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.28574 | 0 | 222 |  |  |  |  | 0.28574 | 63.4353 |  |  |  |  | 0 | 0
60070 | HHOLLOW31A | 1 | West | YES | 0.12179 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.28574 | 0 | 224 |  |  |  |  | 0.28574 | 64.0068 |  |  |  |  | 0 | 0
60060 | CIRELLO | 1 | West | YES | 0.12179 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.28574 | 0 | 233 |  |  |  |  | 0.28574 | 66.5785 |  |  |  |  | 0 | 0
1044 | MRGNFG_6G | F | West | YES | 0.12184 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.2858 | 66 | 66 |  |  |  |  | 0.2858 | 18.8628 |  |  |  |  | 0 | 0
1042 | MRGNDG_4G | D | West | YES | 0.12184 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.2858 | 68 | 68 |  |  |  |  | 0.2858 | 19.4344 |  |  |  |  | 0 | 0
1039 | MRGNAG_1G | A | West | YES | 0.12184 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.2858 | 69 | 69 |  |  |  |  | 0.2858 | 19.7202 |  |  |  |  | 0 | 0
1041 | MRGNCG_3G | C | West | YES | 0.12184 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.2858 | 70 | 70 |  |  |  |  | 0.2858 | 20.006 |  |  |  |  | 0 | 0
1043 | MRGNEG_5G | E | West | YES | 0.12184 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.2858 | 70 | 70 |  |  |  |  | 0.2858 | 20.006 |  |  |  |  | 0 | 0
1040 | MRGNBG_2G | B | West | YES | 0.12184 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.2858 | 71 | 71 |  |  |  |  | 0.2858 | 20.2918 |  |  |  |  | 0 | 0
1037 | MORGAN5G_5G | 5 | West | YES | 0.12184 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.2858 | 137 | 137 |  |  |  |  | 0.2858 | 39.1545 |  |  |  |  | 0 | 0
6637 | SNYDERW1A | 1 | West | YES | 0.12188 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.28583 | 0 | 63 |  |  |  |  | 0.28583 | 18.0076 |  |  |  |  | 0 | 0
1073 | SCURRYCW_2G | 2 | West | YES | 0.12194 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.2859 | 0 | 120 |  |  |  |  | 0.2859 | 34.3079 |  |  |  |  | 0 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.12194 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.2859 | 0 | 141 |  |  |  |  | 0.2859 | 40.3118 |  |  |  |  | 0 | 0
1069 | KINDERMG_1G | 1 | West | YES | 0.12195 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0 |  |  |  |  | 0 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.12195 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0 |  |  |  |  | 0 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.12195 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28591 | 0 | 0 |  |  |  |  | 0.28591 | 0 |  |  |  |  | 0 | 0
1062 | CIELOGEN_2G | 1 | West | YES | 0.12195 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.28591 | 0 | 61 |  |  |  |  | 0.28591 | 17.4405 |  |  |  |  | 0 | 0
1061 | CIELOGEN_1G | 1 | West | YES | 0.12195 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.28591 | 0 | 99 |  |  |  |  | 0.28591 | 28.305 |  |  |  |  | 0 | 0
36998 | RDCNYNG1 | 1 | West | YES | 0.12212 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.28608 | 0 | 84 |  |  |  |  | 0.28608 | 24.0306 |  |  |  |  | 0 | 0
1354 | AEPWIND_8 | 1 | West | YES | 0.12222 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.28618 | 0 | 101 |  |  |  |  | 0.28618 | 28.904 |  |  |  |  | 0 | 0
1343 | TRENTIPP_8 | 1 | West | YES | 0.12222 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.28618 | 0 | 150 |  |  |  |  | 0.28618 | 42.9268 |  |  |  |  | 0 | 0
6407 | TURKTRAK1A | 1 | West | YES | 0.12241 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.28637 | 0 | 169.5 |  |  |  |  | 0.28637 | 48.5393 |  |  |  |  | 0 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | 0.12284 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 37.5 |  |  |  |  | 0.2868 | 10.7549 |  |  |  |  | 0 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | 0.12284 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 80.5 |  |  |  |  | 0.2868 | 23.0871 |  |  |  |  | 0 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | 0.12284 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 105 |  |  |  |  | 0.2868 | 30.1136 |  |  |  |  | 0 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | 0.12284 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 107.5 |  |  |  |  | 0.2868 | 30.8306 |  |  |  |  | 0 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | 0.12284 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.2868 | 0 | 119 |  |  |  |  | 0.2868 | 34.1288 |  |  |  |  | 0 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | 0.12284 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.2868 | 0 | 135 |  |  |  |  | 0.2868 | 38.7175 |  |  |  |  | 0 | 0
6144 | MCADOO1A | 1 | West | YES | 0.12286 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.28682 | 0 | 150 |  |  |  |  | 0.28682 | 43.0231 |  |  |  |  | 0 | 0
11057 | CHAMPION_1G | 1 | West | YES | 0.12289 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.28685 | 0 | 126.5 |  |  |  |  | 0.28685 | 36.286 |  |  |  |  | 0 | 0
11059 | INADALE_1G | 1 | West | YES | 0.12289 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.28685 | 0 | 197 |  |  |  |  | 0.28685 | 56.5086 |  |  |  |  | 0 | 0
11056 | ROSCOE_1G | 1 | West | YES | 0.12289 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.28685 | 0 | 209 |  |  |  |  | 0.28685 | 59.9507 |  |  |  |  | 0 | 0
11058 | PYRON_1G | 1 | West | YES | 0.12289 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.28685 | 0 | 249 |  |  |  |  | 0.28685 | 71.4245 |  |  |  |  | 0 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.12319 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.28714 | 0 | 60 | 7.3912 | 60 |  |  | 0.28714 | 17.2287 |  |  |  |  | 0 | 0
1416 | SWETWATR_1G | 1 | West | YES | 0.12334 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.28729 | 30 | 30 |  |  |  |  | 0.28729 | 8.6188 |  |  |  |  | 0 | 0
1419 | SWETWATR_4G | 4 | West | YES | 0.12334 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.28729 | 61 | 61 |  |  |  |  | 0.28729 | 17.525 |  |  |  |  | 0 | 0
1418 | SWETWATR_3G | 3 | West | YES | 0.12334 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.28729 | 68 | 68 |  |  |  |  | 0.28729 | 19.536 |  |  |  |  | 0 | 0
1417 | SWETWATR_2G | 2 | West | YES | 0.12334 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.28729 | 72 | 72 |  |  |  |  | 0.28729 | 20.6852 |  |  |  |  | 0 | 0
60081 | WHRLWIND1A | 1 | West | YES | 0.12384 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.2878 | 0 | 60 |  |  |  |  | 0.2878 | 17.2679 |  |  |  |  | 0 | 0
1437 | MESQUITW_1G | 1 | North | YES | 0.12542 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.28938 | 0 | 400 | 50.1684 | 400 |  |  | 0.28938 | 115.7514 |  |  |  |  | 0 | 0
1438 | MESQUITW_2G | 1 | North | YES | 0.12543 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.28938 | 0 | 236 | 29.6005 | 236 |  |  | 0.28938 | 68.2945 |  |  |  |  | 0 | 0
1442 | COKFIELD_5 | 1 | North | YES | 0.12625 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.29021 | 0 | 165 | 20.8311 | 165 |  |  | 0.29021 | 47.8841 |  |  |  |  | 0 | 0
6100 | OKLA7A | EQ | West | YES | 0.12691 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.29087 | 0 | 0 |  |  |  |  | 0.29087 | 0 |  |  |  |  | 0 | 0
6752 | OKLA0A | 1 | West | YES | 0.12691 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.29087 | 0 | 649.7 |  |  |  |  | 0.29087 | 188.9753 |  |  |  |  | 0 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.16023 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.16023 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.16023 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.16023 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.16023 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.16023 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.16023 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.16023 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.16023 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.16023 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.16023 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.16023 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.16023 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.16023 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.16023 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.29124 | 0 | 0 |  |  | 0 | 0 | -0.29124 | 0 |  |  |  |  | 0 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.12811 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.29207 | 242 | 242 | 31.0024 | 242 |  |  | 0.29207 | 70.6801 |  |  |  |  | 0 | 0
332 | RWMILLER01 | 1 | North | YES | 0.12818 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.29214 | 73 | 73 | 9.3571 | 73 |  |  | 0.29214 | 21.326 |  |  |  |  | 0 | 0
336 | RWMILLER05 | 5 | North | YES | 0.12818 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.29214 | 101 | 101 | 12.9462 | 101 |  |  | 0.29214 | 29.5059 |  |  |  |  | 0 | 0
335 | RWMILLER04 | 4 | North | YES | 0.12818 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.29214 | 102 | 102 | 13.0744 | 102 |  |  | 0.29214 | 29.798 |  |  |  |  | 0 | 0
333 | RWMILLER02 | 2 | North | YES | 0.12818 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.29214 | 119 | 119 | 15.2534 | 119 |  |  | 0.29214 | 34.7644 |  |  |  |  | 0 | 0
334 | RWMILLER03 | 3 | North | YES | 0.12818 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.29214 | 208 | 208 | 26.6614 | 208 |  |  | 0.29214 | 60.7646 |  |  |  |  | 0 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.12886 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.29281 | 366 | 366 | 47.1617 | 366 |  |  | 0.29281 | 107.1701 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.12897 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.12897 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.29292 | 0 | 0 | 0 | 0 |  |  | 0.29292 | 0 |  |  |  |  | 0 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.12915 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.29311 | 0 | 120 | 15.4984 | 120 |  |  | 0.29311 | 35.1733 |  |  |  |  | 0 | 0
344 | MRSSHPRD | 1 | North | YES | 0.12934 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.2933 | 0 | 0 | 0 | 0 |  |  | 0.2933 | 0 |  |  |  |  | 0 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.12934 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.2933 | 0 | 0 | 0 | 0 |  |  | 0.2933 | 0 |  |  |  |  | 0 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.12969 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.29365 | 0 | 0 | 0 | 0 |  |  | 0.29365 | 0 |  |  |  |  | 0 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.12969 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.29365 | 0 | 0 | 0 | 0 |  |  | 0.29365 | 0 |  |  |  |  | 0 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.16281 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.29382 | 0 | 0 |  |  | 0 | 0 | -0.29382 | 0 |  |  |  |  | 0 | 0
1895 | DECRDOVA_5G | D | North | YES | 0.13052 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.29448 | 68 | 68 | 8.8752 | 68 |  |  | 0.29448 | 20.0243 |  |  |  |  | 0 | 0
1893 | DECRDOVA_3G | B | North | YES | 0.13052 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.29448 | 69 | 69 | 9.0057 | 69 |  |  | 0.29448 | 20.3188 |  |  |  |  | 0 | 0
1894 | DECRDOVA_4G | C | North | YES | 0.13052 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.29448 | 69 | 69 | 9.0057 | 69 |  |  | 0.29448 | 20.3188 |  |  |  |  | 0 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.13052 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.29448 | 70 | 70 | 9.1363 | 70 |  |  | 0.29448 | 20.6133 |  |  |  |  | 0 | 0
503 | NTHTEXAS01 | 1 | North | YES | 0.13058 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.29454 | 18 | 18 | 2.3505 | 18 |  |  | 0.29454 | 5.3017 |  |  |  |  | 0 | 0
504 | NTHTEXAS02 | 2 | North | YES | 0.13058 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.29454 | 18 | 18 | 2.3505 | 18 |  |  | 0.29454 | 5.3017 |  |  |  |  | 0 | 0
505 | NTHTEXAS03 | 3 | North | YES | 0.13058 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.29454 | 38 | 38 | 4.9622 | 38 |  |  | 0.29454 | 11.1925 |  |  |  |  | 0 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.1312 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.29515 | 0 | 0 | 0 | 0 |  |  | 0.29515 | 0 |  |  |  |  | 0 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.1312 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.29515 | 0 | 0 | 0 | 0 |  |  | 0.29515 | 0 |  |  |  |  | 0 | 0
1453 | WCPWRCO_1G | 1 | North | YES | 0.13141 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.29537 | 204 | 204 | 26.808 | 204 |  |  | 0.29537 | 60.2554 |  |  |  |  | 0 | 0
1454 | WCPWRCO_2G | 2 | North | YES | 0.13141 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.29537 | 204 | 204 | 26.808 | 204 |  |  | 0.29537 | 60.2554 |  |  |  |  | 0 | 0
1455 | WCPWRCO_3G | 3 | North | YES | 0.13141 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.29537 | 242 | 242 | 31.8017 | 242 |  |  | 0.29537 | 71.4794 |  |  |  |  | 0 | 0
1878 | WLFHOLW_2G | 2 | North | YES | 0.13156 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.29552 | 215.7 | 215.7 | 28.3779 | 215.7 |  |  | 0.29552 | 63.7436 |  |  |  |  | 0 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.13156 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.29552 | 217.3 | 217.3 | 28.5884 | 217.3 |  |  | 0.29552 | 64.2164 |  |  |  |  | 0 | 0
1879 | WLFHOLW_3G | 3 | North | YES | 0.13156 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.29552 | 272.4 | 272.4 | 35.8375 | 272.4 |  |  | 0.29552 | 80.4995 |  |  |  |  | 0 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.16462 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 |  |  |  |  | 0 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.16462 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 |  |  |  |  | 0 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.16462 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 |  |  |  |  | 0 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.16462 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 |  |  |  |  | 0 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.16462 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.29562 | 0 | 0 |  |  | 0 | 0 | -0.29562 | 0 |  |  |  |  | 0 | 0
1889 | DECRDOVA_1G | 1 | North | YES | 0.13182 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.29578 | 779 | 779 | 102.6917 | 779 |  |  | 0.29578 | 230.4146 |  |  |  |  | 0 | 0
581 | JCKCNTY802 | 2 | North | YES | 0.1323 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.29626 | 147 | 147 | 19.4481 | 147 |  |  | 0.29626 | 43.5499 |  |  |  |  | 0 | 0
582 | JCKCNTY803 | 3 | North | YES | 0.1323 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.29626 | 147 | 147 | 19.4481 | 147 |  |  | 0.29626 | 43.5499 |  |  |  |  | 0 | 0
580 | JCKCNTY801 | 1 | North | YES | 0.1323 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.29626 | 288 | 288 | 38.1024 | 288 |  |  | 0.29626 | 85.3222 |  |  |  |  | 0 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.16531 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0 |  |  |  |  | 0 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.16531 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0 |  |  |  |  | 0 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.16531 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0 |  |  |  |  | 0 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.16531 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.29631 | 0 | 0 |  |  | 0 | 0 | -0.29631 | 0 |  |  |  |  | 0 | 0
1944 | MDLTHELP_4G | 4 | North | YES | 0.13269 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.29665 | 211 | 211 | 27.998 | 211 |  |  | 0.29665 | 62.593 |  |  |  |  | 0 | 0
1943 | MDLTHELP_3G | 3 | North | YES | 0.13269 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.29665 | 212 | 212 | 28.1307 | 212 |  |  | 0.29665 | 62.8897 |  |  |  |  | 0 | 0
1937 | MDLTHELP_5G | 5 | North | YES | 0.13269 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.29665 | 224 | 224 | 29.723 | 224 |  |  | 0.29665 | 66.4495 |  |  |  |  | 0 | 0
1938 | MDLTHELP_6G | 6 | North | YES | 0.13269 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.29665 | 226 | 226 | 29.9884 | 226 |  |  | 0.29665 | 67.0428 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | E | Houston | YES | -0.1662 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.29721 | 57 | 57 |  |  | -9.4734 | 57 | -0.29721 | -16.9408 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | D | Houston | YES | -0.1662 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.29721 | 55 | 55 |  |  | -9.141 | 55 | -0.29721 | -16.3464 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | F | Houston | YES | -0.1662 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.29721 | 54 | 54 |  |  | -8.9748 | 54 | -0.29721 | -16.0491 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | C | Houston | YES | -0.1662 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.29721 | 47 | 47 |  |  | -7.8114 | 47 | -0.29721 | -13.9687 |  |  |  |  | 0 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.1666 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.29761 | 0 | 0 |  |  | 0 | 0 | -0.29761 | 0 |  |  |  |  | 0 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.1666 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.29761 | 0 | 0 |  |  | 0 | 0 | -0.29761 | 0 |  |  |  |  | 0 | 0
1861 | EAGLEMNT_1G | MB | North | YES | 0.13366 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0 |  |  |  |  | 0 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.13366 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0 |  |  |  |  | 0 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.13366 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.29762 | 0 | 0 | 0 | 0 |  |  | 0.29762 | 0 |  |  |  |  | 0 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.16693 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.29794 | 282 | 282 |  |  | -47.0743 | 282 | -0.29794 | -84.0181 |  |  |  |  | 0 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.16693 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.29794 | 163.2 | 163.2 |  |  | -27.243 | 163.2 | -0.29794 | -48.6232 |  |  |  |  | 0 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.16693 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.29794 | 157.5 | 157.5 |  |  | -26.2915 | 157.5 | -0.29794 | -46.925 |  |  |  |  | 0 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.16693 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.29794 | 157.1 | 157.1 |  |  | -26.2247 | 157.1 | -0.29794 | -46.8058 |  |  |  |  | 0 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.16693 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.29794 | 157 | 157 |  |  | -26.208 | 157 | -0.29794 | -46.776 |  |  |  |  | 0 | 0
1942 | MDLTHELP_2G | 2 | North | YES | 0.13411 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.29807 | 216.1 | 216.1 | 28.9818 | 216.1 |  |  | 0.29807 | 64.413 |  |  |  |  | 0 | 0
1941 | MDLTHELP_1G | 1 | North | YES | 0.13411 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.29807 | 216.4 | 216.4 | 29.0221 | 216.4 |  |  | 0.29807 | 64.5025 |  |  |  |  | 0 | 0
1947 | HANDLEY_3G | 3 | North | YES | 0.13422 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.29818 | 395 | 395 | 53.0173 | 395 |  |  | 0.29818 | 117.7805 |  |  |  |  | 0 | 0
1949 | HANDLEY_5G | 5 | North | YES | 0.13422 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.29818 | 435 | 435 | 58.3861 | 435 |  |  | 0.29818 | 129.7077 |  |  |  |  | 0 | 0
728 | WOLFRIDGE801 | 1 | North | YES | 0.13423 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.29819 | 0 | 112.5 | 15.1009 | 112.5 |  |  | 0.29819 | 33.5461 |  |  |  |  | 0 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.16726 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.29827 | 0 | 0 |  |  | 0 | 0 | -0.29827 | 0 |  |  |  |  | 0 | 0
1948 | HANDLEY_4G | 4 | North | YES | 0.13446 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.29842 | 435 | 435 | 58.4914 | 435 |  |  | 0.29842 | 129.8129 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.16758 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.29859 | 18 | 18 |  |  | -3.0164 | 18 | -0.29859 | -5.3745 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | -0.16758 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.29859 | 12 | 12 |  |  | -2.0109 | 12 | -0.29859 | -3.583 |  |  |  |  | 0 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.1676 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.2986 | 176 | 176 |  |  | -29.4971 | 176 | -0.2986 | -52.5542 |  |  |  |  | 0 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.16762 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.29863 | 165 | 165 |  |  | -27.6575 | 165 | -0.29863 | -49.2735 |  |  |  |  | 0 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.16763 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.29864 | 0 | 0 |  |  | 0 | 0 | -0.29864 | 0 |  |  |  |  | 0 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.16763 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.29864 | 0 | 0 |  |  | 0 | 0 | -0.29864 | 0 |  |  |  |  | 0 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.16771 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.29871 | 213 | 213 |  |  | -35.7214 | 213 | -0.29871 | -63.6257 |  |  |  |  | 0 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.16771 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.29872 | 16.2 | 16.2 |  |  | -2.7169 | 16.2 | -0.29872 | -4.8392 |  |  |  |  | 0 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.16772 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0 |  |  |  |  | 0 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.16772 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0 |  |  |  |  | 0 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.16772 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0 |  |  |  |  | 0 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.16772 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.29872 | 0 | 0 |  |  | 0 | 0 | -0.29872 | 0 |  |  |  |  | 0 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.16773 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.29873 | 228 | 228 |  |  | -38.2413 | 228 | -0.29873 | -68.1108 |  |  |  |  | 0 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.16773 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0 |  |  |  |  | 0 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.16773 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0 |  |  |  |  | 0 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.16773 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.29873 | 0 | 0 |  |  | 0 | 0 | -0.29873 | 0 |  |  |  |  | 0 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.16818 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0 |  |  |  |  | 0 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.16818 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.16818 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.16818 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.29918 | 0 | 0 |  |  | 0 | 0 | -0.29918 | 0 |  |  |  |  | 0 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.13553 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.29948 | 61 | 61 | 8.267 | 61 |  |  | 0.29948 | 18.2684 |  |  |  |  | 0 | 0
924 | SPENCER_G5 | 1 | North | YES | 0.13553 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.29948 | 66 | 66 | 8.9446 | 66 |  |  | 0.29948 | 19.7658 |  |  |  |  | 0 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.16881 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.29982 | 0 | 0 |  |  | 0 | 0 | -0.29982 | 0 |  |  |  |  | 0 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.16895 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.29995 | 42 | 42 |  |  | -7.0957 | 42 | -0.29995 | -12.598 |  |  |  |  | 0 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.16895 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.29995 | 42 | 42 |  |  | -7.0957 | 42 | -0.29995 | -12.598 |  |  |  |  | 0 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.16895 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.29995 | 39 | 39 |  |  | -6.5889 | 39 | -0.29995 | -11.6981 |  |  |  |  | 0 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.16895 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.29995 | 39 | 39 |  |  | -6.5889 | 39 | -0.29995 | -11.6981 |  |  |  |  | 0 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.16905 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.30005 | 0 | 0 |  |  | 0 | 0 | -0.30005 | 0 |  |  |  |  | 0 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.16905 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.30005 | 0 | 0 |  |  | 0 | 0 | -0.30005 | 0 |  |  |  |  | 0 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.16998 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.30099 | 108 | 108 |  |  | -18.3579 | 108 | -0.30099 | -32.5066 |  |  |  |  | 0 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.16998 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.30099 | 107 | 107 |  |  | -18.188 | 107 | -0.30099 | -32.2057 |  |  |  |  | 0 | 0
48881 | THW_4344 | G | Houston | YES | -0.16998 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.30099 | 58 | 58 |  |  | -9.8589 | 58 | -0.30099 | -17.4573 |  |  |  |  | 0 | 0
48881 | THW_4344 | H | Houston | YES | -0.16998 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.30099 | 58 | 58 |  |  | -9.8589 | 58 | -0.30099 | -17.4573 |  |  |  |  | 0 | 0
48877 | THW_3334 | D | Houston | YES | -0.16998 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.30099 | 57 | 57 |  |  | -9.6889 | 57 | -0.30099 | -17.1563 |  |  |  |  | 0 | 0
48879 | THW_4142 | E | Houston | YES | -0.16998 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.30099 | 56 | 56 |  |  | -9.5189 | 56 | -0.30099 | -16.8553 |  |  |  |  | 0 | 0
48875 | THW_3132 | A | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543 |  |  |  |  | 0 | 0
48877 | THW_3334 | C | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543 |  |  |  |  | 0 | 0
48879 | THW_4142 | F | Houston | YES | -0.16998 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.30099 | 55 | 55 |  |  | -9.349 | 55 | -0.30099 | -16.5543 |  |  |  |  | 0 | 0
48875 | THW_3132 | B | Houston | YES | -0.16998 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.30099 | 53 | 53 |  |  | -9.009 | 53 | -0.30099 | -15.9523 |  |  |  |  | 0 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.17071 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.30171 | 746 | 746 |  |  | -127.3467 | 746 | -0.30171 | -225.0775 |  |  |  |  | 0 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.13798 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.30194 | 156 | 156 | 21.5257 | 156 |  |  | 0.30194 | 47.103 |  |  |  |  | 0 | 0
2382 | NTHLK2_G | 2 | North | YES | 0.13798 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.30194 | 181 | 181 | 24.9753 | 181 |  |  | 0.30194 | 54.6516 |  |  |  |  | 0 | 0
2383 | NTHLK3_G | 3 | North | YES | 0.13798 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.30194 | 329 | 329 | 45.3971 | 329 |  |  | 0.30194 | 99.3391 |  |  |  |  | 0 | 0
12323 | ENNSTRAC_2G | 2 | North | YES | 0.13803 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.30199 | 116 | 116 | 16.0114 | 116 |  |  | 0.30199 | 35.0304 |  |  |  |  | 0 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | 0.13803 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.30199 | 196 | 196 | 27.0537 | 196 |  |  | 0.30199 | 59.1894 |  |  |  |  | 0 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.1711 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.3021 | 12 | 12 |  |  | -2.0532 | 12 | -0.3021 | -3.6252 |  |  |  |  | 0 | 0
2371 | COLLIN_1G | MB | North | YES | 0.13823 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.30219 | 0 | 0 | 0 | 0 |  |  | 0.30219 | 0 |  |  |  |  | 0 | 0
49803 | EXN_15GT | 1 | Houston | YES | -0.17121 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.17121 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.17121 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.17121 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.17121 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.17121 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.17121 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.17121 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.17121 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.17121 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.17121 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.30221 | 0 | 0 |  |  | 0 | 0 | -0.30221 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.17169 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.3027 | 0 | 0 |  |  | 0 | 0 | -0.3027 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.17169 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.3027 | 0 | 0 |  |  | 0 | 0 | -0.3027 | 0 |  |  |  |  | 0 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.17171 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.30271 | 0 | 0 |  |  | 0 | 0 | -0.30271 | 0 |  |  |  |  | 0 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.17172 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.30273 | 744 | 744 |  |  | -127.7619 | 744 | -0.30273 | -225.2307 |  |  |  |  | 0 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.17175 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 |  |  |  |  | 0 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.17175 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 |  |  |  |  | 0 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.17175 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 |  |  |  |  | 0 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.17175 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 |  |  |  |  | 0 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.17175 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 |  |  |  |  | 0 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.17175 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 |  |  |  |  | 0 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.17175 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.30275 | 0 | 0 |  |  | 0 | 0 | -0.30275 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 1 | North | YES | 0.13895 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.30291 | 0 | 0 | 0 | 0 |  |  | 0.30291 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 2 | North | YES | 0.13895 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.30291 | 0 | 0 | 0 | 0 |  |  | 0.30291 | 0 |  |  |  |  | 0 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.17201 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.30302 | 0 | 0 |  |  | 0 | 0 | -0.30302 | 0 |  |  |  |  | 0 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.13918 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.30314 | 170 | 170 | 23.6606 | 170 |  |  | 0.30314 | 51.5334 |  |  |  |  | 0 | 0
1688 | VALLEY_2G | 2 | North | YES | 0.13918 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.30314 | 527 | 527 | 73.3479 | 527 |  |  | 0.30314 | 159.7535 |  |  |  |  | 0 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431 |  |  |  |  | 0 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431 |  |  |  |  | 0 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.17215 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.30316 | 172 | 172 |  |  | -29.61 | 172 | -0.30316 | -52.1431 |  |  |  |  | 0 | 0
2414 | MTCK7_G | 7 | North | YES | 0.13923 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.30319 | 115 | 115 | 16.0112 | 115 |  |  | 0.30319 | 34.8663 |  |  |  |  | 0 | 0
2413 | MTCK6_G | 6 | North | YES | 0.13923 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.30319 | 118 | 118 | 16.4289 | 118 |  |  | 0.30319 | 35.7759 |  |  |  |  | 0 | 0
2417 | MTCK8_G | 8 | North | YES | 0.13923 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.30319 | 556 | 556 | 77.4108 | 556 |  |  | 0.30319 | 168.5711 |  |  |  |  | 0 | 0
11691 | KMICHICT1_G | 1 | North | YES | 0.13947 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30343 | 144 | 144 | 20.0843 | 144 |  |  | 0.30343 | 43.6941 |  |  |  |  | 0 | 0
11694 | KMICHICT4_G | 4 | North | YES | 0.13947 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30343 | 144 | 144 | 20.0843 | 144 |  |  | 0.30343 | 43.6941 |  |  |  |  | 0 | 0
11692 | KMICHICT2_G | 2 | North | YES | 0.13947 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.30343 | 146 | 146 | 20.3632 | 146 |  |  | 0.30343 | 44.301 |  |  |  |  | 0 | 0
11695 | KMICHICT5_G | 5 | North | YES | 0.13947 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.30343 | 148 | 148 | 20.6422 | 148 |  |  | 0.30343 | 44.9079 |  |  |  |  | 0 | 0
11696 | KMICHIST6_G | 6 | North | YES | 0.13947 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.30343 | 310 | 310 | 43.2369 | 310 |  |  | 0.30343 | 94.0638 |  |  |  |  | 0 | 0
11693 | KMICHIST3_G | 3 | North | YES | 0.13947 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.30343 | 312 | 312 | 43.5159 | 312 |  |  | 0.30343 | 94.6706 |  |  |  |  | 0 | 0
1689 | VALLEY_3G | 3 | North | YES | 0.13947 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.30343 | 375 | 375 | 52.3028 | 375 |  |  | 0.30343 | 113.7868 |  |  |  |  | 0 | 0
1679 | LAMARPWR_2G | 2 | North | YES | 0.1396 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30356 | 156 | 156 | 21.7781 | 156 |  |  | 0.30356 | 47.3554 |  |  |  |  | 0 | 0
1681 | LAMARPWR_4G | 4 | North | YES | 0.1396 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30356 | 156 | 156 | 21.7781 | 156 |  |  | 0.30356 | 47.3554 |  |  |  |  | 0 | 0
1682 | LAMARPWR_5G | 5 | North | YES | 0.1396 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.30356 | 157 | 157 | 21.9177 | 157 |  |  | 0.30356 | 47.659 |  |  |  |  | 0 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.1396 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.30356 | 160 | 160 | 22.3365 | 160 |  |  | 0.30356 | 48.5697 |  |  |  |  | 0 | 0
1680 | LAMARPWR_3G | 3 | North | YES | 0.1396 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.30356 | 196 | 196 | 27.3622 | 196 |  |  | 0.30356 | 59.4979 |  |  |  |  | 0 | 0
1683 | LAMARPWR_6G | 6 | North | YES | 0.1396 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.30356 | 198 | 198 | 27.6414 | 198 |  |  | 0.30356 | 60.105 |  |  |  |  | 0 | 0
1675 | PEC_1G | 1 | North | YES | 0.13969 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0 |  |  |  |  | 0 | 0
1676 | PEC_2G | 2 | North | YES | 0.13969 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0 |  |  |  |  | 0 | 0
1677 | PEC_3G | 3 | North | YES | 0.13969 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.30365 | 0 | 0 | 0 | 0 |  |  | 0.30365 | 0 |  |  |  |  | 0 | 0
5925 | DCEAST | EQ | North | YES | 0.13983 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.30379 | 0 | 0 | 0 | 0 |  |  | 0.30379 | 0 |  |  |  |  | 0 | 0
1701 | MOSES_1G | 1 | North | YES | 0.13983 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 558 | 78.0279 | 558 |  |  | 0.30379 | 169.5162 |  |  |  |  | 0 | 0
1702 | MOSES_2G | 2 | North | YES | 0.13983 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 579 | 80.9645 | 579 |  |  | 0.30379 | 175.8959 |  |  |  |  | 0 | 0
1703 | MOSES_3G | 3 | North | YES | 0.13983 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.30379 | 0 | 808 | 112.9867 | 808 |  |  | 0.30379 | 245.4643 |  |  |  |  | 0 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.17299 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.304 | 269.2 | 269.2 |  |  | -46.57 | 269.2 | -0.304 | -81.8369 |  |  |  |  | 0 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.17299 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.304 | 162.8 | 162.8 |  |  | -28.1634 | 162.8 | -0.304 | -49.4913 |  |  |  |  | 0 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.17299 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.304 | 161.4 | 161.4 |  |  | -27.9212 | 161.4 | -0.304 | -49.0657 |  |  |  |  | 0 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.17299 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.304 | 158.9 | 158.9 |  |  | -27.4887 | 158.9 | -0.304 | -48.3057 |  |  |  |  | 0 | 0
845 | OLINGER_G4 | 1 | North | YES | 0.14013 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.30409 | 76 | 76 | 10.6497 | 76 |  |  | 0.30409 | 23.1105 |  |  |  |  | 0 | 0
842 | OLINGER_G1 | 1 | North | YES | 0.14013 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.30409 | 79 | 79 | 11.0701 | 79 |  |  | 0.30409 | 24.0228 |  |  |  |  | 0 | 0
843 | OLINGER_G2 | 1 | North | YES | 0.14013 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.30409 | 110 | 110 | 15.4141 | 110 |  |  | 0.30409 | 33.4494 |  |  |  |  | 0 | 0
844 | OLINGER_G3 | 1 | North | YES | 0.14013 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.30409 | 150 | 150 | 21.0192 | 150 |  |  | 0.30409 | 45.6128 |  |  |  |  | 0 | 0
837 | NEWMAN_G5 | 1 | North | YES | 0.14016 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.30412 | 40 | 40 | 5.6063 | 40 |  |  | 0.30412 | 12.1646 |  |  |  |  | 0 | 0
948 | STEAM1 | 1 | North | YES | 0.14031 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.30427 | 20 | 20 | 2.8063 | 20 |  |  | 0.30427 | 6.0855 |  |  |  |  | 0 | 0
949 | STEAM2 | 1 | North | YES | 0.14031 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.30427 | 26 | 26 | 3.6482 | 26 |  |  | 0.30427 | 7.9111 |  |  |  |  | 0 | 0
950 | STEAM3 | 1 | North | YES | 0.14031 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.30427 | 42 | 42 | 5.8932 | 42 |  |  | 0.30427 | 12.7794 |  |  |  |  | 0 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.17327 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.30428 | 398 | 398 |  |  | -68.9619 | 398 | -0.30428 | -121.1024 |  |  |  |  | 0 | 0
48885 | THW_5152 | B | Houston | YES | -0.17364 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.30465 | 59 | 59 |  |  | -10.2449 | 59 | -0.30465 | -17.9743 |  |  |  |  | 0 | 0
48887 | THW_5556 | E | Houston | YES | -0.17364 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.30465 | 59 | 59 |  |  | -10.2449 | 59 | -0.30465 | -17.9743 |  |  |  |  | 0 | 0
48885 | THW_5152 | A | Houston | YES | -0.17364 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.30465 | 58 | 58 |  |  | -10.0713 | 58 | -0.30465 | -17.6697 |  |  |  |  | 0 | 0
48886 | THW_5354 | D | Houston | YES | -0.17364 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.30465 | 58 | 58 |  |  | -10.0713 | 58 | -0.30465 | -17.6697 |  |  |  |  | 0 | 0
48886 | THW_5354 | C | Houston | YES | -0.17364 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.30465 | 57 | 57 |  |  | -9.8977 | 57 | -0.30465 | -17.365 |  |  |  |  | 0 | 0
48887 | THW_5556 | F | Houston | YES | -0.17364 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.30465 | 57 | 57 |  |  | -9.8977 | 57 | -0.30465 | -17.365 |  |  |  |  | 0 | 0
12440 | PARKD_1SVC8 | 1 | North | YES | 0.14071 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30467 | 0 | 0 | 0 | 0 |  |  | 0.30467 | 0 |  |  |  |  | 0 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.14071 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30467 | 0 | 0 | 0 | 0 |  |  | 0.30467 | 0 |  |  |  |  | 0 | 0
2451 | LKHB1_G | 1 | North | YES | 0.14076 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.30471 | 391 | 391 | 55.036 | 391 |  |  | 0.30471 | 119.1434 |  |  |  |  | 0 | 0
2452 | LKHB2_G | 2 | North | YES | 0.14076 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.30471 | 516 | 516 | 72.6306 | 516 |  |  | 0.30471 | 157.2327 |  |  |  |  | 0 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.14146 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.30542 | 161 | 161 | 22.7747 | 161 |  |  | 0.30542 | 49.1719 |  |  |  |  | 0 | 0
12422 | FPLEFR2B_G | 2 | North | YES | 0.14146 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.30542 | 161 | 161 | 22.7747 | 161 |  |  | 0.30542 | 49.1719 |  |  |  |  | 0 | 0
12421 | FPLEFR2A_G | 1 | North | YES | 0.14146 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.30542 | 162 | 162 | 22.9162 | 162 |  |  | 0.30542 | 49.4773 |  |  |  |  | 0 | 0
12423 | FPLEFR2C_G | 3 | North | YES | 0.14146 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.30542 | 163 | 163 | 23.0577 | 163 |  |  | 0.30542 | 49.7827 |  |  |  |  | 0 | 0
12412 | FPLEFR1B_G | 2 | North | YES | 0.14146 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.30542 | 164 | 164 | 23.1991 | 164 |  |  | 0.30542 | 50.0881 |  |  |  |  | 0 | 0
12413 | FPLEFR1C_G | 3 | North | YES | 0.14146 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.30542 | 164 | 164 | 23.1991 | 164 |  |  | 0.30542 | 50.0881 |  |  |  |  | 0 | 0
12414 | FPLEFR1S_G | 4 | North | YES | 0.14146 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.30542 | 414 | 414 | 58.5636 | 414 |  |  | 0.30542 | 126.442 |  |  |  |  | 0 | 0
12424 | FPLEFR2S_G | 4 | North | YES | 0.14146 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.30542 | 415 | 415 | 58.7051 | 415 |  |  | 0.30542 | 126.7474 |  |  |  |  | 0 | 0
3126 | TRINIDAD_6G | 1 | North | YES | 0.14175 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.30571 | 224 | 224 | 31.7531 | 224 |  |  | 0.30571 | 68.4796 |  |  |  |  | 0 | 0
3097 | MARTLAKE_1G | 1 | North | YES | 0.14521 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 790 | 114.7167 | 790 |  |  | 0.30917 | 244.2431 |  |  |  |  | 0 | 0
3098 | MARTLAKE_2G | 2 | North | YES | 0.14521 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 795 | 115.4427 | 795 |  |  | 0.30917 | 245.789 |  |  |  |  | 0 | 0
3099 | MARTLAKE_3G | 3 | North | YES | 0.14521 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.30917 | 0 | 804 | 116.7496 | 804 |  |  | 0.30917 | 248.5715 |  |  |  |  | 0 | 0
13117 | TGATEWAY_2G | 2 | North | YES | 0.14572 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.30967 | 130 | 130 | 18.9429 | 130 |  |  | 0.30967 | 40.2574 |  |  |  |  | 0 | 0
13118 | TGATEWAY_3G | 3 | North | YES | 0.14572 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.30967 | 148 | 148 | 21.5658 | 148 |  |  | 0.30967 | 45.8315 |  |  |  |  | 0 | 0
13116 | TGATEWAY_1G | 1 | North | YES | 0.14572 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.30967 | 151 | 151 | 22.003 | 151 |  |  | 0.30967 | 46.7605 |  |  |  |  | 0 | 0
13119 | TGATEWAY_4G | 4 | North | YES | 0.14572 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.30967 | 399 | 399 | 58.1403 | 399 |  |  | 0.30967 | 123.5593 |  |  |  |  | 0 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.17877 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 |  |  |  |  | 0 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.17877 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 |  |  |  |  | 0 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.17877 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 |  |  |  |  | 0 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.17877 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 |  |  |  |  | 0 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.17877 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.30978 | 0 | 0 |  |  | 0 | 0 | -0.30978 | 0 |  |  |  |  | 0 | 0
3348 | CHAMPION_1G | MB | North | YES | 0.14625 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0 |  |  |  |  | 0 | 0
3309 | ASPN_G | 1 | North | YES | 0.1463 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.31026 | 50 | 50 | 7.3151 | 50 |  |  | 0.31026 | 15.5129 |  |  |  |  | 0 | 0
3107 | STRYKER_1G | 1 | North | YES | 0.14652 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.31048 | 182 | 182 | 26.6668 | 182 |  |  | 0.31048 | 56.5071 |  |  |  |  | 0 | 0
3108 | STRYKER_2G | 2 | North | YES | 0.14652 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.31048 | 484 | 484 | 70.9162 | 484 |  |  | 0.31048 | 150.2716 |  |  |  |  | 0 | 0
13134 | CALFREST_4G | 4 | North | YES | 0.15119 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.31515 | 151.5 | 151.5 | 22.9053 | 151.5 |  |  | 0.31515 | 47.7448 |  |  |  |  | 0 | 0
13135 | CALFREST_5G | 5 | North | YES | 0.15119 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.31515 | 152.3 | 152.3 | 23.0262 | 152.3 |  |  | 0.31515 | 47.997 |  |  |  |  | 0 | 0
13136 | CALFREST_6G | 6 | North | YES | 0.15119 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.31515 | 177.5 | 177.5 | 26.8362 | 177.5 |  |  | 0.31515 | 55.9387 |  |  |  |  | 0 | 0
13131 | CALFREST_1G | 1 | North | YES | 0.15145 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.31541 | 150.7 | 150.7 | 22.8232 | 150.7 |  |  | 0.31541 | 47.5316 |  |  |  |  | 0 | 0
13132 | CALFREST_2G | 2 | North | YES | 0.15145 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.31541 | 151 | 151 | 22.8686 | 151 |  |  | 0.31541 | 47.6262 |  |  |  |  | 0 | 0
13133 | CALFREST_3G | 3 | North | YES | 0.15145 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.31541 | 177.4 | 177.4 | 26.8669 | 177.4 |  |  | 0.31541 | 55.9529 |  |  |  |  | 0 | 0
3382 | BBRN_2G | 2 | North | YES | 0.15256 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.31652 | 0 | 589 | 89.8596 | 589 |  |  | 0.31652 | 186.4306 |  |  |  |  | 0 | 0
3381 | BBRN_1G | 1 | North | YES | 0.15256 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.31652 | 0 | 618 | 94.2839 | 618 |  |  | 0.31652 | 195.6097 |  |  |  |  | 0 | 0
48722 | LEG_2___2 | 2 | North | YES | 0.17253 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.33648 | 0 | 819 | 141.2996 | 819 |  |  | 0.33648 | 275.5808 |  |  |  |  | 0 | 0
48721 | LEG_1___1 | 1 | North | YES | 0.17253 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.33648 | 0 | 827 | 142.6798 | 827 |  |  | 0.33648 | 278.2727 |  |  |  |  | 0 | 0
39960 | TNTNPONE_18 | 1 | North | YES | 0.1953 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.35926 | 0 | 152.3 | 29.7448 | 152.3 |  |  | 0.35926 | 54.7155 |  |  |  |  | 0 | 0
39970 | TNTNPONE_28 | 1 | North | YES | 0.1953 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.35926 | 0 | 153 | 29.8815 | 153 |  |  | 0.35926 | 54.967 |  |  |  |  | 0 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.22242 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.38638 | 46 | 46 | 10.2315 | 46 |  |  | 0.38638 | 17.7735 |  |  |  |  | 0 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.22242 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.38638 | 48 | 48 | 10.6764 | 48 |  |  | 0.38638 | 18.5463 |  |  |  |  | 0 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.22242 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.38638 | 105 | 105 | 23.3545 | 105 |  |  | 0.38638 | 40.5701 |  |  |  |  | 0 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | 0.22931 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0 |  |  |  |  | 0 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.22931 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0 |  |  |  |  | 0 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | 0.22931 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0 |  |  |  |  | 0 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.22931 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.39327 | 0 | 0 | 0 | 0 |  |  | 0.39327 | 0 |  |  |  |  | 0 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.22931 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.39327 | 17 | 17 | 3.8983 | 17 |  |  | 0.39327 | 6.6856 |  |  |  |  | 0 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.23292 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.39688 | 32 | 32 | 7.4535 | 32 |  |  | 0.39688 | 12.7001 |  |  |  |  | 0 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | 0.25699 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.42094 | 0 | 463 | 118.9841 | 463 |  |  | 0.42094 | 194.8964 |  |  |  |  | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0

## Zones
Houston | -1
North | 1
South | -1
West | 1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | Houston | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1073 | SCURRYCW_2G | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3126 | TRINIDAD_6G | GST
3309 | ASPN_G | Bio
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5920 | WELSHDC1 | DCTie
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6096 | NORTHDC7 | DCTie
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NBEC7 | GST
8442 | NBEC7 | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11056 | ROSCOE_1G | Wind
11057 | CHAMPION_1G | Wind
11058 | PYRON_1G | Wind
11059 | INADALE_1G | Wind
11065 | ELBOWCK_1G | Wind
11147 | NOTREES_1G | Wind
11309 | BULLCREK_2G | Wind
11310 | BULLCREK_1G | Wind
11320 | COYOTE_1G | Wind
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
48940 | WARVUE_GT1 | Cogen
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
71061 | L_SWEETW1_5N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
76095 | L_CAPRSI1_1N | Wind
76096 | L_CAPRSI1_2N | Wind
76097 | L_CAPRGE1_1N | Wind
80003 | MILHWYS | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80263 | B_DAVIS31A | CC
80264 | B_DAVIS41A | CC
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
86104 | CID-138 | DCTie
86105 | CID-230 | DCTie
86106 | CUF-230 | DCTie
86107 | CUF-138 | DCTie
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR