## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  | Summary of Key Data points | Value
File Description: Cont_ Singleton to Wharton and Singleton to Obrien OL_ Tomball to Singleton
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K27 |  | Number of units | 645
|  |  | Dec PTDF cutoff point | 258
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  | Dec PTDF cutoff unit | FRNDDRCS
|  |  | Dec 10% unit | BBRN_2G
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  | Dec max cumltv zone impact - cumltv zone share | 0.022139
|  |  | Dec max cumltv zone impact - cumltv zone share pt | 91
Step 5 | Enter Dennis' file name into cell K27 |  | Dec max cumltv zone impact - cumltv zone share unit | ENNSTRAC_2G
|  |  | North Zonal weighted AWGSF | 0.15194
Step 6 | click the step one button |  | Houston Zonal weighted AWGSF | -0.17072
|  |  | Inc PTDF cutoff point | 387
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  | Inc PTDF cutoff unit | SANDOW_5G
| X6:X30, or to the end of the selected list. |  | Inc 10% unit | BTE_GT3_8045
|  |  | Inc max cumltv zone impact - cumltv zone share | 0.12481
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  | Inc max cumltv zone impact - cumltv zone share pt | 167
| of the formulas in columns L:V (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  | Inc max cumltv zone impact - cumltv zone share unit | CBE_ST34
| If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct leng |  | North Zonal weighted AWGSF | 0.15194
| It is only necessary to match the Distributed Slack - Dec worksheet. |  | Houston Zonal weighted AWGSF | -0.17072
|  |  | Min of zone correlation | 0.10737
Step 9 | Click the step 2 button |  | Bounary gen in Houston Zone | 0
| The last file saved will still be open, yopu will need to close this file. |  | Bounary gen in soucre zone as % of line | 0%
| This sheet willno longer be open. |  | Bounary gen in North Zone | 0
|  |  | Bounary gen in soucre zone as % of line | 0
|  |  | OL element line rating | 1793
|  |  | North Zonal weighted AWGSF | 0.15194
|  | NH_043009automation.xls | Houston Zonal weighted AWGSF | -0.17072
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ Singleton to Wharton and Singleton to Obrien OL_ Tomball to Singleton |  | i_PTDF_DEC_pt | 258 |  | ENNSTRAC_2G | Unit at max
990 | GIBN_CREK_G1 | 1 | North | YES | 0.2205 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.39121 | 0 | 463 | 102.0896 | 463 |  |  | 0.39121 | 181.132 | 0.010992 | 0.013573 |  |  | i_10pctunit | 20 |  | 91 | # units @ max
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.20478 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.3755 | 32 | 32 | 6.5531 | 32 |  |  | 0.3755 | 12.0161 | 0.011752 | 0.014473 |  |  | # units | 645 |  | 0.022139 | delta max
32886 | BRYN_ATKINS3 | MB | North | YES | 0.20233 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0 | 0.011752 | 0.014473 | [5 empty] | Delta
32887 | BRYN_ATKINS6 | MB | North | YES | 0.20233 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0 | 0.011752 | 0.014473 | Weighted Shift Factors |  |  |  | 1 | 0.002581
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.20233 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.37305 | 17 | 17 | 3.4397 | 17 |  |  | 0.37305 | 6.3419 | 0.012155 | 0.014948 | North | 0.15194 |  |  | 2 | 0.0027217
32890 | BRYN_ATKINS4 | MB | North | YES | 0.20233 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0 | 0.012155 | 0.014948 | Houston | -0.17072 |  |  | 3 | 0.0027217
32891 | BRYN_ATKINS5 | MB | North | YES | 0.20233 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0 | 0.012155 | 0.014948 |  |  |  |  | 4 | 0.0027217
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.19756 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.36828 | 48 | 48 | 9.4831 | 48 |  |  | 0.36828 | 17.6776 | 0.013295 | 0.016273 |  |  |  |  | 5 | 0.0027934
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.19756 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.36828 | 46 | 46 | 9.088 | 46 |  |  | 0.36828 | 16.941 | 0.014387 | 0.017543 |  |  |  |  | 6 | 0.0027934
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.19756 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.36828 | 105 | 105 | 20.7443 | 105 |  |  | 0.36828 | 38.6697 | 0.01688 | 0.02044 |  |  |  |  | 7 | 0.0027934
48671 | FTR_GT1_5105 | 1 | North | YES | 0.19668 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.3674 | 154.2 | 154.2 | 30.3288 | 154.2 |  |  | 0.3674 | 56.6535 | 0.02054 | 0.024685 |  |  |  |  | 8 | 0.0029785
48672 | FTR_GT2_5110 | 2 | North | YES | 0.19668 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.3674 | 159 | 159 | 31.2729 | 159 |  |  | 0.3674 | 58.417 | 0.024315 | 0.029063 |  |  |  |  | 9 | 0.0031558
48673 | FTR_GT3_5085 | 3 | North | YES | 0.19668 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.3674 | 158 | 158 | 31.0762 | 158 |  |  | 0.3674 | 58.0496 | 0.028066 | 0.033413 |  |  |  |  | 10 | 0.0035607
48674 | FTR_CN4_5095 | 4 | North | YES | 0.19668 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.3674 | 380 | 380 | 74.7403 | 380 |  |  | 0.3674 | 139.613 | 0.037087 | 0.043874 |  |  |  |  | 11 | 0.0041452
39960 | TNTNPONE_18 | 1 | North | YES | 0.19301 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.36372 | 0 | 152.3 | 29.3947 | 152.3 |  |  | 0.36372 | 55.395 | 0.040703 | 0.048025 |  |  |  |  | 12 | 0.0047479
39970 | TNTNPONE_28 | 1 | North | YES | 0.19301 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.36372 | 0 | 153 | 29.5298 | 153 |  |  | 0.36372 | 55.6496 | 0.044335 | 0.052195 |  |  |  |  | 13 | 0.0053467
48721 | LEG_1___1 | 1 | North | YES | 0.18228 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.353 | 0 | 827 | 150.7456 | 827 |  |  | 0.353 | 291.9291 | 0.063969 | 0.074071 |  |  |  |  | 14 | 0.006787
48722 | LEG_2___2 | 2 | North | YES | 0.18228 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.353 | 0 | 819 | 149.2873 | 819 |  |  | 0.353 | 289.1052 | 0.083412 | 0.095734 |  |  |  |  | 15 | 0.0073223
3381 | BBRN_1G | 1 | North | YES | 0.16547 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.33618 | 0 | 618 | 102.258 | 618 |  |  | 0.33618 | 207.7616 | 0.098084 | 0.1113 |  |  |  |  | 16 | 0.00786
3382 | BBRN_2G | 2 | North | YES | 0.16547 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.33618 | 0 | 589 | 97.4595 | 589 |  |  | 0.33618 | 198.0122 | 0.11207 | 0.12614 |  |  |  |  | 17 | 0.010102
13131 | CALFREST_1G | 1 | North | YES | 0.16409 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.33481 | 150.7 | 150.7 | 24.7288 | 150.7 |  |  | 0.33481 | 50.456 | 0.11564 | 0.12992 |  |  |  |  | 18 | 0.012322
13132 | CALFREST_2G | 2 | North | YES | 0.16409 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.33481 | 151 | 151 | 24.778 | 151 |  |  | 0.33481 | 50.5564 | 0.11923 | 0.13371 |  |  |  |  | 19 | 0.013219
13133 | CALFREST_3G | 3 | North | YES | 0.16409 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.33481 | 177.4 | 177.4 | 29.1101 | 177.4 |  |  | 0.33481 | 59.3954 | 0.12344 | 0.13816 |  |  |  |  | 20 | 0.014073
13134 | CALFREST_4G | 4 | North | YES | 0.1638 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.33452 | 151.5 | 151.5 | 24.8163 | 151.5 |  |  | 0.33452 | 50.68 | 0.12704 | 0.14196 |  |  |  |  | 21 | 0.014277
13135 | CALFREST_5G | 5 | North | YES | 0.1638 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.33452 | 152.3 | 152.3 | 24.9473 | 152.3 |  |  | 0.33452 | 50.9477 | 0.13065 | 0.14578 |  |  |  |  | 22 | 0.01448
13136 | CALFREST_6G | 6 | North | YES | 0.1638 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.33452 | 177.5 | 177.5 | 29.0752 | 177.5 |  |  | 0.33452 | 59.3776 | 0.13487 | 0.15023 |  |  |  |  | 23 | 0.014719
3107 | STRYKER_1G | 1 | North | YES | 0.15784 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.32856 | 182 | 182 | 28.7272 | 182 |  |  | 0.32856 | 59.7979 | 0.13919 | 0.15471 |  |  |  |  | 24 | 0.01492
3108 | STRYKER_2G | 2 | North | YES | 0.15784 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.32856 | 484 | 484 | 76.3955 | 484 |  |  | 0.32856 | 159.0229 | 0.15068 | 0.16662 |  |  |  |  | 25 | 0.015122
3309 | ASPN_G | 1 | North | YES | 0.15775 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.32847 | 50 | 50 | 7.8874 | 50 |  |  | 0.32847 | 16.4233 | 0.15187 | 0.16785 |  |  |  |  | 26 | 0.015358
3348 | CHAMPION_1G | MB | North | YES | 0.15768 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.3284 | 0 | 0 | 0 | 0 |  |  | 0.3284 | 0 | 0.15187 | 0.16785 |  |  |  |  | 27 | 0.015518
13116 | TGATEWAY_1G | 1 | North | YES | 0.15714 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.32786 | 151 | 151 | 23.7278 | 151 |  |  | 0.32786 | 49.5062 | 0.15545 | 0.17156 |  |  |  |  | 28 | 0.015944
13117 | TGATEWAY_2G | 2 | North | YES | 0.15714 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.32786 | 130 | 130 | 20.4279 | 130 |  |  | 0.32786 | 42.6212 | 0.15854 | 0.17476 |  |  |  |  | 29 | 0.015987
13118 | TGATEWAY_3G | 3 | North | YES | 0.15714 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.32786 | 148 | 148 | 23.2564 | 148 |  |  | 0.32786 | 48.5227 | 0.16205 | 0.17839 |  |  |  |  | 30 | 0.015987
13119 | TGATEWAY_4G | 4 | North | YES | 0.15714 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.32786 | 399 | 399 | 62.6981 | 399 |  |  | 0.32786 | 130.8144 | 0.17152 | 0.18819 |  |  |  |  | 31 | 0.016112
3097 | MARTLAKE_1G | 1 | North | YES | 0.15654 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 790 | 123.6634 | 790 |  |  | 0.32725 | 258.5305 | 0.19028 | 0.20757 |  |  |  |  | 32 | 0.01622
3098 | MARTLAKE_2G | 2 | North | YES | 0.15654 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 795 | 124.4461 | 795 |  |  | 0.32725 | 260.1667 | 0.20915 | 0.22706 |  |  |  |  | 33 | 0.016342
3099 | MARTLAKE_3G | 3 | North | YES | 0.15654 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 804 | 125.8549 | 804 |  |  | 0.32725 | 263.112 | 0.22824 | 0.24678 |  |  |  |  | 34 | 0.016672
3126 | TRINIDAD_6G | 1 | North | YES | 0.15258 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.3233 | 224 | 224 | 34.1784 | 224 |  |  | 0.3233 | 72.4191 | 0.23356 | 0.25221 |  |  |  |  | 35 | 0.017289
12411 | FPLEFR1A_G | 1 | North | YES | 0.15233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32305 | 161 | 161 | 24.5248 | 161 |  |  | 0.32305 | 52.0104 | 0.23738 | 0.2561 |  |  |  |  | 36 | 0.017911
12412 | FPLEFR1B_G | 2 | North | YES | 0.15233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32305 | 164 | 164 | 24.9818 | 164 |  |  | 0.32305 | 52.9795 | 0.24127 | 0.26007 |  |  |  |  | 37 | 0.01854
12413 | FPLEFR1C_G | 3 | North | YES | 0.15233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32305 | 164 | 164 | 24.9818 | 164 |  |  | 0.32305 | 52.9795 | 0.24517 | 0.26404 |  |  |  |  | 38 | 0.018648
12414 | FPLEFR1S_G | 4 | North | YES | 0.15233 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.32305 | 414 | 414 | 63.0638 | 414 |  |  | 0.32305 | 133.7409 | 0.25499 | 0.27406 |  |  |  |  | 39 | 0.018723
12421 | FPLEFR2A_G | 1 | North | YES | 0.15233 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.32305 | 162 | 162 | 24.6771 | 162 |  |  | 0.32305 | 52.3334 | 0.25884 | 0.27799 |  |  |  |  | 40 | 0.0188
12422 | FPLEFR2B_G | 2 | North | YES | 0.15233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32305 | 161 | 161 | 24.5248 | 161 |  |  | 0.32305 | 52.0104 | 0.26266 | 0.28188 |  |  |  |  | 41 | 0.018876
12423 | FPLEFR2C_G | 3 | North | YES | 0.15233 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.32305 | 163 | 163 | 24.8295 | 163 |  |  | 0.32305 | 52.6565 | 0.26653 | 0.28583 |  |  |  |  | 42 | 0.019069
12424 | FPLEFR2S_G | 4 | North | YES | 0.15233 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.32305 | 415 | 415 | 63.2161 | 415 |  |  | 0.32305 | 134.064 | 0.27638 | 0.29587 |  |  |  |  | 43 | 0.019145
2451 | LKHB1_G | 1 | North | YES | 0.15155 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.32227 | 391 | 391 | 59.2564 | 391 |  |  | 0.32227 | 126.0071 | 0.28567 | 0.30532 |  |  |  |  | 44 | 0.01922
2452 | LKHB2_G | 2 | North | YES | 0.15155 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.32227 | 516 | 516 | 78.2003 | 516 |  |  | 0.32227 | 166.2907 | 0.29792 | 0.31778 |  |  |  |  | 45 | 0.019296
12440 | PARKD_1SVC8 | 1 | North | YES | 0.15148 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.3222 | 0 | 0 | 0 | 0 |  |  | 0.3222 | 0 | 0.29792 | 0.31778 |  |  |  |  | 46 | 0.01949
12449 | PARKD_2SVC8 | 1 | North | YES | 0.15148 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.3222 | 0 | 0 | 0 | 0 |  |  | 0.3222 | 0 | 0.29792 | 0.31778 |  |  |  |  | 47 | 0.019649
948 | STEAM1 | 1 | North | YES | 0.15111 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.32183 | 20 | 20 | 3.0222 | 20 |  |  | 0.32183 | 6.4365 | 0.29839 | 0.31826 |  |  |  |  | 48 | 0.01986
949 | STEAM2 | 1 | North | YES | 0.15111 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.32182 | 26 | 26 | 3.9288 | 26 |  |  | 0.32182 | 8.3674 | 0.29901 | 0.31889 |  |  |  |  | 49 | 0.01986
950 | STEAM3 | 1 | North | YES | 0.15111 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.32182 | 42 | 42 | 6.3465 | 42 |  |  | 0.32182 | 13.5166 | 0.30001 | 0.3199 |  |  |  |  | 50 | 0.01986
837 | NEWMAN_G5 | 1 | North | YES | 0.15093 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.32165 | 40 | 40 | 6.0372 | 40 |  |  | 0.32165 | 12.8659 | 0.30096 | 0.32086 |  |  |  |  | 51 | 0.019868
842 | OLINGER_G1 | 1 | North | YES | 0.15091 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.32162 | 79 | 79 | 11.9216 | 79 |  |  | 0.32162 | 25.4083 | 0.30283 | 0.32277 |  |  |  |  | 52 | 0.019877
843 | OLINGER_G2 | 1 | North | YES | 0.15091 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.32162 | 110 | 110 | 16.5997 | 110 |  |  | 0.32162 | 35.3786 | 0.30544 | 0.32542 |  |  |  |  | 53 | 0.019893
844 | OLINGER_G3 | 1 | North | YES | 0.15091 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.32162 | 150 | 150 | 22.6359 | 150 |  |  | 0.32162 | 48.2436 | 0.309 | 0.32903 |  |  |  |  | 54 | 0.019908
845 | OLINGER_G4 | 1 | North | YES | 0.15091 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.32162 | 76 | 76 | 11.4689 | 76 |  |  | 0.32162 | 24.4434 | 0.31081 | 0.33087 |  |  |  |  | 55 | 0.019936
1701 | MOSES_1G | 1 | North | YES | 0.15062 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 558 | 84.0437 | 558 |  |  | 0.32133 | 179.3042 | 0.32406 | 0.3443 |  |  |  |  | 56 | 0.019976
1702 | MOSES_2G | 2 | North | YES | 0.15062 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 579 | 87.2067 | 579 |  |  | 0.32133 | 186.0522 | 0.3378 | 0.35824 |  |  |  |  | 57 | 0.02003
1703 | MOSES_3G | 3 | North | YES | 0.15062 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 808 | 121.6977 | 808 |  |  | 0.32133 | 259.6377 | 0.35698 | 0.3777 |  |  |  |  | 58 | 0.020057
5925 | DCEAST | EQ | North | YES | 0.15062 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.32133 | 0 | 0 | 0 | 0 |  |  | 0.32133 | 0 | 0.35698 | 0.3777 |  |  |  |  | 59 | 0.020246
1675 | PEC_1G | 1 | North | YES | 0.15046 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0 | 0.35698 | 0.3777 |  |  |  |  | 60 | 0.020441
1676 | PEC_2G | 2 | North | YES | 0.15046 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0 | 0.35698 | 0.3777 |  |  |  |  | 61 | 0.020715
1677 | PEC_3G | 3 | North | YES | 0.15046 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0 | 0.35698 | 0.3777 |  |  |  |  | 62 | 0.020715
1678 | LAMARPWR_1G | 1 | North | YES | 0.15037 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.32109 | 160 | 160 | 24.0592 | 160 |  |  | 0.32109 | 51.374 | 0.36078 | 0.38155 |  |  |  |  | 63 | 0.020715
1679 | LAMARPWR_2G | 2 | North | YES | 0.15037 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32109 | 156 | 156 | 23.4577 | 156 |  |  | 0.32109 | 50.0897 | 0.36449 | 0.3853 |  |  |  |  | 64 | 0.020715
1680 | LAMARPWR_3G | 3 | North | YES | 0.15037 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.32109 | 196 | 196 | 29.4725 | 196 |  |  | 0.32109 | 62.9332 | 0.36914 | 0.39002 |  |  |  |  | 65 | 0.020715
1681 | LAMARPWR_4G | 4 | North | YES | 0.15037 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32109 | 156 | 156 | 23.4577 | 156 |  |  | 0.32109 | 50.0897 | 0.37284 | 0.39377 |  |  |  |  | 66 | 0.020766
1682 | LAMARPWR_5G | 5 | North | YES | 0.15037 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.32109 | 157 | 157 | 23.6081 | 157 |  |  | 0.32109 | 50.4108 | 0.37657 | 0.39755 |  |  |  |  | 67 | 0.020816
1683 | LAMARPWR_6G | 6 | North | YES | 0.15037 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.32109 | 198 | 198 | 29.7733 | 198 |  |  | 0.32109 | 63.5754 | 0.38127 | 0.40231 |  |  |  |  | 68 | 0.020878
1689 | VALLEY_3G | 3 | North | YES | 0.15023 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.32095 | 375 | 375 | 56.337 | 375 |  |  | 0.32095 | 120.3562 | 0.39017 | 0.41133 |  |  |  |  | 69 | 0.020928
11691 | KMICHICT1_G | 1 | North | YES | 0.15023 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32095 | 144 | 144 | 21.6334 | 144 |  |  | 0.32095 | 46.2168 | 0.39359 | 0.41479 |  |  |  |  | 70 | 0.020978
11692 | KMICHICT2_G | 2 | North | YES | 0.15023 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.32095 | 146 | 146 | 21.9339 | 146 |  |  | 0.32095 | 46.8587 | 0.39706 | 0.41831 |  |  |  |  | 71 | 0.021042
11693 | KMICHIST3_G | 3 | North | YES | 0.15023 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.32095 | 312 | 312 | 46.8724 | 312 |  |  | 0.32095 | 100.1363 | 0.40446 | 0.42581 |  |  |  |  | 72 | 0.021158
11694 | KMICHICT4_G | 4 | North | YES | 0.15023 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32095 | 144 | 144 | 21.6334 | 144 |  |  | 0.32095 | 46.2168 | 0.40788 | 0.42927 |  |  |  |  | 73 | 0.021202
11695 | KMICHICT5_G | 5 | North | YES | 0.15023 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.32095 | 148 | 148 | 22.2343 | 148 |  |  | 0.32095 | 47.5006 | 0.4114 | 0.43283 |  |  |  |  | 74 | 0.021247
11696 | KMICHIST6_G | 6 | North | YES | 0.15023 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.32095 | 310 | 310 | 46.5719 | 310 |  |  | 0.32095 | 99.4944 | 0.41876 | 0.44029 |  |  |  |  | 75 | 0.021344
1687 | VALLEY_1G | 1 | North | YES | 0.14992 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.32064 | 170 | 170 | 25.4866 | 170 |  |  | 0.32064 | 54.5086 | 0.42279 | 0.44437 |  |  |  |  | 76 | 0.021389
1688 | VALLEY_2G | 2 | North | YES | 0.14992 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.32064 | 527 | 527 | 79.0084 | 527 |  |  | 0.32064 | 168.9766 | 0.4353 | 0.45703 |  |  |  |  | 77 | 0.021434
2413 | MTCK6_G | 6 | North | YES | 0.14991 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.32062 | 118 | 118 | 17.6889 | 118 |  |  | 0.32062 | 37.8336 | 0.4381 | 0.45987 |  |  |  |  | 78 | 0.02153
2414 | MTCK7_G | 7 | North | YES | 0.14991 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.32062 | 115 | 115 | 17.2392 | 115 |  |  | 0.32062 | 36.8717 | 0.44084 | 0.46263 |  |  |  |  | 79 | 0.021579
2417 | MTCK8_G | 8 | North | YES | 0.14991 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.32062 | 556 | 556 | 83.3477 | 556 |  |  | 0.32062 | 178.2668 | 0.45403 | 0.47599 |  |  |  |  | 80 | 0.02173
6948 | DENISNDM | 1 | North | YES | 0.14967 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.32039 | 0 | 0 | 0 | 0 |  |  | 0.32039 | 0 | 0.45403 | 0.47599 |  |  |  |  | 81 | 0.021763
6948 | DENISNDM | 2 | North | YES | 0.14967 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.32039 | 0 | 0 | 0 | 0 |  |  | 0.32039 | 0 | 0.45403 | 0.47599 |  |  |  |  | 82 | 0.021796
2371 | COLLIN_1G | MB | North | YES | 0.14891 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.31963 | 0 | 0 | 0 | 0 |  |  | 0.31963 | 0 | 0.45403 | 0.47599 |  |  |  |  | 83 | 0.021955
2381 | NTHLK1_G | 1 | North | YES | 0.14864 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.31936 | 156 | 156 | 23.188 | 156 |  |  | 0.31936 | 49.82 | 0.45774 | 0.47972 |  |  |  |  | 84 | 0.021955
2382 | NTHLK2_G | 2 | North | YES | 0.14864 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.31936 | 181 | 181 | 26.904 | 181 |  |  | 0.31936 | 57.8039 | 0.46204 | 0.48405 |  |  |  |  | 85 | 0.021955
2383 | NTHLK3_G | 3 | North | YES | 0.14864 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.31936 | 329 | 329 | 48.9029 | 329 |  |  | 0.31936 | 105.069 | 0.46985 | 0.49193 |  |  |  |  | 86 | 0.021955
12322 | ENNSTRAC_1G | 1 | North | YES | 0.14859 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.31931 | 196 | 196 | 29.1232 | 196 |  |  | 0.31931 | 62.5839 | 0.4745 | 0.49662 |  |  |  |  | 87 | 0.021984
12323 | ENNSTRAC_2G | 2 | North | YES | 0.14859 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.31931 | 116 | 116 | 17.2362 | 116 |  |  | 0.31931 | 37.0395 | 0.47725 | 0.49939 |  |  |  |  | 88 | 0.022019
923 | SPENCER_G4 | 1 | North | YES | 0.14605 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.31677 | 61 | 61 | 8.9092 | 61 |  |  | 0.31677 | 19.323 | 0.4787 | 0.50084 |  |  |  |  | 89 | 0.022081
924 | SPENCER_G5 | 1 | North | YES | 0.14605 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.31677 | 66 | 66 | 9.6395 | 66 |  |  | 0.31677 | 20.9069 | 0.48027 | 0.50241 |  |  |  |  | 90 | 0.022118
1948 | HANDLEY_4G | 4 | North | YES | 0.14497 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31568 | 435 | 435 | 63.0606 | 435 |  |  | 0.31568 | 137.3229 | 0.4906 | 0.5127 |  |  |  |  | 91 | 0.022139
1947 | HANDLEY_3G | 3 | North | YES | 0.14472 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.31543 | 395 | 395 | 57.1624 | 395 |  |  | 0.31543 | 124.5959 | 0.49997 | 0.52203 |  |  |  |  | 92 | 0.022139
1949 | HANDLEY_5G | 5 | North | YES | 0.14472 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31543 | 435 | 435 | 62.951 | 435 |  |  | 0.31543 | 137.2132 | 0.5103 | 0.53232 |  |  |  |  | 93 | 0.022139
1941 | MDLTHELP_1G | 1 | North | YES | 0.14469 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.31541 | 216.4 | 216.4 | 31.3113 | 216.4 |  |  | 0.31541 | 68.2547 | 0.51544 | 0.53743 |  |  |  |  | 94 | 0.022102
1942 | MDLTHELP_2G | 2 | North | YES | 0.14469 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.31541 | 216.1 | 216.1 | 31.2679 | 216.1 |  |  | 0.31541 | 68.16 | 0.52057 | 0.54254 |  |  |  |  | 95 | 0.022061
728 | WOLFRIDGE801 | 1 | North | YES | 0.14468 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.3154 | 0 | 112.5 | 16.2764 | 112.5 |  |  | 0.3154 | 35.4821 | 0.52324 | 0.5452 |  |  |  |  | 96 | 0.022015
1861 | EAGLEMNT_1G | MB | North | YES | 0.1441 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0 | 0.52324 | 0.5452 |  |  |  |  | 97 | 0.021993
1862 | EAGLEMNT_2G | MB | North | YES | 0.1441 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0 | 0.52324 | 0.5452 |  |  |  |  | 98 | 0.02197
1863 | EAGLEMNT_3G | MB | North | YES | 0.1441 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0 | 0.52324 | 0.5452 |  |  |  |  | 99 | 0.021958
1937 | MDLTHELP_5G | 5 | North | YES | 0.14319 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.31391 | 224 | 224 | 32.0757 | 224 |  |  | 0.31391 | 70.3165 | 0.52856 | 0.55047 |  |  |  |  | 100 | 0.021958
1938 | MDLTHELP_6G | 6 | North | YES | 0.14319 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.31391 | 226 | 226 | 32.3621 | 226 |  |  | 0.31391 | 70.9443 | 0.53392 | 0.55578 |  |  |  |  | 101 | 0.021958
1943 | MDLTHELP_3G | 3 | North | YES | 0.14319 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.31391 | 212 | 212 | 30.3573 | 212 |  |  | 0.31391 | 66.5495 | 0.53895 | 0.56077 |  |  |  |  | 102 | 0.021958
1944 | MDLTHELP_4G | 4 | North | YES | 0.14319 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.31391 | 211 | 211 | 30.2141 | 211 |  |  | 0.31391 | 66.2356 | 0.54396 | 0.56573 |  |  |  |  | 103 | 0.021909
580 | JCKCNTY801 | 1 | North | YES | 0.14264 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.31336 | 288 | 288 | 41.0797 | 288 |  |  | 0.31336 | 90.2465 | 0.5508 | 0.57249 |  |  |  |  | 104 | 0.02186
581 | JCKCNTY802 | 2 | North | YES | 0.14264 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.31336 | 147 | 147 | 20.9678 | 147 |  |  | 0.31336 | 46.0633 | 0.55429 | 0.57595 |  |  |  |  | 105 | 0.021814
582 | JCKCNTY803 | 3 | North | YES | 0.14264 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.31336 | 147 | 147 | 20.9678 | 147 |  |  | 0.31336 | 46.0633 | 0.55778 | 0.5794 |  |  |  |  | 106 | 0.021768
1889 | DECRDOVA_1G | 1 | North | YES | 0.14217 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.31289 | 779 | 779 | 110.7543 | 779 |  |  | 0.31289 | 243.7434 | 0.57627 | 0.59766 |  |  |  |  | 107 | 0.021693
1877 | WLFHOLW_1G | 1 | North | YES | 0.1419 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.31262 | 217.3 | 217.3 | 30.8344 | 217.3 |  |  | 0.31262 | 67.9314 | 0.58143 | 0.60275 |  |  |  |  | 108 | 0.021655
1878 | WLFHOLW_2G | 2 | North | YES | 0.1419 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.31262 | 215.7 | 215.7 | 30.6074 | 215.7 |  |  | 0.31262 | 67.4312 | 0.58655 | 0.60781 |  |  |  |  | 109 | 0.021616
1879 | WLFHOLW_3G | 3 | North | YES | 0.1419 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.31262 | 272.4 | 272.4 | 38.653 | 272.4 |  |  | 0.31262 | 85.1565 | 0.59302 | 0.61419 |  |  |  |  | 110 | 0.021387
1453 | WCPWRCO_1G | 1 | North | YES | 0.1417 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.31242 | 204 | 204 | 28.9074 | 204 |  |  | 0.31242 | 63.7338 | 0.59786 | 0.61896 |  |  |  |  | 111 | 0.021319
1454 | WCPWRCO_2G | 2 | North | YES | 0.1417 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.31242 | 204 | 204 | 28.9074 | 204 |  |  | 0.31242 | 63.7338 | 0.60271 | 0.62374 |  |  |  |  | 112 | 0.021251
1455 | WCPWRCO_3G | 3 | North | YES | 0.1417 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.31242 | 242 | 242 | 34.2921 | 242 |  |  | 0.31242 | 75.6058 | 0.60845 | 0.6294 |  |  |  |  | 113 | 0.021165
1898 | COMCHEPK_1G | 1 | North | YES | 0.14151 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.31222 | 0 | 0 | 0 | 0 |  |  | 0.31222 | 0 | 0.60845 | 0.6294 |  |  |  |  | 114 | 0.021098
1899 | COMCHEPK_2G | 2 | North | YES | 0.14151 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.31222 | 0 | 0 | 0 | 0 |  |  | 0.31222 | 0 | 0.60845 | 0.6294 |  |  |  |  | 115 | 0.02103
503 | NTHTEXAS01 | 1 | North | YES | 0.14081 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.31153 | 18 | 18 | 2.5346 | 18 |  |  | 0.31153 | 5.6075 | 0.60888 | 0.62982 |  |  |  |  | 116 | 0.020951
504 | NTHTEXAS02 | 2 | North | YES | 0.14081 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.31153 | 18 | 18 | 2.5346 | 18 |  |  | 0.31153 | 5.6075 | 0.60931 | 0.63024 |  |  |  |  | 117 | 0.020951
505 | NTHTEXAS03 | 3 | North | YES | 0.14081 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.31153 | 38 | 38 | 5.3508 | 38 |  |  | 0.31153 | 11.8381 | 0.61021 | 0.63113 |  |  |  |  | 118 | 0.020951
1892 | DECRDOVA_2G | A | North | YES | 0.14077 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.31149 | 70 | 70 | 9.8542 | 70 |  |  | 0.31149 | 21.8044 | 0.61187 | 0.63276 |  |  |  |  | 119 | 0.020943
1893 | DECRDOVA_3G | B | North | YES | 0.14077 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.31149 | 69 | 69 | 9.7134 | 69 |  |  | 0.31149 | 21.4929 | 0.61351 | 0.63438 |  |  |  |  | 120 | 0.020936
1894 | DECRDOVA_4G | C | North | YES | 0.14077 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.31149 | 69 | 69 | 9.7134 | 69 |  |  | 0.31149 | 21.4929 | 0.61515 | 0.63599 |  |  |  |  | 121 | 0.020921
1895 | DECRDOVA_5G | D | North | YES | 0.14077 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.31149 | 68 | 68 | 9.5726 | 68 |  |  | 0.31149 | 21.1814 | 0.61676 | 0.63757 |  |  |  |  | 122 | 0.020893
366 | JNSNCNTY802 | 1 | North | YES | 0.13991 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.31062 | 0 | 0 | 0 | 0 |  |  | 0.31062 | 0 | 0.61676 | 0.63757 |  |  |  |  | 123 | 0.020866
367 | JNSNCNTY802 | 2 | North | YES | 0.13991 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.31062 | 0 | 0 | 0 | 0 |  |  | 0.31062 | 0 | 0.61676 | 0.63757 |  |  |  |  | 124 | 0.020838
344 | MRSSHPRD | 1 | North | YES | 0.13949 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0 | 0.61676 | 0.63757 |  |  |  |  | 125 | 0.020811
345 | MRSSHPRD01 | 2 | North | YES | 0.13949 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0 | 0.61676 | 0.63757 |  |  |  |  | 126 | 0.020811
1600 | BARTNWND_1G | 1 | North | YES | 0.13929 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.31 | 0 | 120 | 16.7143 | 120 |  |  | 0.31 | 37.2004 | 0.61961 | 0.64036 |  |  |  |  | 127 | 0.020811
1479 | WFCOGEN_1G | 1 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0 | 0.61961 | 0.64036 |  |  |  |  | 128 | 0.020811
1479 | WFCOGEN_1G | 2 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0 | 0.61961 | 0.64036 |  |  |  |  | 129 | 0.020811
1482 | WFCOGEN_2G | 1 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0 | 0.61961 | 0.64036 |  |  |  |  | 130 | 0.02075
1482 | WFCOGEN_2G | 2 | North | YES | 0.13909 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0 | 0.61961 | 0.64036 |  |  |  |  | 131 | 0.02075
1432 | GRHAMSES_2G | 2 | North | YES | 0.13897 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.30969 | 366 | 366 | 50.8648 | 366 |  |  | 0.30969 | 113.3475 | 0.6283 | 0.64885 |  |  |  |  | 132 | 0.02075
332 | RWMILLER01 | 1 | North | YES | 0.13825 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.30897 | 73 | 73 | 10.0923 | 73 |  |  | 0.30897 | 22.5547 | 0.63003 | 0.65054 |  |  |  |  | 133 | 0.02075
333 | RWMILLER02 | 2 | North | YES | 0.13825 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.30897 | 119 | 119 | 16.4519 | 119 |  |  | 0.30897 | 36.7673 | 0.63286 | 0.6533 |  |  |  |  | 134 | 0.02075
334 | RWMILLER03 | 3 | North | YES | 0.13825 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.30897 | 208 | 208 | 28.7562 | 208 |  |  | 0.30897 | 64.2655 | 0.6378 | 0.65811 |  |  |  |  | 135 | 0.020554
335 | RWMILLER04 | 4 | North | YES | 0.13825 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.30897 | 102 | 102 | 14.1016 | 102 |  |  | 0.30897 | 31.5148 | 0.64022 | 0.66048 |  |  |  |  | 136 | 0.020511
336 | RWMILLER05 | 5 | North | YES | 0.13825 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.30897 | 101 | 101 | 13.9634 | 101 |  |  | 0.30897 | 31.2058 | 0.64262 | 0.66281 |  |  |  |  | 137 | 0.020441
1433 | GRHAMSES_1G | 1 | North | YES | 0.13817 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.30889 | 242 | 242 | 33.4381 | 242 |  |  | 0.30889 | 74.7518 | 0.64836 | 0.66842 |  |  |  |  | 138 | 0.020319
6100 | OKLA7A | EQ | West | YES | 0.13689 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.30761 | 0 | 0 |  |  |  |  | 0.30761 | 0 | 0.64836 | 0.66842 |  |  |  |  | 139 | 0.020259
6752 | OKLA0A | 1 | West | YES | 0.13689 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.30761 | 0 | 649.7 |  |  |  |  | 0.30761 | 199.8541 | 0.66378 | 0.68339 |  |  |  |  | 140 | 0.020199
1442 | COKFIELD_5 | 1 | North | YES | 0.13619 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.30691 | 0 | 165 | 22.4714 | 165 |  |  | 0.30691 | 50.6398 | 0.6677 | 0.68719 |  |  |  |  | 141 | 0.020056
1438 | MESQUITW_2G | 1 | North | YES | 0.13531 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.30603 | 0 | 236 | 31.9334 | 236 |  |  | 0.30603 | 72.2228 | 0.6733 | 0.6926 |  |  |  |  | 142 | 0.020056
1437 | MESQUITW_1G | 1 | North | YES | 0.13531 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.30602 | 0 | 400 | 54.1224 | 400 |  |  | 0.30602 | 122.4095 | 0.6828 | 0.70177 |  |  |  |  | 143 | 0.019607
60081 | WHRLWIND1A | 1 | West | YES | 0.13362 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.30433 | 0 | 60 |  |  |  |  | 0.30433 | 18.2601 | 0.68423 | 0.70314 |  |  |  |  | 144 | 0.019485
1416 | SWETWATR_1G | 1 | West | YES | 0.13308 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.3038 | 30 | 30 |  |  |  |  | 0.3038 | 9.114 | 0.68494 | 0.70382 |  |  |  |  | 145 | 0.019294
1417 | SWETWATR_2G | 2 | West | YES | 0.13308 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.3038 | 72 | 72 |  |  |  |  | 0.3038 | 21.8735 | 0.68665 | 0.70546 |  |  |  |  | 146 | 0.01897
1418 | SWETWATR_3G | 3 | West | YES | 0.13308 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.3038 | 68 | 68 |  |  |  |  | 0.3038 | 20.6583 | 0.68826 | 0.70701 |  |  |  |  | 147 | 0.018914
1419 | SWETWATR_4G | 4 | West | YES | 0.13308 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.3038 | 61 | 61 |  |  |  |  | 0.3038 | 18.5317 | 0.68971 | 0.7084 |  |  |  |  | 148 | 0.018885
1643 | SLSTR1PP_1G | 1 | North | YES | 0.13291 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.30363 | 0 | 60 | 7.9747 | 60 |  |  | 0.30363 | 18.2177 | 0.69113 | 0.70976 |  |  |  |  | 149 | 0.018815
11056 | ROSCOE_1G | 1 | West | YES | 0.1326 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.30332 | 0 | 209 |  |  |  |  | 0.30332 | 63.3938 | 0.6961 | 0.71451 |  |  |  |  | 150 | 0.018748
11057 | CHAMPION_1G | 1 | West | YES | 0.1326 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.30332 | 0 | 126.5 |  |  |  |  | 0.30332 | 38.3699 | 0.6991 | 0.71739 |  |  |  |  | 151 | 0.018689
11058 | PYRON_1G | 1 | West | YES | 0.1326 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.30332 | 0 | 249 |  |  |  |  | 0.30332 | 75.5266 | 0.70501 | 0.72305 |  |  |  |  | 152 | 0.018629
11059 | INADALE_1G | 1 | West | YES | 0.1326 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.30332 | 0 | 197 |  |  |  |  | 0.30332 | 59.754 | 0.70969 | 0.72753 |  |  |  |  | 153 | 0.018418
6144 | MCADOO1A | 1 | West | YES | 0.13257 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.30329 | 0 | 150 |  |  |  |  | 0.30329 | 45.4936 | 0.71325 | 0.73093 |  |  |  |  | 154 | 0.01829
71051 | L_BITTCR1_1N | W1 | West | YES | 0.13255 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 37.5 |  |  |  |  | 0.30327 | 11.3725 | 0.71414 | 0.73179 |  |  |  |  | 155 | 0.018038
71054 | L_SWEETW1_1N | W1 | West | YES | 0.13255 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 107.5 |  |  |  |  | 0.30327 | 32.6012 | 0.71669 | 0.73423 |  |  |  |  | 156 | 0.017839
71057 | L_SWEETW1_2N | W1 | West | YES | 0.13255 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 135 |  |  |  |  | 0.30327 | 40.941 | 0.7199 | 0.7373 |  |  |  |  | 157 | 0.017687
71059 | L_SWEETW1_3N | W1 | West | YES | 0.13255 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 119 |  |  |  |  | 0.30327 | 36.0887 | 0.72272 | 0.74 |  |  |  |  | 158 | 0.017649
71060 | L_SWEETW1_4N | W1 | West | YES | 0.13255 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 105 |  |  |  |  | 0.30327 | 31.843 | 0.72521 | 0.74239 |  |  |  |  | 159 | 0.017539
71061 | L_SWEETW1_5N | W1 | West | YES | 0.13255 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 80.5 |  |  |  |  | 0.30327 | 24.413 | 0.72712 | 0.74422 |  |  |  |  | 160 | 0.017402
6407 | TURKTRAK1A | 1 | West | YES | 0.13209 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.3028 | 0 | 169.5 |  |  |  |  | 0.3028 | 51.3254 | 0.73115 | 0.74806 |  |  |  |  | 161 | 0.017281
1343 | TRENTIPP_8 | 1 | West | YES | 0.13189 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.3026 | 0 | 150 |  |  |  |  | 0.3026 | 45.3907 | 0.73471 | 0.75146 |  |  |  |  | 162 | 0.017175
1354 | AEPWIND_8 | 1 | West | YES | 0.13189 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.3026 | 0 | 101 |  |  |  |  | 0.3026 | 30.5631 | 0.73711 | 0.75375 |  |  |  |  | 163 | 0.017093
36998 | RDCNYNG1 | 1 | West | YES | 0.13178 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.3025 | 0 | 84 |  |  |  |  | 0.3025 | 25.4101 | 0.7391 | 0.75566 |  |  |  |  | 164 | 0.016915
1061 | CIELOGEN_1G | 1 | West | YES | 0.1316 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.30232 | 0 | 99 |  |  |  |  | 0.30232 | 29.9298 | 0.74145 | 0.7579 |  |  |  |  | 165 | 0.016755
1062 | CIELOGEN_2G | 1 | West | YES | 0.1316 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.30232 | 0 | 61 |  |  |  |  | 0.30232 | 18.4416 | 0.7429 | 0.75928 |  |  |  |  | 166 | 0.016648
1069 | KINDERMG_1G | 1 | West | YES | 0.1316 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0 | 0.7429 | 0.75928 |  |  |  |  | 167 | 0.016557
1070 | KINDERMG_2G | 1 | West | YES | 0.1316 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0 | 0.7429 | 0.75928 |  |  |  |  | 168 | 0.01645
1071 | KINDERMG_3G | 1 | West | YES | 0.1316 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0 | 0.7429 | 0.75928 |  |  |  |  | 169 | 0.016384
1068 | SCURRYCW_1G | 1 | West | YES | 0.13159 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.30231 | 0 | 141 |  |  |  |  | 0.30231 | 42.6257 | 0.74625 | 0.76248 |  |  |  |  | 170 | 0.016384
1073 | SCURRYCW_2G | 2 | West | YES | 0.13159 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.30231 | 0 | 120 |  |  |  |  | 0.30231 | 36.2772 | 0.7491 | 0.7652 |  |  |  |  | 171 | 0.016384
6637 | SNYDERW1A | 1 | West | YES | 0.13152 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.30224 | 0 | 63 |  |  |  |  | 0.30224 | 19.0412 | 0.75059 | 0.76662 |  |  |  |  | 172 | 0.016384
1037 | MORGAN5G_5G | 5 | West | YES | 0.13148 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.3022 | 137 | 137 |  |  |  |  | 0.3022 | 41.4018 | 0.75384 | 0.76973 |  |  |  |  | 173 | 0.01623
1039 | MRGNAG_1G | A | West | YES | 0.13148 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.3022 | 69 | 69 |  |  |  |  | 0.3022 | 20.852 | 0.75548 | 0.77129 |  |  |  |  | 174 | 0.0161
1040 | MRGNBG_2G | B | West | YES | 0.13148 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.3022 | 71 | 71 |  |  |  |  | 0.3022 | 21.4564 | 0.75717 | 0.7729 |  |  |  |  | 175 | 0.016031
1041 | MRGNCG_3G | C | West | YES | 0.13148 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.3022 | 70 | 70 |  |  |  |  | 0.3022 | 21.1542 | 0.75883 | 0.77448 |  |  |  |  | 176 | 0.015881
1042 | MRGNDG_4G | D | West | YES | 0.13148 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.3022 | 68 | 68 |  |  |  |  | 0.3022 | 20.5498 | 0.76044 | 0.77602 |  |  |  |  | 177 | 0.015805
1043 | MRGNEG_5G | E | West | YES | 0.13148 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.3022 | 70 | 70 |  |  |  |  | 0.3022 | 21.1542 | 0.76211 | 0.77761 |  |  |  |  | 178 | 0.015728
1044 | MRGNFG_6G | F | West | YES | 0.13148 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.3022 | 66 | 66 |  |  |  |  | 0.3022 | 19.9454 | 0.76367 | 0.7791 |  |  |  |  | 179 | 0.015651
60058 | BUFF_GAP1A | 1 | West | YES | 0.13142 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30214 | 0 | 120 |  |  |  |  | 0.30214 | 36.257 | 0.76652 | 0.78182 |  |  |  |  | 180 | 0.015576
60060 | CIRELLO | 1 | West | YES | 0.13142 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.30214 | 0 | 233 |  |  |  |  | 0.30214 | 70.399 | 0.77205 | 0.78709 |  |  |  |  | 181 | 0.0155
60063 | BUFF_GAP1B | 1 | West | YES | 0.13142 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.30214 | 0 | 170.2 |  |  |  |  | 0.30214 | 51.4245 | 0.77609 | 0.79095 |  |  |  |  | 182 | 0.015427
60066 | H_HOLLOW1A | 1 | West | YES | 0.13142 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.30214 | 0 | 222 |  |  |  |  | 0.30214 | 67.0755 | 0.78136 | 0.79597 |  |  |  |  | 183 | 0.015295
60068 | HHOLLOW21A | 1 | West | YES | 0.13142 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 184 |  |  |  |  | 0.30214 | 55.5941 | 0.78573 | 0.80014 |  |  |  |  | 184 | 0.015039
60070 | HHOLLOW31A | 1 | West | YES | 0.13142 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 224 |  |  |  |  | 0.30214 | 67.6798 | 0.79105 | 0.80521 |  |  |  |  | 185 | 0.014852
60072 | HHOLLOW41A | 1 | West | YES | 0.13142 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 115 |  |  |  |  | 0.30214 | 34.7463 | 0.79378 | 0.80781 |  |  |  |  | 186 | 0.014608
1058 | LONGSHORE_5 | 1 | West | YES | 0.13136 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.30208 | 0 | 150 |  |  |  |  | 0.30208 | 45.312 | 0.79734 | 0.81121 |  |  |  |  | 187 | 0.014405
1058 | LONGSHORE_5 | 2 | West | YES | 0.13136 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.30208 | 0 | 220 |  |  |  |  | 0.30208 | 66.4575 | 0.80256 | 0.81619 |  |  |  |  | 188 | 0.014159
11065 | ELBOWCK_1G | 1 | West | YES | 0.13136 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.30208 | 0 | 121.9 |  |  |  |  | 0.30208 | 36.8235 | 0.80546 | 0.81895 |  |  |  |  | 189 | 0.014032
1045 | CALENG1G_1G | 1 | West | YES | 0.13116 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0 | 0.80546 | 0.81895 |  |  |  |  | 190 | 0.013867
1046 | CALENG2G_2G | 2 | West | YES | 0.13116 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0 | 0.80546 | 0.81895 |  |  |  |  | 191 | 0.013624
1047 | CALENG3G_3G | 3 | West | YES | 0.13116 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0 | 0.80546 | 0.81895 |  |  |  |  | 192 | 0.013489
11309 | BULLCREK_2G | 1 | West | YES | 0.13114 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.30186 | 0 | 180 |  |  |  |  | 0.30186 | 54.3348 | 0.80973 | 0.82302 |  |  |  |  | 193 | 0.013489
11310 | BULLCREK_1G | 1 | West | YES | 0.13114 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.30186 | 0 | 180 |  |  |  |  | 0.30186 | 54.3348 | 0.814 | 0.82709 |  |  |  |  | 194 | 0.013489
11320 | COYOTE_1G | 1 | West | YES | 0.13107 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.30179 | 0 | 225 |  |  |  |  | 0.30179 | 67.9034 | 0.81935 | 0.83218 |  |  |  |  | 195 | 0.013489
1360 | GUNSIGHT_8 | 1 | West | YES | 0.1308 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.30152 | 0 | 120 |  |  |  |  | 0.30152 | 36.1819 | 0.8222 | 0.83489 |  |  |  |  | 196 | 0.013287
1327 | WILDHRSE_1G | 1 | West | YES | 0.13076 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.30148 | 0 | 120 |  |  |  |  | 0.30148 | 36.1774 | 0.82504 | 0.8376 |  |  |  |  | 197 | 0.013086
1333 | MCDDONAL_8 | 1 | West | YES | 0.13054 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.30126 | 0 | 214.2 |  |  |  |  | 0.30126 | 64.5292 | 0.83013 | 0.84244 |  |  |  |  | 198 | 0.012832
1328 | OCOTILLO_1G | 1 | West | YES | 0.13036 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.30107 | 0 | 58 |  |  |  |  | 0.30107 | 17.4623 | 0.83151 | 0.84374 |  |  |  |  | 199 | 0.012695
11001 | NAV1CT | 1 | West | YES | 0.13029 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.30101 | 70.4 | 70.4 |  |  |  |  | 0.30101 | 21.1912 | 0.83318 | 0.84533 |  |  |  |  | 200 | 0.012557
11009 | NAV2CT | 1 | West | YES | 0.13029 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.30101 | 71.4 | 71.4 |  |  |  |  | 0.30101 | 21.4922 | 0.83487 | 0.84694 |  |  |  |  | 201 | 0.012307
11011 | NAV3ST | 1 | West | YES | 0.13029 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.30101 | 92.8 | 92.8 |  |  |  |  | 0.30101 | 27.9339 | 0.83708 | 0.84904 |  |  |  |  | 202 | 0.012238
11012 | NAV4CT | 1 | West | YES | 0.13029 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30101 | 80 | 80 |  |  |  |  | 0.30101 | 24.0809 | 0.83898 | 0.85084 |  |  |  |  | 203 | 0.012155
11013 | NAV5CT | 1 | West | YES | 0.13029 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30101 | 80 | 80 |  |  |  |  | 0.30101 | 24.0809 | 0.84087 | 0.85265 |  |  |  |  | 204 | 0.01207
11014 | NAV6ST | 1 | West | YES | 0.13029 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.30101 | 115 | 115 |  |  |  |  | 0.30101 | 34.6164 | 0.8436 | 0.85524 |  |  |  |  | 205 | 0.01196
11020 | TIEHVSG_1G | 1 | West | YES | 0.13028 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.301 | 208.2 | 208.2 |  |  |  |  | 0.301 | 62.6681 | 0.84855 | 0.85994 |  |  |  |  | 206 | 0.011866
11021 | TIEHVCG_1G | 1 | West | YES | 0.13028 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.301 | 142.1 | 142.1 |  |  |  |  | 0.301 | 42.7721 | 0.85192 | 0.86314 |  |  |  |  | 207 | 0.011771
11022 | TIEHVCG_2G | 1 | West | YES | 0.13028 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.301 | 132.4 | 132.4 |  |  |  |  | 0.301 | 39.8524 | 0.85506 | 0.86613 |  |  |  |  | 208 | 0.011635
11023 | TIEHVCG_3G | 1 | West | YES | 0.13028 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.301 | 137.4 | 137.4 |  |  |  |  | 0.301 | 41.3574 | 0.85833 | 0.86923 |  |  |  |  | 209 | 0.011388
11024 | TIEHVCG_4G | 1 | West | YES | 0.13028 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.301 | 147 | 147 |  |  |  |  | 0.301 | 44.247 | 0.86182 | 0.87254 |  |  |  |  | 210 | 0.011219
11025 | TIEHVSG_2G | 1 | West | YES | 0.13028 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.301 | 213.2 | 213.2 |  |  |  |  | 0.301 | 64.1731 | 0.86688 | 0.87735 |  |  |  |  | 211 | 0.011062
1326 | STANTONW_8 | 1 | West | YES | 0.13024 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.30095 | 0 | 100.5 |  |  |  |  | 0.30095 | 30.2459 | 0.86926 | 0.87962 |  |  |  |  | 212 | 0.0109
1320 | BSP 1 | 1 | West | YES | 0.13011 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.30083 | 0 | 0 |  |  |  |  | 0.30083 | 0 | 0.86926 | 0.87962 |  |  |  |  | 213 | 0.010725
76031 | L_GASCCR1_1N | W1 | West | YES | 0.1298 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.30052 | 0 | 150 |  |  |  |  | 0.30052 | 45.0783 | 0.87282 | 0.88299 |  |  |  |  | 214 | 0.010473
11147 | NOTREES_1G | 1 | West | YES | 0.12945 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.30017 | 0 | 149 |  |  |  |  | 0.30017 | 44.7256 | 0.87636 | 0.88635 |  |  |  |  | 215 | 0.010353
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.12945 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.30016 | 0 | 112.5 |  |  |  |  | 0.30016 | 33.7683 | 0.87903 | 0.88888 |  |  |  |  | 216 | 0.010353
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.12945 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 149.5 |  |  |  |  | 0.30016 | 44.8743 | 0.88258 | 0.89224 |  |  |  |  | 217 | 0.01017
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.12945 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 186 |  |  |  |  | 0.30016 | 55.8303 | 0.887 | 0.89642 |  |  |  |  | 218 | 0.0099839
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.12945 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 214.5 |  |  |  |  | 0.30016 | 64.3849 | 0.89209 | 0.90125 |  |  |  |  | 219 | 0.0098435
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.12932 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.30003 | 0 | 35 |  |  |  |  | 0.30003 | 10.5012 | 0.89292 | 0.90203 |  |  |  |  | 220 | 0.0096569
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.12932 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.30003 | 0 | 30 |  |  |  |  | 0.30003 | 9.001 | 0.89363 | 0.90271 |  |  |  |  | 221 | 0.0094247
1002 | PBCTAGE_1G | A | West | YES | 0.12924 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.29996 | 66 | 66 |  |  |  |  | 0.29996 | 19.7975 | 0.8952 | 0.90419 |  |  |  |  | 222 | 0.009157
1003 | PBCTBGE_2G | B | West | YES | 0.12924 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.29996 | 66 | 66 |  |  |  |  | 0.29996 | 19.7975 | 0.89677 | 0.90568 |  |  |  |  | 223 | 0.0091129
1004 | PBCTCGE_3G | C | West | YES | 0.12924 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.29996 | 67 | 67 |  |  |  |  | 0.29996 | 20.0975 | 0.89836 | 0.90718 |  |  |  |  | 224 | 0.0090752
1005 | PBCTDGE_4G | D | West | YES | 0.12924 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.29996 | 68 | 68 |  |  |  |  | 0.29996 | 20.3975 | 0.89997 | 0.90871 |  |  |  |  | 225 | 0.0089918
1006 | PBCTEGE_5G | E | West | YES | 0.12924 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.29996 | 67 | 67 |  |  |  |  | 0.29996 | 20.0975 | 0.90156 | 0.91022 |  |  |  |  | 226 | 0.0089085
1007 | PB5GEN_6G | 5 | West | YES | 0.12924 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.29996 | 114 | 114 |  |  |  |  | 0.29996 | 34.1958 | 0.90427 | 0.91278 |  |  |  |  | 227 | 0.0088238
1008 | PB6GEN_7G | 6 | West | YES | 0.12924 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.29996 | 515 | 515 |  |  |  |  | 0.29996 | 154.4808 | 0.9165 | 0.92435 |  |  |  |  | 228 | 0.0087379
60057 | CALLAHAN1A | 1 | West | YES | 0.12912 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.29984 | 0 | 114 |  |  |  |  | 0.29984 | 34.1821 | 0.9192 | 0.92692 |  |  |  |  | 229 | 0.0086533
1349 | WESTXWIN_1G | 1 | West | YES | 0.12878 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.2995 | 0 | 6.6 |  |  |  |  | 0.2995 | 1.9767 | 0.91936 | 0.92706 |  |  |  |  | 230 | 0.0085093
1350 | NWPWRG1_1G | 1 | West | YES | 0.12878 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.2995 | 0 | 34.3 |  |  |  |  | 0.2995 | 10.2727 | 0.92017 | 0.92783 |  |  |  |  | 231 | 0.0078587
60007 | KING_SW1A | 1 | West | YES | 0.12239 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29311 | 0 | 80 |  |  |  |  | 0.29311 | 23.4485 | 0.92207 | 0.92959 |  |  |  |  | 232 | 0.0077137
60019 | KING_NW1A | 1 | West | YES | 0.12239 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29311 | 0 | 80 |  |  |  |  | 0.29311 | 23.4485 | 0.92397 | 0.93135 |  |  |  |  | 233 | 0.0077051
244 | WHITNYDM01 | 1 | North | YES | 0.12239 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.2931 | 0 | 0 | 0 | 0 |  |  | 0.2931 | 0 | 0.92397 | 0.93135 |  |  |  |  | 234 | 0.0076606
245 | WHITNYDM02 | 2 | North | YES | 0.12239 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.2931 | 0 | 0 | 0 | 0 |  |  | 0.2931 | 0 | 0.92397 | 0.93135 |  |  |  |  | 235 | 0.0075184
60201 | RIO DRCS | F | West | YES | 0.12207 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.29279 | 0 | 0 |  |  |  |  | 0.29279 | 0 | 0.92397 | 0.93135 |  |  |  |  | 236 | 0.0073763
6016 | SWMESA | 1 | West | YES | 0.12194 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.29266 | 0 | 75 |  |  |  |  | 0.29266 | 21.9496 | 0.92575 | 0.93299 |  |  |  |  | 237 | 0.0073763
60003 | KING_NE1A | 1 | West | YES | 0.12194 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29266 | 0 | 80 |  |  |  |  | 0.29266 | 23.4129 | 0.92765 | 0.93475 |  |  |  |  | 238 | 0.0073763
60005 | KING_SE1A | 1 | West | YES | 0.12194 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.29266 | 0 | 40 |  |  |  |  | 0.29266 | 11.7065 | 0.9286 | 0.93562 |  |  |  |  | 239 | 0.0073763
60016 | WOODWRD11A | 1 | West | YES | 0.12186 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.29258 | 0 | 80 |  |  |  |  | 0.29258 | 23.4063 | 0.9305 | 0.93738 |  |  |  |  | 240 | 0.0072405
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.12184 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.29256 | 0 | 80 |  |  |  |  | 0.29256 | 23.405 | 0.9324 | 0.93913 |  |  |  |  | 241 | 0.0070957
38437 | TNSRBNMESA9 | 1 | West | YES | 0.12178 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.2925 | 0 | 150 |  |  |  |  | 0.2925 | 43.8744 | 0.93596 | 0.94242 |  |  |  |  | 242 | 0.0070233
60017 | ORNNWP1 | 1 | West | YES | 0.11942 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.29014 | 0 | 80 |  |  |  |  | 0.29014 | 23.2109 | 0.93786 | 0.94416 |  |  |  |  | 243 | 0.0068779
60000 | DSKY2 | 1 | West | YES | 0.11883 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.28955 | 0 | 76.5 |  |  |  |  | 0.28955 | 22.1502 | 0.93968 | 0.94582 |  |  |  |  | 244 | 0.0067325
60018 | DSKY1 | 1 | West | YES | 0.11862 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.28934 | 0 | 84 |  |  |  |  | 0.28934 | 24.3045 | 0.94167 | 0.94764 |  |  |  |  | 245 | 0.0064591
251 | BOSQUESW803 | 2 | North | YES | 0.11786 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.28857 | 150 | 150 | 17.6782 | 150 |  |  | 0.28857 | 43.2859 | 0.94523 | 0.95088 |  |  |  |  | 246 | 0.0062991
253 | BOSQUESW804 | 2 | North | YES | 0.11786 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.28857 | 80 | 80 | 9.4284 | 80 |  |  | 0.28857 | 23.0858 | 0.94713 | 0.95261 |  |  |  |  | 247 | 0.0061428
238 | BOSQUESW505 | 1 | North | YES | 0.11477 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.28549 | 255 | 255 | 29.2674 | 255 |  |  | 0.28549 | 72.8004 | 0.95318 | 0.95807 |  |  |  |  | 248 | 0.0059698
239 | BOSQUESW502 | 1 | North | YES | 0.11477 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.28549 | 149 | 149 | 17.1013 | 149 |  |  | 0.28549 | 42.5383 | 0.95672 | 0.96126 |  |  |  |  | 249 | 0.0056523
247 | BOSQUESW501 | 2 | North | YES | 0.11477 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.28549 | 156 | 156 | 17.9047 | 156 |  |  | 0.28549 | 44.5367 | 0.96042 | 0.96459 |  |  |  |  | 250 | 0.005483
3403 | THOUSE_1G | 1 | North | YES | 0.11301 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.28372 | 563 | 563 | 63.6224 | 563 |  |  | 0.28372 | 159.7365 | 0.97379 | 0.97656 |  |  |  |  | 251 | 0.0048843
3404 | THOUSE_2G | 2 | North | YES | 0.11301 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.28372 | 807 | 807 | 91.1958 | 807 |  |  | 0.28372 | 228.9651 | 0.99295 | 0.99372 |  |  |  |  | 252 | 0.0045345
3416 | LAKE_CRK1_G | 1 | North | YES | 0.11148 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.28219 | 75 | 75 | 8.3608 | 75 |  |  | 0.28219 | 21.1646 | 0.99473 | 0.99531 |  |  |  |  | 253 | 0.0041683
3417 | LAKE_CRK2_G | 2 | North | YES | 0.11148 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.28219 | 222 | 222 | 24.7479 | 222 |  |  | 0.28219 | 62.6472 | 1 | 1 |  |  |  |  | 254 | 0.002772
60202 | FRNDDRCS | F | West | YES | 0.1063 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.27701 | 0 | 0 |  |  |  |  | 0.27701 | 0 | 1 | 1 |  |  |  |  | 255 | 0.00077061
13432 | SANDOW_5G | 5 | South | YES | 0.044563 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.10737 | 0 | 581 |  |  |  |  | -0.10737 | 0 | [6 empty] | 256 | 0.00057601
3432 | SANDOW_4G | 4 | South | YES | 0.025209 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.12673 | 0 | 580 |  |  |  |  | -0.12673 | 0 | [6 empty] | 257 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.009199 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 | [6 empty] | 258 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.009199 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 | [6 empty] | 259 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.009199 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 | [6 empty] | 260 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.008542 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.14339 | 0 | 0 |  |  |  |  | -0.14339 | 0 | [6 empty] | 261 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.002445 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 | [6 empty] | 262 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.002445 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 | [6 empty] | 263 | 0
88253 | HAMILTON | F | South | YES | 0.002445 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 | [6 empty] | 264 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.15194 | 15 | 15 |  |  |  |  | -0.15194 | -2.2791 | [6 empty] | 265 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | [6 empty] | 266 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | [6 empty] | 267 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | [6 empty] | 268 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | [6 empty] | 269 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | [6 empty] | 270 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | [6 empty] | 271 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | [6 empty] | 272 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | [6 empty] | 273 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.15194 | 0 | 0 |  |  | 0 | 0 | -0.15194 | 0 | [6 empty] | 274 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.000339 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.15228 | 0 | 0 |  |  |  |  | -0.15228 | 0 | [6 empty] | 275 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.000339 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.15228 | 0 | 0 |  |  |  |  | -0.15228 | 0 | [6 empty] | 276 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.000571 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.15251 | 423.3 | 423.3 |  |  |  |  | -0.15251 | -64.5566 | [6 empty] | 277 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.003309 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.15525 | 0 | 0 |  |  |  |  | -0.15525 | 0 | [6 empty] | 278 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.003309 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.15525 | 0 | 0 |  |  |  |  | -0.15525 | 0 | [6 empty] | 279 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.008971 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 | [6 empty] | 280 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.008971 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 | [6 empty] | 281 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.008971 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 | [6 empty] | 282 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.01105 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.16299 | 42 | 42 |  |  |  |  | -0.16299 | -6.8455 | [6 empty] | 283 | 0
9003 | DECKR_G4 | 4 | South | YES | -0.01105 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.16299 | 44 | 44 |  |  |  |  | -0.16299 | -7.1714 | [6 empty] | 284 | 0
9004 | DECKR_G5 | 5 | South | YES | -0.01105 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.16299 | 44 | 44 |  |  |  |  | -0.16299 | -7.1714 | [6 empty] | 285 | 0
9005 | DECKR_G6 | 6 | South | YES | -0.01105 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.16299 | 47 | 47 |  |  |  |  | -0.16299 | -7.6604 | [6 empty] | 286 | 0
9000 | DECKR_G1 | 1 | South | YES | -0.012116 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.16405 | 321 | 321 |  |  |  |  | -0.16405 | -52.661 | [6 empty] | 287 | 0
9001 | DECKR_G2 | 2 | South | YES | -0.012116 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.16405 | 426 | 426 |  |  |  |  | -0.16405 | -69.8865 | [6 empty] | 288 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.012215 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.16415 | 0 | 0 |  |  |  |  | -0.16415 | 0 | [6 empty] | 289 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.012215 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.16415 | 0 | 0 |  |  |  |  | -0.16415 | 0 | [6 empty] | 290 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.013615 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.16555 | 49 | 49 |  |  |  |  | -0.16555 | -8.112 | [6 empty] | 291 | 0
9017 | SANDH_G2 | 2 | South | YES | -0.013615 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.16555 | 46 | 46 |  |  |  |  | -0.16555 | -7.6154 | [6 empty] | 292 | 0
9018 | SANDH_G3 | 3 | South | YES | -0.013615 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.16555 | 46 | 46 |  |  |  |  | -0.16555 | -7.6154 | [6 empty] | 293 | 0
9019 | SANDH_G4 | 4 | South | YES | -0.013615 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.16555 | 47 | 47 |  |  |  |  | -0.16555 | -7.7809 | [6 empty] | 294 | 0
9020 | SANDHG5A | 5A | South | YES | -0.013615 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.16555 | 155 | 155 |  |  |  |  | -0.16555 | -25.6605 | [6 empty] | 295 | 0
9021 | SANDHG5C | 5C | South | YES | -0.013615 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.16555 | 148 | 148 |  |  |  |  | -0.16555 | -24.5017 | [6 empty] | 296 | 0
8262 | ELPS | 1 | South | YES | -0.014069 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.16601 | 0 | 0 |  |  |  |  | -0.16601 | 0 | [6 empty] | 297 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.017461 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.1694 | 152.5 | 152.5 |  |  |  |  | -0.1694 | -25.8332 | [6 empty] | 298 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.017461 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.1694 | 149.5 | 149.5 |  |  |  |  | -0.1694 | -25.325 | [6 empty] | 299 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.017461 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.1694 | 232.6 | 232.6 |  |  |  |  | -0.1694 | -39.402 | [6 empty] | 300 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.019922 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.17186 | 158 | 158 |  |  |  |  | -0.17186 | -27.1537 | [6 empty] | 301 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.019922 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.17186 | 160 | 160 |  |  |  |  | -0.17186 | -27.4974 | [6 empty] | 302 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.019922 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.17186 | 175 | 175 |  |  |  |  | -0.17186 | -30.0753 | [6 empty] | 303 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.022083 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.17402 | 132 | 132 |  |  |  |  | -0.17402 | -22.9706 | [6 empty] | 304 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.022083 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.17402 | 139 | 139 |  |  |  |  | -0.17402 | -24.1888 | [6 empty] | 305 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.022083 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.17402 | 329 | 329 |  |  |  |  | -0.17402 | -57.2526 | [6 empty] | 306 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.031678 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.18361 | 0 | 0 |  |  |  |  | -0.18361 | 0 | [6 empty] | 307 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.036626 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.18856 | 223.9 | 223.9 |  |  |  |  | -0.18856 | -42.2192 | [6 empty] | 308 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.036626 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.18856 | 225 | 225 |  |  |  |  | -0.18856 | -42.4267 | [6 empty] | 309 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.036626 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.18856 | 224.6 | 224.6 |  |  |  |  | -0.18856 | -42.3512 | [6 empty] | 310 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.036626 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.18856 | 226.7 | 226.7 |  |  |  |  | -0.18856 | -42.7472 | [6 empty] | 311 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 | [6 empty] | 312 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 | [6 empty] | 313 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 | [6 empty] | 314 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 | [6 empty] | 315 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.039706 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.19164 | 0 | 606 |  |  |  |  | -0.19164 | 0 | [6 empty] | 316 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.039706 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.19164 | 0 | 598 |  |  |  |  | -0.19164 | 0 | [6 empty] | 317 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.039835 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.19177 | 0 | 436 |  |  |  |  | -0.19177 | 0 | [6 empty] | 318 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.041131 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 | [6 empty] | 319 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.041131 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 | [6 empty] | 320 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.041131 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 | [6 empty] | 321 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.041424 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.19336 | 148 | 148 |  |  |  |  | -0.19336 | -28.6174 | [6 empty] | 322 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.041424 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.19336 | 148 | 148 |  |  |  |  | -0.19336 | -28.6174 | [6 empty] | 323 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.041424 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.19336 | 154 | 154 |  |  |  |  | -0.19336 | -29.7776 | [6 empty] | 324 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.041424 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.19336 | 293 | 293 |  |  |  |  | -0.19336 | -56.6547 | [6 empty] | 325 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.042126 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.19406 | 0 | 0 |  |  |  |  | -0.19406 | 0 | [6 empty] | 326 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.044521 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.19646 | 0 | 0 |  |  |  |  | -0.19646 | 0 | [6 empty] | 327 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.044521 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.19646 | 0 | 0 |  |  |  |  | -0.19646 | 0 | [6 empty] | 328 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 329 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 330 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 331 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 332 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 333 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 334 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 335 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 336 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 337 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 338 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 339 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 340 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 341 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 342 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 343 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 344 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 345 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 346 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 347 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 348 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 349 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 350 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 351 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | [6 empty] | 352 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.045929 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.19787 | 147 | 147 |  |  |  |  | -0.19787 | -29.0863 | [6 empty] | 353 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.045929 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.19787 | 138 | 138 |  |  |  |  | -0.19787 | -27.3055 | [6 empty] | 354 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.045929 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.19787 | 146 | 146 |  |  |  |  | -0.19787 | -28.8884 | [6 empty] | 355 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.045929 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.19787 | 149 | 149 |  |  |  |  | -0.19787 | -29.482 | [6 empty] | 356 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.045929 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.19787 | 182 | 182 |  |  |  |  | -0.19787 | -36.0116 | [6 empty] | 357 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.045929 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.19787 | 203 | 203 |  |  |  |  | -0.19787 | -40.1668 | [6 empty] | 358 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.046913 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.19885 | 407 | 407 |  |  |  |  | -0.19885 | -80.9319 | [6 empty] | 359 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.046925 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.19886 | 24 | 24 |  |  |  |  | -0.19886 | -4.7727 | [6 empty] | 360 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.046925 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.19886 | 24.3 | 24.3 |  |  |  |  | -0.19886 | -4.8323 | [6 empty] | 361 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.046925 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.19886 | 23.9 | 23.9 |  |  |  |  | -0.19886 | -4.7528 | [6 empty] | 362 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | -0.046951 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.19889 | 0 | 430 |  |  |  |  | -0.19889 | 0 | [6 empty] | 363 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.046951 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.19889 | 0 | 430 |  |  |  |  | -0.19889 | 0 | [6 empty] | 364 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.046953 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.19889 | 418 | 418 |  |  |  |  | -0.19889 | -83.136 | [6 empty] | 365 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | -0.046953 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.19889 | 400 | 400 |  |  |  |  | -0.19889 | -79.556 | [6 empty] | 366 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.046973 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.19891 | 58 | 58 |  |  |  |  | -0.19891 | -11.5368 | [6 empty] | 367 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | -0.046973 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.19891 | 89 | 89 |  |  |  |  | -0.19891 | -17.703 | [6 empty] | 368 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | -0.046973 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.19891 | 44 | 44 |  |  |  |  | -0.19891 | -8.752 | [6 empty] | 369 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | -0.046973 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.19891 | 44 | 44 |  |  |  |  | -0.19891 | -8.752 | [6 empty] | 370 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | -0.046973 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.19891 | 43 | 43 |  |  |  |  | -0.19891 | -8.5531 | [6 empty] | 371 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | -0.046973 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.19891 | 45 | 45 |  |  |  |  | -0.19891 | -8.9509 | [6 empty] | 372 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.046999 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.19894 | 61 | 61 |  |  |  |  | -0.19894 | -12.1351 | [6 empty] | 373 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.046999 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.19894 | 95 | 95 |  |  |  |  | -0.19894 | -18.8989 | [6 empty] | 374 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.046999 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.19894 | 151 | 151 |  |  |  |  | -0.19894 | -30.0393 | [6 empty] | 375 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.047121 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.19906 | 215 | 215 |  |  |  |  | -0.19906 | -42.7975 | [6 empty] | 376 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.047121 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.19906 | 216 | 216 |  |  |  |  | -0.19906 | -42.9965 | [6 empty] | 377 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.04861 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.20055 | 155 | 155 |  |  |  |  | -0.20055 | -31.0848 | [6 empty] | 378 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | -0.04861 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.20055 | 174 | 174 |  |  |  |  | -0.20055 | -34.8952 | [6 empty] | 379 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.04861 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.20055 | 155 | 155 |  |  |  |  | -0.20055 | -31.0848 | [6 empty] | 380 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.04973 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.20167 | 0 | 562 |  |  |  |  | -0.20167 | 0 | [6 empty] | 381 | 0
8189 | CUECPL2A | 1 | South | YES | -0.053362 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.2053 | 0 | 0 |  |  |  |  | -0.2053 | 0 | [6 empty] | 382 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.055475 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.20741 | 0 | 396.3 |  |  |  |  | -0.20741 | 0 | [6 empty] | 383 | 0
80265 | LARECU40A | 4 | South | YES | -0.055804 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.20774 | 100 | 100 |  |  |  |  | -0.20774 | -20.7741 | [6 empty] | 384 | 0
80266 | LARECU50A | 5 | South | YES | -0.055804 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.20774 | 100 | 100 |  |  |  |  | -0.20774 | -20.7741 | [6 empty] | 385 | 0
80012 | LAR | F | South | YES | -0.055808 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.20774 | 0 | 0 |  |  |  |  | -0.20774 | 0 | [6 empty] | 386 | 0
88299 | ZAPATA | F | South | YES | -0.062149 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.21409 | 0 | 0 |  |  |  |  | -0.21409 | 0 | [6 empty] | 387 | 0
88198 | BEEVILLE | F | South | YES | -0.065317 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.21725 | 0 | 0 |  |  |  |  | -0.21725 | 0 | [6 empty] | 388 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.066451 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0 | [6 empty] | 389 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.066451 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0 | [6 empty] | 390 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.066451 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0
88508 | FALFURRI | F | South | YES | -0.067258 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.21919 | 0 | 0 |  |  |  |  | -0.21919 | 0
8161 | COLETO0A | 1 | South | YES | -0.068894 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.22083 | 0 | 633 |  |  |  |  | -0.22083 | 0
8933 | FGNTS001 | 1 | South | YES | -0.070946 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.22288 | 146.5 | 146.5 |  |  |  |  | -0.22288 | -32.6523
8934 | FGNTS101 | 2 | South | YES | -0.070946 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.22288 | 147.9 | 147.9 |  |  |  |  | -0.22288 | -32.9644
8935 | FGNTS201 | 3 | South | YES | -0.070946 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.22288 | 173 | 173 |  |  |  |  | -0.22288 | -38.5587
8981 | HECN1 | 1 | South | YES | -0.071702 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.22364 | 144.8 | 144.8 |  |  |  |  | -0.22364 | -32.3829
8982 | HECN2 | 2 | South | YES | -0.071702 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.22364 | 144.1 | 144.1 |  |  |  |  | -0.22364 | -32.2264
8983 | HECN3 | 3 | South | YES | -0.071702 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.22364 | 171.9 | 171.9 |  |  |  |  | -0.22364 | -38.4435
8936 | MVGN#1 | 1 | South | YES | -0.071704 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.22364 | 216.6 | 216.6 |  |  |  |  | -0.22364 | -48.4406
8937 | MVGN#2 | 2 | South | YES | -0.071704 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.22364 | 216.7 | 216.7 |  |  |  |  | -0.22364 | -48.463
8938 | MVGN#3 | 3 | South | YES | -0.071704 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.22364 | 250.9 | 250.9 |  |  |  |  | -0.22364 | -56.1115
80003 | MILHWYS | F | South | YES | -0.072035 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.22397 | 0 | 0 |  |  |  |  | -0.22397 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.072036 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.22397 | 38 | 38 |  |  |  |  | -0.22397 | -8.511
5933 | SI_RAY6 | 6 | South | YES | -0.072036 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.22397 | 19.3 | 19.3 |  |  |  |  | -0.22397 | -4.3227
5935 | SI_RAY10 | 10 | South | YES | -0.072036 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.22397 | 47 | 47 |  |  |  |  | -0.22397 | -10.5267
80080 | GWINDT11A | 1 | South | YES | -0.072238 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 94 |  |  |  |  | -0.22417 | 0
80080 | GWINDT11A | 2 | South | YES | -0.072238 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 41 |  |  |  |  | -0.22417 | 0
80080 | GWINDT11A | 3 | South | YES | -0.072238 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 38 |  |  |  |  | -0.22417 | 0
80080 | GWINDT11A | 4 | South | YES | -0.072238 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 19 |  |  |  |  | -0.22417 | 0
80081 | GWINDT21A | 1 | South | YES | -0.072238 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 94 |  |  |  |  | -0.22417 | 0
80081 | GWINDT21A | 2 | South | YES | -0.072238 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 36 |  |  |  |  | -0.22417 | 0
80081 | GWINDT21A | 3 | South | YES | -0.072238 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 43 |  |  |  |  | -0.22417 | 0
80081 | GWINDT21A | 4 | South | YES | -0.072238 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 22 |  |  |  |  | -0.22417 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.072238 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 148 |  |  |  |  | -0.22417 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.072238 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 50 |  |  |  |  | -0.22417 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.072238 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 55 |  |  |  |  | -0.22417 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.072238 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 50 |  |  |  |  | -0.22417 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.072335 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.22427 | 0 | 0 |  |  |  |  | -0.22427 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.072936 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.22487 | 0 | 0 |  |  |  |  | -0.22487 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.07299 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.22493 | 0 | 0 |  |  |  |  | -0.22493 | 0
8506 | VAL #1 | 1 | South | YES | -0.073101 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.22504 | 0 | 0 |  |  |  |  | -0.22504 | 0
8507 | VAL #2 | 2 | South | YES | -0.073101 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.22504 | 0 | 0 |  |  |  |  | -0.22504 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.073242 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.22518 | 0 | 0 |  |  |  |  | -0.22518 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.073242 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.22518 | 0 | 0 |  |  |  |  | -0.22518 | 0
80263 | B_DAVIS31A | 3 | South | YES | -0.073242 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.22518 | 180 | 180 |  |  |  |  | -0.22518 | -40.5322
80264 | B_DAVIS41A | 4 | South | YES | -0.073242 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.22518 | 180 | 180 |  |  |  |  | -0.22518 | -40.5322
8456 | COSW#1 | 1 | South | YES | -0.07341 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.22535 | 0 | 0 |  |  |  |  | -0.22535 | 0
8457 | COSW#2 | 2 | South | YES | -0.07341 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.22535 | 0 | 0 |  |  |  |  | -0.22535 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.07349 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.07349 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0
8562 | CNOPST1 | 3 | South | YES | -0.07349 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0
8442 | NBEC7 | 7 | South | YES | -0.073507 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.22544 | 367 | 367 |  |  |  |  | -0.22544 | -82.7379
8442 | NBEC7 | MB | South | YES | -0.073507 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.22544 | 0 | 0 |  |  |  |  | -0.22544 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.074954 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.074954 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.074954 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0
8930 | ICPGN10A | 1 | South | YES | -0.074954 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0
8931 | ICPGN20A | 2 | South | YES | -0.074954 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0
8932 | ICPGN30A | 3 | South | YES | -0.074954 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0
80223 | REYSHR G | 1 | South | YES | -0.074954 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0
8173 | VICEC51A | 5 | South | YES | -0.075848 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.22778 | 144 | 144 |  |  |  |  | -0.22778 | -32.801
8174 | VICEC61A | 6 | South | YES | -0.075848 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.22778 | 188 | 188 |  |  |  |  | -0.22778 | -42.8236
5508 | RAYBURNCC9 | 1 | South | YES | -0.077106 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.22904 | 47.7 | 47.7 |  |  |  |  | -0.22904 | -10.9253
5509 | RAYBURNCC10 | 1 | South | YES | -0.077106 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.22904 | 37.3 | 37.3 |  |  |  |  | -0.22904 | -8.5433
5511 | RAYBURNCC7 | 1 | South | YES | -0.077106 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.22904 | 47.5 | 47.5 |  |  |  |  | -0.22904 | -10.8795
5512 | RAYBURNCC8 | 1 | South | YES | -0.077106 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.22904 | 49.3 | 49.3 |  |  |  |  | -0.22904 | -11.2918
8066 | DUP1V#1 | 1 | South | YES | -0.077236 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.22917 | 0 | 0 |  |  |  |  | -0.22917 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.077767 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.2297 | 22 | 22 |  |  |  |  | -0.2297 | -5.0535
5505 | RAYBURNGEN1 | 1 | South | YES | -0.077767 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.2297 | 11 | 11 |  |  |  |  | -0.2297 | -2.5267
5506 | RAYBURNGEN2 | 1 | South | YES | -0.077767 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.2297 | 11 | 11 |  |  |  |  | -0.2297 | -2.5267
80224 | VISTRONG1 | 1 | South | YES | -0.079573 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.23151 | 0 | 0 |  |  |  |  | -0.23151 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.079573 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.23151 | 0 | 0 |  |  |  |  | -0.23151 | 0
80227 | AIRCO G | 1 | South | YES | -0.080386 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.23232 | 0 | 0 |  |  |  |  | -0.23232 | 0
8147 | UCAR #2 | 10 | South | YES | -0.080967 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0
8148 | UCAR #1 | 2 | South | YES | -0.080967 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0
80137 | CSDR89 | 8 | South | YES | -0.080967 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0
80137 | CSDR89 | 9 | South | YES | -0.080967 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0
80138 | CSDR7 | 7 | South | YES | -0.080967 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0
80139 | CSDR56 | 5 | South | YES | -0.080967 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0
80139 | CSDR56 | 6 | South | YES | -0.080967 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0
80140 | CSDR11 | 11 | South | YES | -0.080967 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0
80226 | ALCOA G | 1 | South | YES | -0.084515 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.23645 | 0 | 0 |  |  |  |  | -0.23645 | 0
8134 | FOR #1 | 1 | South | YES | -0.085582 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
8138 | FOR #2 | 2 | South | YES | -0.085582 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
8153 | FOR #3 | 3 | South | YES | -0.085582 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
8154 | FOR #4 | 4 | South | YES | -0.085582 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
8155 | FOR #5 | 5 | South | YES | -0.085582 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
8156 | FOR #6 | 6 | South | YES | -0.085582 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
8157 | FOR #7 | 7 | South | YES | -0.085582 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
80051 | FOR #8 | 8 | South | YES | -0.085582 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
80052 | FOR #9 | 9 | South | YES | -0.085582 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
80053 | FOR #10 | 10 | South | YES | -0.085582 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.12209 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.27403 | 0 | 0 |  |  | 0 | 0 | -0.27403 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.12209 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.27403 | 0 | 0 |  |  | 0 | 0 | -0.27403 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253
48732 | CBE_GT2 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253
48733 | CBE_ST12 | 1 | Houston | YES | -0.12734 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.27928 | 105 | 105 |  |  | -13.371 | 105 | -0.27928 | -29.3244
48734 | CBE_GT3 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253
48735 | CBE_GT4 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253
48736 | CBE_ST34 | 1 | Houston | YES | -0.12734 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.27928 | 105 | 105 |  |  | -13.371 | 105 | -0.27928 | -29.3244
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.13008 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.28202 | 0 | 0 |  |  | 0 | 0 | -0.28202 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.14065 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.14065 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.14065 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.14065 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.14065 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.14065 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.14065 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.14065 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.14065 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.14065 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.14065 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.14065 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.14065 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.14065 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.14065 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.14065 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.14065 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.14065 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.14065 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.14065 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.14503 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.29697 | 0 | 0 |  |  | 0 | 0 | -0.29697 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.14503 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.29697 | 0 | 0 |  |  | 0 | 0 | -0.29697 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.14876 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.14876 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.14876 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.14876 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.1554 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 651 |  |  | 0 | 0 | -0.30733 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.1554 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 564 |  |  | 0 | 0 | -0.30733 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.1554 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 603 |  |  | 0 | 0 | -0.30733 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.1555 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.30744 | 167.7 | 167.7 |  |  | -26.0773 | 167.7 | -0.30744 | -51.5572
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.1555 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.30744 | 166.4 | 166.4 |  |  | -25.8752 | 166.4 | -0.30744 | -51.1575
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.1555 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.30744 | 252.4 | 252.4 |  |  | -39.2482 | 252.4 | -0.30744 | -77.5971
48730 | MNS_GT | 1 | Houston | YES | -0.15817 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.3101 | 0 | 0 |  |  | 0 | 0 | -0.3101 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.15966 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.31159 | 0 | 0 |  |  | 0 | 0 | -0.31159 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.1608 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.31274 | 166 | 166 |  |  | -26.6933 | 166 | -0.31274 | -51.9148
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.1608 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.31274 | 166 | 166 |  |  | -26.6933 | 166 | -0.31274 | -51.9148
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.1608 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.31274 | 248 | 248 |  |  | -39.8791 | 248 | -0.31274 | -77.5595
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.1608 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.31274 | 546 | 546 |  |  | -87.7984 | 546 | -0.31274 | -170.756
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.1608 | 607.1 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.31274 | 0 | 654 |  |  | 0 | 0 | -0.31274 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.1608 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.31274 | 13 | 13 |  |  | -2.0904 | 13 | -0.31274 | -4.0656
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.16573 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.16573 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.16573 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.16573 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.16573 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.16573 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.16573 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.16573 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.16573 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.16573 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.16573 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.16573 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.16573 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.16573 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.16573 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.169 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.32093 | 0 | 0 |  |  | 0 | 0 | -0.32093 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.17133 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.17133 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.17133 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.17133 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.17133 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.17223 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.17223 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.17223 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.17223 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.1726 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.32454 | 163.2 | 163.2 |  |  | -28.1685 | 163.2 | -0.32454 | -52.9646
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.1726 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.32454 | 157.1 | 157.1 |  |  | -27.1156 | 157.1 | -0.32454 | -50.9849
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.1726 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.32454 | 157.5 | 157.5 |  |  | -27.1847 | 157.5 | -0.32454 | -51.1147
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.1726 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.32454 | 157 | 157 |  |  | -27.0984 | 157 | -0.32454 | -50.9525
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.1726 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.32454 | 282 | 282 |  |  | -48.6735 | 282 | -0.32454 | -91.5197
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.17391 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.32585 | 0 | 0 |  |  | 0 | 0 | -0.32585 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.17391 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.32585 | 0 | 0 |  |  | 0 | 0 | -0.32585 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179
48691 | GBY_73741085 | B | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179
48692 | GBY_81821075 | C | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179
48692 | GBY_81821075 | D | Houston | YES | -0.17398 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.32591 | 55 | 55 |  |  | -9.5687 | 55 | -0.32591 | -17.9252
48693 | GBY_83841065 | E | Houston | YES | -0.17398 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.32591 | 57 | 57 |  |  | -9.9166 | 57 | -0.32591 | -18.577
48693 | GBY_83841065 | F | Houston | YES | -0.17398 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.32591 | 54 | 54 |  |  | -9.3947 | 54 | -0.32591 | -17.5993
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.17439 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.32633 | 0 | 0 |  |  | 0 | 0 | -0.32633 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.17481 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.32675 | 0 | 0 |  |  | 0 | 0 | -0.32675 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.17481 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.32675 | 0 | 0 |  |  | 0 | 0 | -0.32675 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.17481 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.32675 | 18 | 18 |  |  | -3.1466 | 18 | -0.32675 | -5.8814
48855 | SRB_GT211035 | B2 | Houston | YES | -0.17481 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.32675 | 12 | 12 |  |  | -2.0977 | 12 | -0.32675 | -3.921
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.17483 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.32677 | 176 | 176 |  |  | -30.7706 | 176 | -0.32677 | -57.5115
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.17486 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.3268 | 165 | 165 |  |  | -28.8517 | 165 | -0.3268 | -53.9213
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.17488 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.17488 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.17488 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.17495 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.32688 | 228 | 228 |  |  | -39.8877 | 228 | -0.32688 | -74.5293
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.17496 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.17496 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.17496 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.17496 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.17497 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.3269 | 16.2 | 16.2 |  |  | -2.8345 | 16.2 | -0.3269 | -5.2958
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.17498 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.32691 | 213 | 213 |  |  | -37.2701 | 213 | -0.32691 | -69.6327
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.17533 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.17533 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.17533 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.17533 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.17606 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.328 | 42 | 42 |  |  | -7.3946 | 42 | -0.328 | -13.776
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.17606 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.328 | 42 | 42 |  |  | -7.3946 | 42 | -0.328 | -13.776
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.17606 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.328 | 39 | 39 |  |  | -6.8665 | 39 | -0.328 | -12.792
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.17606 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.328 | 39 | 39 |  |  | -6.8665 | 39 | -0.328 | -12.792
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.1763 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.32823 | 0 | 0 |  |  | 0 | 0 | -0.32823 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.17653 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.32847 | 0 | 0 |  |  | 0 | 0 | -0.32847 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.17653 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.32847 | 0 | 0 |  |  | 0 | 0 | -0.32847 | 0
48885 | THW_5152 | A | Houston | YES | -0.17751 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.32945 | 58 | 58 |  |  | -10.2958 | 58 | -0.32945 | -19.1081
48885 | THW_5152 | B | Houston | YES | -0.17751 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.32945 | 59 | 59 |  |  | -10.4733 | 59 | -0.32945 | -19.4375
48886 | THW_5354 | C | Houston | YES | -0.17751 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.32945 | 57 | 57 |  |  | -10.1182 | 57 | -0.32945 | -18.7786
48886 | THW_5354 | D | Houston | YES | -0.17751 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.32945 | 58 | 58 |  |  | -10.2958 | 58 | -0.32945 | -19.1081
48887 | THW_5556 | E | Houston | YES | -0.17751 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.32945 | 59 | 59 |  |  | -10.4733 | 59 | -0.32945 | -19.4375
48887 | THW_5556 | F | Houston | YES | -0.17751 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.32945 | 57 | 57 |  |  | -10.1182 | 57 | -0.32945 | -18.7786
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.17776 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.32969 | 746 | 746 |  |  | -132.6067 | 746 | -0.32969 | -245.9517
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.1787 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.33064 | 162.8 | 162.8 |  |  | -29.0922 | 162.8 | -0.33064 | -53.8275
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.1787 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.33064 | 161.4 | 161.4 |  |  | -28.842 | 161.4 | -0.33064 | -53.3646
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.1787 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.33064 | 158.9 | 158.9 |  |  | -28.3953 | 158.9 | -0.33064 | -52.538
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.1787 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.33064 | 269.2 | 269.2 |  |  | -48.1058 | 269.2 | -0.33064 | -89.0072
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.17885 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.33079 | 744 | 744 |  |  | -133.0644 | 744 | -0.33079 | -246.1055
49803 | EXN_15GT | 1 | Houston | YES | -0.17913 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.17913 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.17913 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.17913 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.17913 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.17913 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.17913 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.17913 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.17913 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.17913 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.17913 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.17979 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.33173 | 0 | 0 |  |  | 0 | 0 | -0.33173 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.18065 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.33259 | 0 | 0 |  |  | 0 | 0 | -0.33259 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.18065 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.33259 | 0 | 0 |  |  | 0 | 0 | -0.33259 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.18088 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.33282 | 107 | 107 |  |  | -19.3541 | 107 | -0.33282 | -35.6113
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.18088 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.33282 | 108 | 108 |  |  | -19.5349 | 108 | -0.33282 | -35.9441
48875 | THW_3132 | A | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049
48875 | THW_3132 | B | Houston | YES | -0.18088 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.33282 | 53 | 53 |  |  | -9.5866 | 53 | -0.33282 | -17.6392
48877 | THW_3334 | C | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049
48877 | THW_3334 | D | Houston | YES | -0.18088 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.33282 | 57 | 57 |  |  | -10.3101 | 57 | -0.33282 | -18.9705
48879 | THW_4142 | E | Houston | YES | -0.18088 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.33282 | 56 | 56 |  |  | -10.1292 | 56 | -0.33282 | -18.6377
48879 | THW_4142 | F | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049
48881 | THW_4344 | G | Houston | YES | -0.18088 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.33282 | 58 | 58 |  |  | -10.491 | 58 | -0.33282 | -19.3033
48881 | THW_4344 | H | Houston | YES | -0.18088 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.33282 | 58 | 58 |  |  | -10.491 | 58 | -0.33282 | -19.3033
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.18206 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.18206 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.18206 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.18206 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.18206 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.18206 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.18206 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.18229 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.33422 | 0 | 0 |  |  | 0 | 0 | -0.33422 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.18272 | 173 | 50 | 173 |  | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.18272 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.18272 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.18272 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.18272 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.18335 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.33529 | 398 | 398 |  |  | -72.9749 | 398 | -0.33529 | -133.4458
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.1846 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.33654 | 12 | 12 |  |  | -2.2152 | 12 | -0.33654 | -4.0385
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ Singleton to Wharton and Singleton to Obrien OL_ Tomball to Singleton |  | i_PTDF_INC_pt | 387 |  | CBE_ST34 | Unit at max
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.1846 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.33654 | 12 | 12 |  |  | -2.2152 | 12 | -0.33654 | -4.0385 | 0.00056694 | 0.00077232 |  |  | i_10pctunit | 42 |  | 167 | # units @ max
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.18335 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.33529 | 398 | 398 |  |  | -72.9749 | 398 | -0.33529 | -133.4458 | 0.019371 | 0.026293 | [5 empty] | 0.12481 | delta max
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.18272 | 173 | 50 | 173 |  | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 | 0.019371 | 0.026293 | [5 empty] | Delta
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.18272 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 | 0.019371 | 0.026293 | Weighted Shift Factors |  |  |  | 1 | 0.00020538
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.18272 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 | 0.019371 | 0.026293 | North | 0.15194 |  |  | 2 | 0.0069222
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.18272 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 | 0.019371 | 0.026293 | Houston | -0.17072 |  |  | 3 | 0.0069222
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.18272 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 | 0.019371 | 0.026293 |  |  |  |  | 4 | 0.0069222
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.18229 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.33422 | 0 | 0 |  |  | 0 | 0 | -0.33422 | 0 | 0.019371 | 0.026293 |  |  |  |  | 5 | 0.0069222
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.18206 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 | 0.019371 | 0.026293 |  |  |  |  | 6 | 0.0069222
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.18206 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 | 0.019371 | 0.026293 |  |  |  |  | 7 | 0.0069222
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.18206 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 | 0.019371 | 0.026293 |  |  |  |  | 8 | 0.0069222
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.18206 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 | 0.019371 | 0.026293 |  |  |  |  | 9 | 0.0069222
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.18206 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 | 0.019371 | 0.026293 |  |  |  |  | 10 | 0.0069222
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.18206 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 | 0.019371 | 0.026293 |  |  |  |  | 11 | 0.0069222
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.18206 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 | 0.019371 | 0.026293 |  |  |  |  | 12 | 0.0069222
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.18088 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.33282 | 107 | 107 |  |  | -19.3541 | 107 | -0.33282 | -35.6113 | 0.024426 | 0.033103 |  |  |  |  | 13 | 0.0069222
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.18088 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.33282 | 108 | 108 |  |  | -19.5349 | 108 | -0.33282 | -35.9441 | 0.029528 | 0.039977 |  |  |  |  | 14 | 0.0069222
48875 | THW_3132 | A | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049 | 0.032127 | 0.043478 |  |  |  |  | 15 | 0.0069222
48875 | THW_3132 | B | Houston | YES | -0.18088 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.33282 | 53 | 53 |  |  | -9.5866 | 53 | -0.33282 | -17.6392 | 0.034631 | 0.046851 |  |  |  |  | 16 | 0.0086773
48877 | THW_3334 | C | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049 | 0.037229 | 0.050352 |  |  |  |  | 17 | 0.010449
48877 | THW_3334 | D | Houston | YES | -0.18088 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.33282 | 57 | 57 |  |  | -10.3101 | 57 | -0.33282 | -18.9705 | 0.039922 | 0.05398 |  |  |  |  | 18 | 0.011351
48879 | THW_4142 | E | Houston | YES | -0.18088 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.33282 | 56 | 56 |  |  | -10.1292 | 56 | -0.33282 | -18.6377 | 0.042568 | 0.057544 |  |  |  |  | 19 | 0.01222
48879 | THW_4142 | F | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049 | 0.045166 | 0.061045 |  |  |  |  | 20 | 0.013123
48881 | THW_4344 | G | Houston | YES | -0.18088 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.33282 | 58 | 58 |  |  | -10.491 | 58 | -0.33282 | -19.3033 | 0.047907 | 0.064736 |  |  |  |  | 21 | 0.014058
48881 | THW_4344 | H | Houston | YES | -0.18088 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.33282 | 58 | 58 |  |  | -10.491 | 58 | -0.33282 | -19.3033 | 0.050647 | 0.068428 |  |  |  |  | 22 | 0.014976
48651 | EP_1_2 | 1 | Houston | YES | -0.18065 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.33259 | 0 | 0 |  |  | 0 | 0 | -0.33259 | 0 | 0.050647 | 0.068428 |  |  |  |  | 23 | 0.015878
48651 | EP_1_2 | 2 | Houston | YES | -0.18065 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.33259 | 0 | 0 |  |  | 0 | 0 | -0.33259 | 0 | 0.050647 | 0.068428 |  |  |  |  | 24 | 0.01683
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.17979 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.33173 | 0 | 0 |  |  | 0 | 0 | -0.33173 | 0 | 0.050647 | 0.068428 |  |  |  |  | 25 | 0.017781
49803 | EXN_15GT | 1 | Houston | YES | -0.17913 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 26 | 0.017781
49804 | EXN_16GT | 2 | Houston | YES | -0.17913 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 27 | 0.017781
49805 | EXN_17GT | 3 | Houston | YES | -0.17913 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 28 | 0.017781
49826 | EXN938GT | 5 | Houston | YES | -0.17913 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 29 | 0.017781
49828 | EXN941GT | 10 | Houston | YES | -0.17913 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 30 | 0.017781
49829 | EXN942GT | 11 | Houston | YES | -0.17913 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 31 | 0.017781
49830 | EXN943GT | 12 | Houston | YES | -0.17913 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 32 | 0.017781
49831 | EXN944GT | 13 | Houston | YES | -0.17913 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 33 | 0.017781
49832 | EXN945GT | 9 | Houston | YES | -0.17913 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 34 | 0.017781
49837 | EXN_GT | 4 | Houston | YES | -0.17913 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 35 | 0.017781
49838 | EXN_14GT | 14 | Houston | YES | -0.17913 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 | 0.050647 | 0.068428 |  |  |  |  | 36 | 0.017781
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.17885 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.33079 | 744 | 744 |  |  | -133.0644 | 744 | -0.33079 | -246.1055 | 0.085797 | 0.11549 |  |  |  |  | 37 | 0.017781
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.1787 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.33064 | 162.8 | 162.8 |  |  | -29.0922 | 162.8 | -0.33064 | -53.8275 | 0.093489 | 0.12579 |  |  |  |  | 38 | 0.017781
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.1787 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.33064 | 161.4 | 161.4 |  |  | -28.842 | 161.4 | -0.33064 | -53.3646 | 0.10111 | 0.13599 |  |  |  |  | 39 | 0.017781
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.1787 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.33064 | 158.9 | 158.9 |  |  | -28.3953 | 158.9 | -0.33064 | -52.538 | 0.10862 | 0.14604 |  |  |  |  | 40 | 0.029696
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.1787 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.33064 | 269.2 | 269.2 |  |  | -48.1058 | 269.2 | -0.33064 | -89.0072 | 0.12134 | 0.16306 |  |  |  |  | 41 | 0.032299
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782 | 0.12947 | 0.17392 |  |  |  |  | 42 | 0.034879
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782 | 0.13759 | 0.18478 |  |  |  |  | 43 | 0.037419
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782 | 0.14572 | 0.19564 |  |  |  |  | 44 | 0.041723
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.17776 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.32969 | 746 | 746 |  |  | -132.6067 | 746 | -0.32969 | -245.9517 | 0.18096 | 0.24268 |  |  |  |  | 45 | 0.044455
48885 | THW_5152 | A | Houston | YES | -0.17751 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.32945 | 58 | 58 |  |  | -10.2958 | 58 | -0.32945 | -19.1081 | 0.1837 | 0.24633 |  |  |  |  | 46 | 0.047188
48885 | THW_5152 | B | Houston | YES | -0.17751 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.32945 | 59 | 59 |  |  | -10.4733 | 59 | -0.32945 | -19.4375 | 0.18649 | 0.25005 |  |  |  |  | 47 | 0.049921
48886 | THW_5354 | C | Houston | YES | -0.17751 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.32945 | 57 | 57 |  |  | -10.1182 | 57 | -0.32945 | -18.7786 | 0.18918 | 0.25364 |  |  |  |  | 48 | 0.061713
48886 | THW_5354 | D | Houston | YES | -0.17751 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.32945 | 58 | 58 |  |  | -10.2958 | 58 | -0.32945 | -19.1081 | 0.19192 | 0.25729 |  |  |  |  | 49 | 0.062627
48887 | THW_5556 | E | Houston | YES | -0.17751 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.32945 | 59 | 59 |  |  | -10.4733 | 59 | -0.32945 | -19.4375 | 0.19471 | 0.26101 |  |  |  |  | 50 | 0.063556
48887 | THW_5556 | F | Houston | YES | -0.17751 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.32945 | 57 | 57 |  |  | -10.1182 | 57 | -0.32945 | -18.7786 | 0.1974 | 0.2646 |  |  |  |  | 51 | 0.064455
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.17653 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.32847 | 0 | 0 |  |  | 0 | 0 | -0.32847 | 0 | 0.1974 | 0.2646 |  |  |  |  | 52 | 0.065369
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.17653 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.32847 | 0 | 0 |  |  | 0 | 0 | -0.32847 | 0 | 0.1974 | 0.2646 |  |  |  |  | 53 | 0.066299
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.1763 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.32823 | 0 | 0 |  |  | 0 | 0 | -0.32823 | 0 | 0.1974 | 0.2646 |  |  |  |  | 54 | 0.067197
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.17606 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.328 | 42 | 42 |  |  | -7.3946 | 42 | -0.328 | -13.776 | 0.19939 | 0.26724 |  |  |  |  | 55 | 0.067197
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.17606 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.328 | 42 | 42 |  |  | -7.3946 | 42 | -0.328 | -13.776 | 0.20137 | 0.26987 |  |  |  |  | 56 | 0.067197
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.17606 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.328 | 39 | 39 |  |  | -6.8665 | 39 | -0.328 | -12.792 | 0.20322 | 0.27232 |  |  |  |  | 57 | 0.067197
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.17606 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.328 | 39 | 39 |  |  | -6.8665 | 39 | -0.328 | -12.792 | 0.20506 | 0.27476 |  |  |  |  | 58 | 0.067847
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.17533 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0 | 0.20506 | 0.27476 |  |  |  |  | 59 | 0.068497
48821 | SHELLG2 | 2 | Houston | YES | -0.17533 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0 | 0.20506 | 0.27476 |  |  |  |  | 60 | 0.069101
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.17533 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0 | 0.20506 | 0.27476 |  |  |  |  | 61 | 0.069705
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.17533 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0 | 0.20506 | 0.27476 |  |  |  |  | 62 | 0.069705
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.17498 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.32691 | 213 | 213 |  |  | -37.2701 | 213 | -0.32691 | -69.6327 | 0.21512 | 0.28808 |  |  |  |  | 63 | 0.069705
48845 | SOL_GT1 | 1 | Houston | YES | -0.17497 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.3269 | 16.2 | 16.2 |  |  | -2.8345 | 16.2 | -0.3269 | -5.2958 | 0.21589 | 0.28909 |  |  |  |  | 64 | 0.069705
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.17496 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0 | 0.21589 | 0.28909 |  |  |  |  | 65 | 0.069705
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.17496 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0 | 0.21589 | 0.28909 |  |  |  |  | 66 | 0.072958
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.17496 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0 | 0.21589 | 0.28909 |  |  |  |  | 67 | 0.073206
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.17496 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0 | 0.21589 | 0.28909 |  |  |  |  | 68 | 0.073206
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.17495 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.32688 | 228 | 228 |  |  | -39.8877 | 228 | -0.32688 | -74.5293 | 0.22666 | 0.30335 |  |  |  |  | 69 | 0.073206
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.17488 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0 | 0.22666 | 0.30335 |  |  |  |  | 70 | 0.073206
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.17488 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0 | 0.22666 | 0.30335 |  |  |  |  | 71 | 0.073206
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.17488 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0 | 0.22666 | 0.30335 |  |  |  |  | 72 | 0.076687
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.17486 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.3268 | 165 | 165 |  |  | -28.8517 | 165 | -0.3268 | -53.9213 | 0.23445 | 0.31366 |  |  |  |  | 73 | 0.076687
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.17483 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.32677 | 176 | 176 |  |  | -30.7706 | 176 | -0.32677 | -57.5115 | 0.24277 | 0.32466 |  |  |  |  | 74 | 0.076687
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.17481 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.32675 | 0 | 0 |  |  | 0 | 0 | -0.32675 | 0 | 0.24277 | 0.32466 |  |  |  |  | 75 | 0.076687
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.17481 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.32675 | 0 | 0 |  |  | 0 | 0 | -0.32675 | 0 | 0.24277 | 0.32466 |  |  |  |  | 76 | 0.079203
48855 | SRB_GT211035 | B1 | Houston | YES | -0.17481 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.32675 | 18 | 18 |  |  | -3.1466 | 18 | -0.32675 | -5.8814 | 0.24362 | 0.32578 |  |  |  |  | 77 | 0.081887
48855 | SRB_GT211035 | B2 | Houston | YES | -0.17481 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.32675 | 12 | 12 |  |  | -2.0977 | 12 | -0.32675 | -3.921 | 0.24419 | 0.32653 |  |  |  |  | 78 | 0.081887
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.17439 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.32633 | 0 | 0 |  |  | 0 | 0 | -0.32633 | 0 | 0.24419 | 0.32653 |  |  |  |  | 79 | 0.081887
48691 | GBY_73741085 | A | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179 | 0.24641 | 0.32946 |  |  |  |  | 80 | 0.082161
48691 | GBY_73741085 | B | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179 | 0.24863 | 0.33239 |  |  |  |  | 81 | 0.082344
48692 | GBY_81821075 | C | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179 | 0.25085 | 0.33532 |  |  |  |  | 82 | 0.082344
48692 | GBY_81821075 | D | Houston | YES | -0.17398 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.32591 | 55 | 55 |  |  | -9.5687 | 55 | -0.32591 | -17.9252 | 0.25345 | 0.33875 |  |  |  |  | 83 | 0.083053
48693 | GBY_83841065 | E | Houston | YES | -0.17398 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.32591 | 57 | 57 |  |  | -9.9166 | 57 | -0.32591 | -18.577 | 0.25614 | 0.3423 |  |  |  |  | 84 | 0.083762
48693 | GBY_83841065 | F | Houston | YES | -0.17398 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.32591 | 54 | 54 |  |  | -9.3947 | 54 | -0.32591 | -17.5993 | 0.25869 | 0.34567 |  |  |  |  | 85 | 0.084471
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.17391 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.32585 | 0 | 0 |  |  | 0 | 0 | -0.32585 | 0 | 0.25869 | 0.34567 |  |  |  |  | 86 | 0.0853
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.17391 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.32585 | 0 | 0 |  |  | 0 | 0 | -0.32585 | 0 | 0.25869 | 0.34567 |  |  |  |  | 87 | 0.08616
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.1726 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.32454 | 163.2 | 163.2 |  |  | -28.1685 | 163.2 | -0.32454 | -52.9646 | 0.2664 | 0.35579 |  |  |  |  | 88 | 0.086975
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.1726 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.32454 | 157.1 | 157.1 |  |  | -27.1156 | 157.1 | -0.32454 | -50.9849 | 0.27382 | 0.36554 |  |  |  |  | 89 | 0.086975
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.1726 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.32454 | 157.5 | 157.5 |  |  | -27.1847 | 157.5 | -0.32454 | -51.1147 | 0.28126 | 0.37532 |  |  |  |  | 90 | 0.086975
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.1726 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.32454 | 157 | 157 |  |  | -27.0984 | 157 | -0.32454 | -50.9525 | 0.28868 | 0.38506 |  |  |  |  | 91 | 0.089393
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.1726 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.32454 | 282 | 282 |  |  | -48.6735 | 282 | -0.32454 | -91.5197 | 0.30201 | 0.40257 |  |  |  |  | 92 | 0.091721
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.17223 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0 | 0.30201 | 0.40257 |  |  |  |  | 93 | 0.094056
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.17223 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0 | 0.30201 | 0.40257 |  |  |  |  | 94 | 0.096382
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.17223 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0 | 0.30201 | 0.40257 |  |  |  |  | 95 | 0.10056
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.17223 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0 | 0.30201 | 0.40257 |  |  |  |  | 96 | 0.10056
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.17133 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 | 0.30201 | 0.40257 |  |  |  |  | 97 | 0.10056
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.17133 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 | 0.30201 | 0.40257 |  |  |  |  | 98 | 0.10056
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.17133 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 | 0.30201 | 0.40257 |  |  |  |  | 99 | 0.10056
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.17133 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 | 0.30201 | 0.40257 |  |  |  |  | 100 | 0.10056
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.17133 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 | 0.30201 | 0.40257 |  |  |  |  | 101 | 0.10056
48772 | PHR_GN2_2 | MB | Houston | YES | -0.169 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.32093 | 0 | 0 |  |  | 0 | 0 | -0.32093 | 0 | 0.30201 | 0.40257 |  |  |  |  | 102 | 0.10056
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.16573 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 103 | 0.10056
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.16573 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 104 | 0.10056
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.16573 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 105 | 0.10056
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.16573 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 106 | 0.10056
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.16573 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 107 | 0.10056
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.16573 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 108 | 0.10056
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.16573 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 109 | 0.10056
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.16573 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 110 | 0.10056
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.16573 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 111 | 0.10056
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.16573 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 112 | 0.10056
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.16573 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 113 | 0.10056
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.16573 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 114 | 0.10056
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.16573 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 115 | 0.10056
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.16573 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 116 | 0.10056
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.16573 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 | 0.30201 | 0.40257 |  |  |  |  | 117 | 0.10056
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.1608 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.31274 | 166 | 166 |  |  | -26.6933 | 166 | -0.31274 | -51.9148 | 0.30985 | 0.41249 |  |  |  |  | 118 | 0.10056
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.1608 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.31274 | 166 | 166 |  |  | -26.6933 | 166 | -0.31274 | -51.9148 | 0.31769 | 0.42242 |  |  |  |  | 119 | 0.10056
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.1608 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.31274 | 248 | 248 |  |  | -39.8791 | 248 | -0.31274 | -77.5595 | 0.32941 | 0.43726 |  |  |  |  | 120 | 0.10056
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.1608 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.31274 | 546 | 546 |  |  | -87.7984 | 546 | -0.31274 | -170.756 | 0.3552 | 0.46991 |  |  |  |  | 121 | 0.10265
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.1608 | 607.1 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.31274 | 0 | 654 |  |  | 0 | 0 | -0.31274 | 0 | 0.3552 | 0.46991 |  |  |  |  | 122 | 0.10473
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.1608 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.31274 | 13 | 13 |  |  | -2.0904 | 13 | -0.31274 | -4.0656 | 0.35582 | 0.47069 |  |  |  |  | 123 | 0.10785
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.15966 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.31159 | 0 | 0 |  |  | 0 | 0 | -0.31159 | 0 | 0.35582 | 0.47069 |  |  |  |  | 124 | 0.11471
48730 | MNS_GT | 1 | Houston | YES | -0.15817 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.3101 | 0 | 0 |  |  | 0 | 0 | -0.3101 | 0 | 0.35582 | 0.47069 |  |  |  |  | 125 | 0.11471
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.1555 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.30744 | 167.7 | 167.7 |  |  | -26.0773 | 167.7 | -0.30744 | -51.5572 | 0.36374 | 0.48055 |  |  |  |  | 126 | 0.11487
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.1555 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.30744 | 166.4 | 166.4 |  |  | -25.8752 | 166.4 | -0.30744 | -51.1575 | 0.3716 | 0.49033 |  |  |  |  | 127 | 0.11487
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.1555 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.30744 | 252.4 | 252.4 |  |  | -39.2482 | 252.4 | -0.30744 | -77.5971 | 0.38353 | 0.50517 |  |  |  |  | 128 | 0.11487
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.1554 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 651 |  |  | 0 | 0 | -0.30733 | 0 | 0.38353 | 0.50517 |  |  |  |  | 129 | 0.11681
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.1554 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 564 |  |  | 0 | 0 | -0.30733 | 0 | 0.38353 | 0.50517 |  |  |  |  | 130 | 0.11873
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.1554 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 603 |  |  | 0 | 0 | -0.30733 | 0 | 0.38353 | 0.50517 |  |  |  |  | 131 | 0.12165
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.14876 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0 | 0.38353 | 0.50517 |  |  |  |  | 132 | 0.12165
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.14876 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0 | 0.38353 | 0.50517 |  |  |  |  | 133 | 0.12165
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.14876 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0 | 0.38353 | 0.50517 |  |  |  |  | 134 | 0.12165
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.14876 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0 | 0.38353 | 0.50517 |  |  |  |  | 135 | 0.12165
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.14503 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.29697 | 0 | 0 |  |  | 0 | 0 | -0.29697 | 0 | 0.38353 | 0.50517 |  |  |  |  | 136 | 0.12165
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.14503 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.29697 | 0 | 0 |  |  | 0 | 0 | -0.29697 | 0 | 0.38353 | 0.50517 |  |  |  |  | 137 | 0.12165
49851 | DOW17000 | 37 | Houston | YES | -0.14065 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 138 | 0.12165
49858 | DOW38100 | 31 | Houston | YES | -0.14065 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 139 | 0.12165
49859 | DOW38200 | 33 | Houston | YES | -0.14065 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 140 | 0.12165
49860 | DOW38300 | 32 | Houston | YES | -0.14065 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 141 | 0.12165
49862 | DOW39100 | 36 | Houston | YES | -0.14065 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 142 | 0.12165
49863 | DOW39200 | 35 | Houston | YES | -0.14065 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 143 | 0.12165
49865 | DOW41000 | 41 | Houston | YES | -0.14065 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 144 | 0.12165
49866 | DOW42000 | 42 | Houston | YES | -0.14065 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 145 | 0.12165
49869 | DOW49000 | 45 | Houston | YES | -0.14065 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 146 | 0.12165
49870 | DOW61000 | 61 | Houston | YES | -0.14065 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 147 | 0.12165
49871 | DOW62000 | 62 | Houston | YES | -0.14065 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 148 | 0.12165
49872 | DOW63000 | 63 | Houston | YES | -0.14065 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 149 | 0.12165
49873 | DOW64000 | 64 | Houston | YES | -0.14065 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 150 | 0.12165
49876 | DOW65000 | 65 | Houston | YES | -0.14065 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 151 | 0.12165
49877 | DOW66000 | 66 | Houston | YES | -0.14065 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 152 | 0.12165
49878 | DOW67000 | 67 | Houston | YES | -0.14065 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 153 | 0.12165
49882 | DOW81000 | 81 | Houston | YES | -0.14065 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 154 | 0.12165
49884 | DOW82000 | 82 | Houston | YES | -0.14065 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 155 | 0.12165
49885 | DOW83000 | 83 | Houston | YES | -0.14065 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 156 | 0.12165
49886 | DOW84000 | 84 | Houston | YES | -0.14065 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 | 0.38353 | 0.50517 |  |  |  |  | 157 | 0.12165
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.13008 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.28202 | 0 | 0 |  |  | 0 | 0 | -0.28202 | 0 | 0.38353 | 0.50517 |  |  |  |  | 158 | 0.12165
48731 | CBE_GT1 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253 | 0.38712 | 0.50923 |  |  |  |  | 159 | 0.12165
48732 | CBE_GT2 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253 | 0.39071 | 0.51329 |  |  |  |  | 160 | 0.12165
48733 | CBE_ST12 | 1 | Houston | YES | -0.12734 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.27928 | 105 | 105 |  |  | -13.371 | 105 | -0.27928 | -29.3244 | 0.39567 | 0.5189 |  |  |  |  | 161 | 0.12165
48734 | CBE_GT3 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253 | 0.39926 | 0.52296 |  |  |  |  | 162 | 0.12211
48735 | CBE_GT4 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253 | 0.40285 | 0.52702 |  |  |  |  | 163 | 0.12258
48736 | CBE_ST34 | 1 | Houston | YES | -0.12734 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.27928 | 105 | 105 |  |  | -13.371 | 105 | -0.27928 | -29.3244 | 0.40781 | 0.53262 |  |  |  |  | 164 | 0.12323
5911 | STP_GN1___1 | 1 | Houston | YES | -0.12209 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.27403 | 0 | 0 |  |  | 0 | 0 | -0.27403 | 0 | 0.40781 | 0.53262 |  |  |  |  | 165 | 0.1237
5912 | STP_GN2___2 | 2 | Houston | YES | -0.12209 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.27403 | 0 | 0 |  |  | 0 | 0 | -0.27403 | 0 | 0.40781 | 0.53262 |  |  |  |  | 166 | 0.12417
8134 | FOR #1 | 1 | South | YES | -0.085582 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 167 | 0.12481
8138 | FOR #2 | 2 | South | YES | -0.085582 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 168 | 0.12481
8153 | FOR #3 | 3 | South | YES | -0.085582 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 169 | 0.12481
8154 | FOR #4 | 4 | South | YES | -0.085582 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 170 | 0.12481
8155 | FOR #5 | 5 | South | YES | -0.085582 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 171 | 0.12481
8156 | FOR #6 | 6 | South | YES | -0.085582 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 172 | 0.12481
8157 | FOR #7 | 7 | South | YES | -0.085582 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 173 | 0.12481
80051 | FOR #8 | 8 | South | YES | -0.085582 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 174 | 0.12481
80052 | FOR #9 | 9 | South | YES | -0.085582 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 175 | 0.12481
80053 | FOR #10 | 10 | South | YES | -0.085582 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 | 0.40781 | 0.53262 |  |  |  |  | 176 | 0.12481
80226 | ALCOA G | 1 | South | YES | -0.084515 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.23645 | 0 | 0 |  |  |  |  | -0.23645 | 0 | 0.40781 | 0.53262 |  |  |  |  | 177 | 0.12481
8147 | UCAR #2 | 10 | South | YES | -0.080967 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 | 0.40781 | 0.53262 |  |  |  |  | 178 | 0.12481
8148 | UCAR #1 | 2 | South | YES | -0.080967 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 | 0.40781 | 0.53262 |  |  |  |  | 179 | 0.12481
80137 | CSDR89 | 8 | South | YES | -0.080967 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 | 0.40781 | 0.53262 |  |  |  |  | 180 | 0.12481
80137 | CSDR89 | 9 | South | YES | -0.080967 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 | 0.40781 | 0.53262 |  |  |  |  | 181 | 0.12481
80138 | CSDR7 | 7 | South | YES | -0.080967 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 | 0.40781 | 0.53262 |  |  |  |  | 182 | 0.12481
80139 | CSDR56 | 5 | South | YES | -0.080967 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 | 0.40781 | 0.53262 |  |  |  |  | 183 | 0.12481
80139 | CSDR56 | 6 | South | YES | -0.080967 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 | 0.40781 | 0.53262 |  |  |  |  | 184 | 0.12481
80140 | CSDR11 | 11 | South | YES | -0.080967 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 | 0.40781 | 0.53262 |  |  |  |  | 185 | 0.12481
80227 | AIRCO G | 1 | South | YES | -0.080386 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.23232 | 0 | 0 |  |  |  |  | -0.23232 | 0 | 0.40781 | 0.53262 |  |  |  |  | 186 | 0.12481
80224 | VISTRONG1 | 1 | South | YES | -0.079573 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.23151 | 0 | 0 |  |  |  |  | -0.23151 | 0 | 0.40781 | 0.53262 |  |  |  |  | 187 | 0.12481
80225 | VISTRONG2 | 2 | South | YES | -0.079573 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.23151 | 0 | 0 |  |  |  |  | -0.23151 | 0 | 0.40781 | 0.53262 |  |  |  |  | 188 | 0.12481
5503 | RAYBURNGEN3 | 1 | South | YES | -0.077767 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.2297 | 22 | 22 |  |  |  |  | -0.2297 | -5.0535 | 0.40885 | 0.53359 |  |  |  |  | 189 | 0.12481
5505 | RAYBURNGEN1 | 1 | South | YES | -0.077767 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.2297 | 11 | 11 |  |  |  |  | -0.2297 | -2.5267 | 0.40937 | 0.53407 |  |  |  |  | 190 | 0.12481
5506 | RAYBURNGEN2 | 1 | South | YES | -0.077767 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.2297 | 11 | 11 |  |  |  |  | -0.2297 | -2.5267 | 0.40989 | 0.53456 |  |  |  |  | 191 | 0.12481
8066 | DUP1V#1 | 1 | South | YES | -0.077236 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.22917 | 0 | 0 |  |  |  |  | -0.22917 | 0 | 0.40989 | 0.53456 |  |  |  |  | 192 | 0.12474
5508 | RAYBURNCC9 | 1 | South | YES | -0.077106 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.22904 | 47.7 | 47.7 |  |  |  |  | -0.22904 | -10.9253 | 0.41214 | 0.53665 |  |  |  |  | 193 | 0.1247
5509 | RAYBURNCC10 | 1 | South | YES | -0.077106 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.22904 | 37.3 | 37.3 |  |  |  |  | -0.22904 | -8.5433 | 0.41391 | 0.53828 |  |  |  |  | 194 | 0.12467
5511 | RAYBURNCC7 | 1 | South | YES | -0.077106 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.22904 | 47.5 | 47.5 |  |  |  |  | -0.22904 | -10.8795 | 0.41615 | 0.54036 |  |  |  |  | 195 | 0.12467
5512 | RAYBURNCC8 | 1 | South | YES | -0.077106 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.22904 | 49.3 | 49.3 |  |  |  |  | -0.22904 | -11.2918 | 0.41848 | 0.54252 |  |  |  |  | 196 | 0.1245
8173 | VICEC51A | 5 | South | YES | -0.075848 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.22778 | 144 | 144 |  |  |  |  | -0.22778 | -32.801 | 0.42528 | 0.54879 |  |  |  |  | 197 | 0.12438
8174 | VICEC61A | 6 | South | YES | -0.075848 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.22778 | 188 | 188 |  |  |  |  | -0.22778 | -42.8236 | 0.43416 | 0.55698 |  |  |  |  | 198 | 0.12421
8926 | LGE_GT10A | 1 | South | YES | -0.074954 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 | 0.43416 | 0.55698 |  |  |  |  | 199 | 0.12404
8927 | LGE_GT20A | 2 | South | YES | -0.074954 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 | 0.43416 | 0.55698 |  |  |  |  | 200 | 0.12351
8928 | LGE_STG0A | 3 | South | YES | -0.074954 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 | 0.43416 | 0.55698 |  |  |  |  | 201 | 0.12282
8930 | ICPGN10A | 1 | South | YES | -0.074954 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 | 0.43416 | 0.55698 |  |  |  |  | 202 | 0.12282
8931 | ICPGN20A | 2 | South | YES | -0.074954 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 | 0.43416 | 0.55698 |  |  |  |  | 203 | 0.12282
8932 | ICPGN30A | 3 | South | YES | -0.074954 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 | 0.43416 | 0.55698 |  |  |  |  | 204 | 0.12282
80223 | REYSHR G | 1 | South | YES | -0.074954 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 | 0.43416 | 0.55698 |  |  |  |  | 205 | 0.12282
8442 | NBEC7 | 7 | South | YES | -0.073507 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.22544 | 367 | 367 |  |  |  |  | -0.22544 | -82.7379 | 0.4515 | 0.57281 |  |  |  |  | 206 | 0.12282
8442 | NBEC7 | MB | South | YES | -0.073507 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.22544 | 0 | 0 |  |  |  |  | -0.22544 | 0 | 0.4515 | 0.57281 |  |  |  |  | 207 | 0.12282
8560 | CNOPGT1 | 1 | South | YES | -0.07349 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0 | 0.4515 | 0.57281 |  |  |  |  | 208 | 0.12282
8561 | CNOPGT2 | 2 | South | YES | -0.07349 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0 | 0.4515 | 0.57281 |  |  |  |  | 209 | 0.1213
8562 | CNOPST1 | 3 | South | YES | -0.07349 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0 | 0.4515 | 0.57281 |  |  |  |  | 210 | 0.1213
8456 | COSW#1 | 1 | South | YES | -0.07341 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.22535 | 0 | 0 |  |  |  |  | -0.22535 | 0 | 0.4515 | 0.57281 |  |  |  |  | 211 | 0.1213
8457 | COSW#2 | 2 | South | YES | -0.07341 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.22535 | 0 | 0 |  |  |  |  | -0.22535 | 0 | 0.4515 | 0.57281 |  |  |  |  | 212 | 0.1213
8459 | B_DAVIS0B | MB | South | YES | -0.073242 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.22518 | 0 | 0 |  |  |  |  | -0.22518 | 0 | 0.4515 | 0.57281 |  |  |  |  | 213 | 0.1213
8460 | B_DAVIS0A | MB | South | YES | -0.073242 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.22518 | 0 | 0 |  |  |  |  | -0.22518 | 0 | 0.4515 | 0.57281 |  |  |  |  | 214 | 0.1213
80263 | B_DAVIS31A | 3 | South | YES | -0.073242 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.22518 | 180 | 180 |  |  |  |  | -0.22518 | -40.5322 | 0.46001 | 0.58056 |  |  |  |  | 215 | 0.1213
80264 | B_DAVIS41A | 4 | South | YES | -0.073242 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.22518 | 180 | 180 |  |  |  |  | -0.22518 | -40.5322 | 0.46851 | 0.58831 |  |  |  |  | 216 | 0.1213
8506 | VAL #1 | 1 | South | YES | -0.073101 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.22504 | 0 | 0 |  |  |  |  | -0.22504 | 0 | 0.46851 | 0.58831 |  |  |  |  | 217 | 0.1213
8507 | VAL #2 | 2 | South | YES | -0.073101 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.22504 | 0 | 0 |  |  |  |  | -0.22504 | 0 | 0.46851 | 0.58831 |  |  |  |  | 218 | 0.12055
8511 | OXY_CC0A | 1 | South | YES | -0.07299 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.22493 | 0 | 0 |  |  |  |  | -0.22493 | 0 | 0.46851 | 0.58831 |  |  |  |  | 219 | 0.1198
8461 | KOCH_UP0A | 1 | South | YES | -0.072936 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.22487 | 0 | 0 |  |  |  |  | -0.22487 | 0 | 0.46851 | 0.58831 |  |  |  |  | 220 | 0.1198
8517 | CELANEBI0A | 1 | South | YES | -0.072335 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.22427 | 0 | 0 |  |  |  |  | -0.22427 | 0 | 0.46851 | 0.58831 |  |  |  |  | 221 | 0.1198
80080 | GWINDT11A | 1 | South | YES | -0.072238 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 94 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 222 | 0.1198
80080 | GWINDT11A | 2 | South | YES | -0.072238 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 41 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 223 | 0.1198
80080 | GWINDT11A | 3 | South | YES | -0.072238 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 38 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 224 | 0.1198
80080 | GWINDT11A | 4 | South | YES | -0.072238 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 19 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 225 | 0.1198
80081 | GWINDT21A | 1 | South | YES | -0.072238 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 94 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 226 | 0.1198
80081 | GWINDT21A | 2 | South | YES | -0.072238 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 36 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 227 | 0.1198
80081 | GWINDT21A | 3 | South | YES | -0.072238 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 43 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 228 | 0.1198
80081 | GWINDT21A | 4 | South | YES | -0.072238 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 22 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 229 | 0.1198
80180 | PNSCALT11A | 1 | South | YES | -0.072238 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 148 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 230 | 0.1198
80180 | PNSCALT11A | 2 | South | YES | -0.072238 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 50 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 231 | 0.1198
80181 | PNSCALT21A | 1 | South | YES | -0.072238 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 55 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 232 | 0.1198
80181 | PNSCALT21A | 2 | South | YES | -0.072238 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 50 |  |  |  |  | -0.22417 | 0 | 0.46851 | 0.58831 |  |  |  |  | 233 | 0.1198
5932 | SI_RAY9 | 9 | South | YES | -0.072036 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.22397 | 38 | 38 |  |  |  |  | -0.22397 | -8.511 | 0.47031 | 0.58994 |  |  |  |  | 234 | 0.1198
5933 | SI_RAY6 | 6 | South | YES | -0.072036 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.22397 | 19.3 | 19.3 |  |  |  |  | -0.22397 | -4.3227 | 0.47122 | 0.59076 |  |  |  |  | 235 | 0.1198
5935 | SI_RAY10 | 10 | South | YES | -0.072036 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.22397 | 47 | 47 |  |  |  |  | -0.22397 | -10.5267 | 0.47344 | 0.59278 |  |  |  |  | 236 | 0.1198
80003 | MILHWYS | F | South | YES | -0.072035 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.22397 | 0 | 0 |  |  |  |  | -0.22397 | 0 | 0.47344 | 0.59278 |  |  |  |  | 237 | 0.11963
8936 | MVGN#1 | 1 | South | YES | -0.071704 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.22364 | 216.6 | 216.6 |  |  |  |  | -0.22364 | -48.4406 | 0.48367 | 0.60204 |  |  |  |  | 238 | 0.11955
8937 | MVGN#2 | 2 | South | YES | -0.071704 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.22364 | 216.7 | 216.7 |  |  |  |  | -0.22364 | -48.463 | 0.49391 | 0.61131 |  |  |  |  | 239 | 0.11934
8938 | MVGN#3 | 3 | South | YES | -0.071704 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.22364 | 250.9 | 250.9 |  |  |  |  | -0.22364 | -56.1115 | 0.50576 | 0.62204 |  |  |  |  | 240 | 0.11934
8981 | HECN1 | 1 | South | YES | -0.071702 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.22364 | 144.8 | 144.8 |  |  |  |  | -0.22364 | -32.3829 | 0.51261 | 0.62823 |  |  |  |  | 241 | 0.11837
8982 | HECN2 | 2 | South | YES | -0.071702 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.22364 | 144.1 | 144.1 |  |  |  |  | -0.22364 | -32.2264 | 0.51941 | 0.6344 |  |  |  |  | 242 | 0.1174
8983 | HECN3 | 3 | South | YES | -0.071702 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.22364 | 171.9 | 171.9 |  |  |  |  | -0.22364 | -38.4435 | 0.52753 | 0.64175 |  |  |  |  | 243 | 0.11628
8933 | FGNTS001 | 1 | South | YES | -0.070946 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.22288 | 146.5 | 146.5 |  |  |  |  | -0.22288 | -32.6523 | 0.53446 | 0.64799 |  |  |  |  | 244 | 0.11563
8934 | FGNTS101 | 2 | South | YES | -0.070946 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.22288 | 147.9 | 147.9 |  |  |  |  | -0.22288 | -32.9644 | 0.54144 | 0.6543 |  |  |  |  | 245 | 0.11498
8935 | FGNTS201 | 3 | South | YES | -0.070946 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.22288 | 173 | 173 |  |  |  |  | -0.22288 | -38.5587 | 0.54962 | 0.66167 |  |  |  |  | 246 | 0.11421
8161 | COLETO0A | 1 | South | YES | -0.068894 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.22083 | 0 | 633 |  |  |  |  | -0.22083 | 0 | 0.54962 | 0.66167 |  |  |  |  | 247 | 0.11354
88508 | FALFURRI | F | South | YES | -0.067258 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.21919 | 0 | 0 |  |  |  |  | -0.21919 | 0 | 0.54962 | 0.66167 |  |  |  |  | 248 | 0.11285
5728 | FALCONHYDRO2 | 2 | South | YES | -0.066451 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0 | 0.54962 | 0.66167 |  |  |  |  | 249 | 0.11205
5729 | FALCONHYDRO3 | 3 | South | YES | -0.066451 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0 | 0.54962 | 0.66167 |  |  |  |  | 250 | 0.11205
8048 | FALCONHYDRO1 | 1 | South | YES | -0.066451 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0 | 0.54962 | 0.66167 |  |  |  |  | 251 | 0.11205
88198 | BEEVILLE | F | South | YES | -0.065317 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.21725 | 0 | 0 |  |  |  |  | -0.21725 | 0 | 0.54962 | 0.66167 |  |  |  |  | 252 | 0.11205
88299 | ZAPATA | F | South | YES | -0.062149 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.21409 | 0 | 0 |  |  |  |  | -0.21409 | 0 | 0.54962 | 0.66167 |  |  |  |  | 253 | 0.11205
80012 | LAR | F | South | YES | -0.055808 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.20774 | 0 | 0 |  |  |  |  | -0.20774 | 0 | 0.54962 | 0.66167 |  |  |  |  | 254 | 0.11205
80265 | LARECU40A | 4 | South | YES | -0.055804 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.20774 | 100 | 100 |  |  |  |  | -0.20774 | -20.7741 | 0.55434 | 0.66564 |  |  |  |  | 255 | 0.11205
80266 | LARECU50A | 5 | South | YES | -0.055804 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.20774 | 100 | 100 |  |  |  |  | -0.20774 | -20.7741 | 0.55907 | 0.66962 |  |  |  |  | 256 | 0.11205
5903 | SANMIGUELGEN | 1 | South | YES | -0.055475 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.20741 | 0 | 396.3 |  |  |  |  | -0.20741 | 0 | 0.55907 | 0.66962 |  |  |  |  | 257 | 0.11205
8189 | CUECPL2A | 1 | South | YES | -0.053362 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.2053 | 0 | 0 |  |  |  |  | -0.2053 | 0 | 0.55907 | 0.66962 |  |  |  |  | 258 | 0.1113
5401 | CALAVER_JKS1 | 1 | South | YES | -0.04973 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.20167 | 0 | 562 |  |  |  |  | -0.20167 | 0 | 0.55907 | 0.66962 |  |  |  |  | 259 | 0.11055
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.04861 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.20055 | 155 | 155 |  |  |  |  | -0.20055 | -31.0848 | 0.56639 | 0.67556 |  |  |  |  | 260 | 0.11055
5477 | BRA_AVR1_ST | 1 | South | YES | -0.04861 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.20055 | 174 | 174 |  |  |  |  | -0.20055 | -34.8952 | 0.57461 | 0.68223 |  |  |  |  | 261 | 0.11055
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.04861 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.20055 | 155 | 155 |  |  |  |  | -0.20055 | -31.0848 | 0.58193 | 0.68818 |  |  |  |  | 262 | 0.11055
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.047121 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.19906 | 215 | 215 |  |  |  |  | -0.19906 | -42.7975 | 0.59209 | 0.69636 |  |  |  |  | 263 | 0.10917
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.047121 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.19906 | 216 | 216 |  |  |  |  | -0.19906 | -42.9965 | 0.6023 | 0.70459 |  |  |  |  | 264 | 0.10762
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.046999 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.19894 | 61 | 61 |  |  |  |  | -0.19894 | -12.1351 | 0.60518 | 0.70691 |  |  |  |  | 265 | 0.10625
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.046999 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.19894 | 95 | 95 |  |  |  |  | -0.19894 | -18.8989 | 0.60967 | 0.71052 |  |  |  |  | 266 | 0.10427
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.046999 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.19894 | 151 | 151 |  |  |  |  | -0.19894 | -30.0393 | 0.6168 | 0.71627 |  |  |  |  | 267 | 0.10229
5264 | LEON_LCP3G3 | 3 | South | YES | -0.046973 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.19891 | 58 | 58 |  |  |  |  | -0.19891 | -11.5368 | 0.61954 | 0.71847 |  |  |  |  | 268 | 0.10173
5265 | LEON_LCP4G4 | 4 | South | YES | -0.046973 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.19891 | 89 | 89 |  |  |  |  | -0.19891 | -17.703 | 0.62374 | 0.72186 |  |  |  |  | 269 | 0.10086
5266 | LEON_LCPCT1 | 1 | South | YES | -0.046973 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.19891 | 44 | 44 |  |  |  |  | -0.19891 | -8.752 | 0.62582 | 0.72353 |  |  |  |  | 270 | 0.099466
5267 | LEON_LCPCT2 | 2 | South | YES | -0.046973 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.19891 | 44 | 44 |  |  |  |  | -0.19891 | -8.752 | 0.6279 | 0.72521 |  |  |  |  | 271 | 0.098932
5268 | LEON_LCPCT3 | 3 | South | YES | -0.046973 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.19891 | 43 | 43 |  |  |  |  | -0.19891 | -8.5531 | 0.62993 | 0.72684 |  |  |  |  | 272 | 0.098113
5269 | LEON_LCPCT4 | 4 | South | YES | -0.046973 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.19891 | 45 | 45 |  |  |  |  | -0.19891 | -8.9509 | 0.63206 | 0.72855 |  |  |  |  | 273 | 0.097708
5396 | CALAVER_OWS1 | 1 | South | YES | -0.046953 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.19889 | 418 | 418 |  |  |  |  | -0.19889 | -83.136 | 0.65181 | 0.74445 |  |  |  |  | 274 | 0.097303
5397 | CALAVER_OWS2 | 2 | South | YES | -0.046953 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.19889 | 400 | 400 |  |  |  |  | -0.19889 | -79.556 | 0.67071 | 0.75967 |  |  |  |  | 275 | 0.096907
5111 | CALAVER_JTD1 | 1 | South | YES | -0.046951 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.19889 | 0 | 430 |  |  |  |  | -0.19889 | 0 | 0.67071 | 0.75967 |  |  |  |  | 276 | 0.096493
5112 | CALAVER_JTD2 | 2 | South | YES | -0.046951 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.19889 | 0 | 430 |  |  |  |  | -0.19889 | 0 | 0.67071 | 0.75967 |  |  |  |  | 277 | 0.092644
5890 | PEARSALLGEN1 | 1 | South | YES | -0.046925 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.19886 | 24 | 24 |  |  |  |  | -0.19886 | -4.7727 | 0.67184 | 0.76058 |  |  |  |  | 278 | 0.08896
5891 | PEARSALLGEN2 | 1 | South | YES | -0.046925 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.19886 | 24.3 | 24.3 |  |  |  |  | -0.19886 | -4.8323 | 0.67299 | 0.7615 |  |  |  |  | 279 | 0.08896
5892 | PEARSALLGEN3 | 1 | South | YES | -0.046925 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.19886 | 23.9 | 23.9 |  |  |  |  | -0.19886 | -4.7528 | 0.67412 | 0.76241 |  |  |  |  | 280 | 0.08896
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.046913 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.19885 | 407 | 407 |  |  |  |  | -0.19885 | -80.9319 | 0.69335 | 0.77789 |  |  |  |  | 281 | 0.088739
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.045929 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.19787 | 147 | 147 |  |  |  |  | -0.19787 | -29.0863 | 0.70029 | 0.78345 |  |  |  |  | 282 | 0.088515
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.045929 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.19787 | 138 | 138 |  |  |  |  | -0.19787 | -27.3055 | 0.70681 | 0.78867 |  |  |  |  | 283 | 0.088295
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.045929 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.19787 | 146 | 146 |  |  |  |  | -0.19787 | -28.8884 | 0.71371 | 0.7942 |  |  |  |  | 284 | 0.084543
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.045929 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.19787 | 149 | 149 |  |  |  |  | -0.19787 | -29.482 | 0.72075 | 0.79984 |  |  |  |  | 285 | 0.083161
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.045929 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.19787 | 182 | 182 |  |  |  |  | -0.19787 | -36.0116 | 0.72935 | 0.80672 |  |  |  |  | 286 | 0.081863
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.045929 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.19787 | 203 | 203 |  |  |  |  | -0.19787 | -40.1668 | 0.73894 | 0.81441 |  |  |  |  | 287 | 0.08049
58909 | PEARSALLSCG1 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.73933 | 0.81472 |  |  |  |  | 288 | 0.079088
58909 | PEARSALLSCG1 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.73973 | 0.81504 |  |  |  |  | 289 | 0.077377
58909 | PEARSALLSCG1 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74013 | 0.81535 |  |  |  |  | 290 | 0.075468
58909 | PEARSALLSCG1 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74052 | 0.81567 |  |  |  |  | 291 | 0.075386
58909 | PEARSALLSCG1 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74092 | 0.81598 |  |  |  |  | 292 | 0.075305
58909 | PEARSALLSCG1 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74132 | 0.8163 |  |  |  |  | 293 | 0.075224
58919 | PEARSALLSCG2 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74172 | 0.81662 |  |  |  |  | 294 | 0.075143
58919 | PEARSALLSCG2 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74211 | 0.81693 |  |  |  |  | 295 | 0.075062
58919 | PEARSALLSCG2 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74251 | 0.81725 |  |  |  |  | 296 | 0.074981
58919 | PEARSALLSCG2 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74291 | 0.81756 |  |  |  |  | 297 | 0.074899
58919 | PEARSALLSCG2 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.7433 | 0.81788 |  |  |  |  | 298 | 0.074818
58919 | PEARSALLSCG2 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.7437 | 0.81819 |  |  |  |  | 299 | 0.074737
58929 | PEARSALLSCG3 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.7441 | 0.81851 |  |  |  |  | 300 | 0.074656
58929 | PEARSALLSCG3 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74449 | 0.81882 |  |  |  |  | 301 | 0.074575
58929 | PEARSALLSCG3 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74489 | 0.81914 |  |  |  |  | 302 | 0.074494
58929 | PEARSALLSCG3 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74529 | 0.81946 |  |  |  |  | 303 | 0.074412
58929 | PEARSALLSCG3 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74568 | 0.81977 |  |  |  |  | 304 | 0.074331
58929 | PEARSALLSCG3 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74608 | 0.82009 |  |  |  |  | 305 | 0.07425
58949 | PEARSALLSCG4 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74648 | 0.8204 |  |  |  |  | 306 | 0.074169
58949 | PEARSALLSCG4 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74687 | 0.82072 |  |  |  |  | 307 | 0.074088
58949 | PEARSALLSCG4 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74727 | 0.82103 |  |  |  |  | 308 | 0.074007
58949 | PEARSALLSCG4 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74767 | 0.82135 |  |  |  |  | 309 | 0.073926
58949 | PEARSALLSCG4 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74807 | 0.82167 |  |  |  |  | 310 | 0.073844
58949 | PEARSALLSCG4 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 | 0.74846 | 0.82198 |  |  |  |  | 311 | 0.073763
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.044521 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.19646 | 0 | 0 |  |  |  |  | -0.19646 | 0 | 0.74846 | 0.82198 |  |  |  |  | 312 | 0.073682
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.044521 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.19646 | 0 | 0 |  |  |  |  | -0.19646 | 0 | 0.74846 | 0.82198 |  |  |  |  | 313 | 0.073601
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.042126 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.19406 | 0 | 0 |  |  |  |  | -0.19406 | 0 | 0.74846 | 0.82198 |  |  |  |  | 314 | 0.07352
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.041424 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.19336 | 148 | 148 |  |  |  |  | -0.19336 | -28.6174 | 0.75545 | 0.82745 |  |  |  |  | 315 | 0.07352
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.041424 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.19336 | 148 | 148 |  |  |  |  | -0.19336 | -28.6174 | 0.76245 | 0.83293 |  |  |  |  | 316 | 0.07352
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.041424 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.19336 | 154 | 154 |  |  |  |  | -0.19336 | -29.7776 | 0.76972 | 0.83862 |  |  |  |  | 317 | 0.07352
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.041424 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.19336 | 293 | 293 |  |  |  |  | -0.19336 | -56.6547 | 0.78357 | 0.84946 |  |  |  |  | 318 | 0.072
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.041131 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 | 0.78357 | 0.84946 |  |  |  |  | 319 | 0.070481
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.041131 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 | 0.78357 | 0.84946 |  |  |  |  | 320 | 0.0689
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.041131 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 | 0.78357 | 0.84946 |  |  |  |  | 321 | 0.065892
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.039835 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.19177 | 0 | 436 |  |  |  |  | -0.19177 | 0 | 0.78357 | 0.84946 |  |  |  |  | 322 | 0.065892
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.039706 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.19164 | 0 | 606 |  |  |  |  | -0.19164 | 0 | 0.78357 | 0.84946 |  |  |  |  | 323 | 0.065892
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.039706 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.19164 | 0 | 598 |  |  |  |  | -0.19164 | 0 | 0.78357 | 0.84946 |  |  |  |  | 324 | 0.065892
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 | 0.78593 | 0.85128 |  |  |  |  | 325 | 0.065892
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 | 0.78829 | 0.85311 |  |  |  |  | 326 | 0.065892
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 | 0.79065 | 0.85494 |  |  |  |  | 327 | 0.065892
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 | 0.79301 | 0.85677 |  |  |  |  | 328 | 0.065357
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.036626 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.18856 | 223.9 | 223.9 |  |  |  |  | -0.18856 | -42.2192 | 0.80359 | 0.86484 |  |  |  |  | 329 | 0.064823
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.036626 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.18856 | 225 | 225 |  |  |  |  | -0.18856 | -42.4267 | 0.81422 | 0.87296 |  |  |  |  | 330 | 0.064288
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.036626 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.18856 | 224.6 | 224.6 |  |  |  |  | -0.18856 | -42.3512 | 0.82483 | 0.88105 |  |  |  |  | 331 | 0.063753
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.036626 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.18856 | 226.7 | 226.7 |  |  |  |  | -0.18856 | -42.7472 | 0.83554 | 0.88923 |  |  |  |  | 332 | 0.061249
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.031678 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.18361 | 0 | 0 |  |  |  |  | -0.18361 | 0 | 0.83554 | 0.88923 |  |  |  |  | 333 | 0.058733
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.022083 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.17402 | 132 | 132 |  |  |  |  | -0.17402 | -22.9706 | 0.84178 | 0.89362 |  |  |  |  | 334 | 0.056221
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.022083 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.17402 | 139 | 139 |  |  |  |  | -0.17402 | -24.1888 | 0.84835 | 0.89825 |  |  |  |  | 335 | 0.053685
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.022083 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.17402 | 329 | 329 |  |  |  |  | -0.17402 | -57.2526 | 0.86389 | 0.9092 |  |  |  |  | 336 | 0.053685
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.019922 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.17186 | 158 | 158 |  |  |  |  | -0.17186 | -27.1537 | 0.87136 | 0.91439 |  |  |  |  | 337 | 0.051842
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.019922 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.17186 | 160 | 160 |  |  |  |  | -0.17186 | -27.4974 | 0.87892 | 0.91965 |  |  |  |  | 338 | 0.049901
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.019922 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.17186 | 175 | 175 |  |  |  |  | -0.17186 | -30.0753 | 0.88718 | 0.9254 |  |  |  |  | 339 | 0.045306
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.017461 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.1694 | 152.5 | 152.5 |  |  |  |  | -0.1694 | -25.8332 | 0.89439 | 0.93034 |  |  |  |  | 340 | 0.043034
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.017461 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.1694 | 149.5 | 149.5 |  |  |  |  | -0.1694 | -25.325 | 0.90145 | 0.93518 |  |  |  |  | 341 | 0.040734
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.017461 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.1694 | 232.6 | 232.6 |  |  |  |  | -0.1694 | -39.402 | 0.91244 | 0.94272 |  |  |  |  | 342 | 0.038218
8262 | ELPS | 1 | South | YES | -0.014069 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.16601 | 0 | 0 |  |  |  |  | -0.16601 | 0 | 0.91244 | 0.94272 |  |  |  |  | 343 | 0.035953
9016 | SANDH_G1 | 1 | South | YES | -0.013615 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.16555 | 49 | 49 |  |  |  |  | -0.16555 | -8.112 | 0.91476 | 0.94427 |  |  |  |  | 344 | 0.033733
9017 | SANDH_G2 | 2 | South | YES | -0.013615 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.16555 | 46 | 46 |  |  |  |  | -0.16555 | -7.6154 | 0.91693 | 0.94573 |  |  |  |  | 345 | 0.030279
9018 | SANDH_G3 | 3 | South | YES | -0.013615 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.16555 | 46 | 46 |  |  |  |  | -0.16555 | -7.6154 | 0.9191 | 0.94718 |  |  |  |  | 346 | 0.030279
9019 | SANDH_G4 | 4 | South | YES | -0.013615 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.16555 | 47 | 47 |  |  |  |  | -0.16555 | -7.7809 | 0.92132 | 0.94867 |  |  |  |  | 347 | 0.029516
9020 | SANDHG5A | 5A | South | YES | -0.013615 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.16555 | 155 | 155 |  |  |  |  | -0.16555 | -25.6605 | 0.92865 | 0.95358 |  |  |  |  | 348 | 0.028799
9021 | SANDHG5C | 5C | South | YES | -0.013615 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.16555 | 148 | 148 |  |  |  |  | -0.16555 | -24.5017 | 0.93564 | 0.95827 |  |  |  |  | 349 | 0.028082
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.012215 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.16415 | 0 | 0 |  |  |  |  | -0.16415 | 0 | 0.93564 | 0.95827 |  |  |  |  | 350 | 0.027349
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.012215 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.16415 | 0 | 0 |  |  |  |  | -0.16415 | 0 | 0.93564 | 0.95827 |  |  |  |  | 351 | 0.024934
9000 | DECKR_G1 | 1 | South | YES | -0.012116 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.16405 | 321 | 321 |  |  |  |  | -0.16405 | -52.661 | 0.9508 | 0.96834 |  |  |  |  | 352 | 0.022627
9001 | DECKR_G2 | 2 | South | YES | -0.012116 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.16405 | 426 | 426 |  |  |  |  | -0.16405 | -69.8865 | 0.97093 | 0.9817 |  |  |  |  | 353 | 0.022627
9002 | DECKR_G3 | 3 | South | YES | -0.01105 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.16299 | 42 | 42 |  |  |  |  | -0.16299 | -6.8455 | 0.97291 | 0.98301 |  |  |  |  | 354 | 0.022627
9003 | DECKR_G4 | 4 | South | YES | -0.01105 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.16299 | 44 | 44 |  |  |  |  | -0.16299 | -7.1714 | 0.97499 | 0.98438 |  |  |  |  | 355 | 0.017532
9004 | DECKR_G5 | 5 | South | YES | -0.01105 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.16299 | 44 | 44 |  |  |  |  | -0.16299 | -7.1714 | 0.97707 | 0.98575 |  |  |  |  | 356 | 0.010771
9005 | DECKR_G6 | 6 | South | YES | -0.01105 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.16299 | 47 | 47 |  |  |  |  | -0.16299 | -7.6604 | 0.97929 | 0.98722 |  |  |  |  | 357 | 0.010096
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.008971 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 | 0.97929 | 0.98722 |  |  |  |  | 358 | 0.0093886
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.008971 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 | 0.97929 | 0.98722 |  |  |  |  | 359 | 0.0086813
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.008971 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 | 0.97929 | 0.98722 |  |  |  |  | 360 | 0.0079258
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.003309 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.15525 | 0 | 0 |  |  |  |  | -0.15525 | 0 | 0.97929 | 0.98722 |  |  |  |  | 361 | 0.0079258
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.003309 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.15525 | 0 | 0 |  |  |  |  | -0.15525 | 0 | 0.97929 | 0.98722 |  |  |  |  | 362 | 0.0079258
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.000571 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.15251 | 423.3 | 423.3 |  |  |  |  | -0.15251 | -64.5566 | 0.99929 | 0.99956 |  |  |  |  | 363 | 0.0079258
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.000339 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.15228 | 0 | 0 |  |  |  |  | -0.15228 | 0 | 0.99929 | 0.99956 |  |  |  |  | 364 | 0.0079258
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.000339 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.15228 | 0 | 0 |  |  |  |  | -0.15228 | 0 | 0.99929 | 0.99956 |  |  |  |  | 365 | 0.0079258
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.15194 | 15 | 15 |  |  |  |  | -0.15194 | -2.2791 | 1 | 1 |  |  |  |  | 366 | 0.00027283
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | 1 | 1 |  |  |  |  | 367 | 0.00027283
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | 1 | 1 |  |  |  |  | 368 | 0.00027283
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | 1 | 1 |  |  |  |  | 369 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | 1 | 1 |  |  |  |  | 370 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | 1 | 1 |  |  |  |  | 371 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | 1 | 1 |  |  |  |  | 372 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | 1 | 1 |  |  |  |  | 373 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | 1 | 1 |  |  |  |  | 374 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.15194 | 0 | 0 |  |  | 0 | 0 | -0.15194 | 0 | 1 | 1 |  |  |  |  | 375 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.002445 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 | 1 | 1 |  |  |  |  | 376 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.002445 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 | 1 | 1 |  |  |  |  | 377 | 0
88253 | HAMILTON | F | South | YES | 0.002445 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 | 1 | 1 |  |  |  |  | 378 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.008542 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.14339 | 0 | 0 |  |  |  |  | -0.14339 | 0 | 1 | 1 |  |  |  |  | 379 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.009199 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 | 1 | 1 |  |  |  |  | 380 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.009199 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 | 1 | 1 |  |  |  |  | 381 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.009199 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 | 1 | 1 |  |  |  |  | 382 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.025209 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.12673 | 0 | 580 |  |  |  |  | -0.12673 | 0 | 1 | 1 |  |  |  |  | 383 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.044563 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.10737 | 0 | 581 |  |  |  |  | -0.10737 | 0 | 1 | 1 |  |  |  |  | 384 | 0
60202 | FRNDDRCS | F | West | YES | 0.1063 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.27701 | 0 | 0 |  |  |  |  | 0.27701 | 0 | [6 empty] | 385 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | 0.11148 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.28219 | 75 | 75 | 8.3608 | 75 |  |  | 0.28219 | 21.1646 | [6 empty] | 386 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | 0.11148 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.28219 | 222 | 222 | 24.7479 | 222 |  |  | 0.28219 | 62.6472 | [6 empty] | 387 | 0
3403 | THOUSE_1G | 1 | North | YES | 0.11301 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.28372 | 563 | 563 | 63.6224 | 563 |  |  | 0.28372 | 159.7365 | [6 empty] | 388 | 0
3404 | THOUSE_2G | 2 | North | YES | 0.11301 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.28372 | 807 | 807 | 91.1958 | 807 |  |  | 0.28372 | 228.9651 | [6 empty] | 389 | 0
238 | BOSQUESW505 | 1 | North | YES | 0.11477 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.28549 | 255 | 255 | 29.2674 | 255 |  |  | 0.28549 | 72.8004 | [6 empty] | 390 | 0
239 | BOSQUESW502 | 1 | North | YES | 0.11477 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.28549 | 149 | 149 | 17.1013 | 149 |  |  | 0.28549 | 42.5383
247 | BOSQUESW501 | 2 | North | YES | 0.11477 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.28549 | 156 | 156 | 17.9047 | 156 |  |  | 0.28549 | 44.5367
251 | BOSQUESW803 | 2 | North | YES | 0.11786 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.28857 | 150 | 150 | 17.6782 | 150 |  |  | 0.28857 | 43.2859
253 | BOSQUESW804 | 2 | North | YES | 0.11786 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.28857 | 80 | 80 | 9.4284 | 80 |  |  | 0.28857 | 23.0858
60018 | DSKY1 | 1 | West | YES | 0.11862 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.28934 | 0 | 84 |  |  |  |  | 0.28934 | 24.3045
60000 | DSKY2 | 1 | West | YES | 0.11883 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.28955 | 0 | 76.5 |  |  |  |  | 0.28955 | 22.1502
60017 | ORNNWP1 | 1 | West | YES | 0.11942 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.29014 | 0 | 80 |  |  |  |  | 0.29014 | 23.2109
38437 | TNSRBNMESA9 | 1 | West | YES | 0.12178 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.2925 | 0 | 150 |  |  |  |  | 0.2925 | 43.8744
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.12184 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.29256 | 0 | 80 |  |  |  |  | 0.29256 | 23.405
60016 | WOODWRD11A | 1 | West | YES | 0.12186 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.29258 | 0 | 80 |  |  |  |  | 0.29258 | 23.4063
6016 | SWMESA | 1 | West | YES | 0.12194 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.29266 | 0 | 75 |  |  |  |  | 0.29266 | 21.9496
60003 | KING_NE1A | 1 | West | YES | 0.12194 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29266 | 0 | 80 |  |  |  |  | 0.29266 | 23.4129
60005 | KING_SE1A | 1 | West | YES | 0.12194 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.29266 | 0 | 40 |  |  |  |  | 0.29266 | 11.7065
60201 | RIO DRCS | F | West | YES | 0.12207 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.29279 | 0 | 0 |  |  |  |  | 0.29279 | 0
244 | WHITNYDM01 | 1 | North | YES | 0.12239 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.2931 | 0 | 0 | 0 | 0 |  |  | 0.2931 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.12239 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.2931 | 0 | 0 | 0 | 0 |  |  | 0.2931 | 0
60007 | KING_SW1A | 1 | West | YES | 0.12239 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29311 | 0 | 80 |  |  |  |  | 0.29311 | 23.4485
60019 | KING_NW1A | 1 | West | YES | 0.12239 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29311 | 0 | 80 |  |  |  |  | 0.29311 | 23.4485
1349 | WESTXWIN_1G | 1 | West | YES | 0.12878 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.2995 | 0 | 6.6 |  |  |  |  | 0.2995 | 1.9767
1350 | NWPWRG1_1G | 1 | West | YES | 0.12878 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.2995 | 0 | 34.3 |  |  |  |  | 0.2995 | 10.2727
60057 | CALLAHAN1A | 1 | West | YES | 0.12912 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.29984 | 0 | 114 |  |  |  |  | 0.29984 | 34.1821
1002 | PBCTAGE_1G | A | West | YES | 0.12924 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.29996 | 66 | 66 |  |  |  |  | 0.29996 | 19.7975
1003 | PBCTBGE_2G | B | West | YES | 0.12924 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.29996 | 66 | 66 |  |  |  |  | 0.29996 | 19.7975
1004 | PBCTCGE_3G | C | West | YES | 0.12924 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.29996 | 67 | 67 |  |  |  |  | 0.29996 | 20.0975
1005 | PBCTDGE_4G | D | West | YES | 0.12924 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.29996 | 68 | 68 |  |  |  |  | 0.29996 | 20.3975
1006 | PBCTEGE_5G | E | West | YES | 0.12924 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.29996 | 67 | 67 |  |  |  |  | 0.29996 | 20.0975
1007 | PB5GEN_6G | 5 | West | YES | 0.12924 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.29996 | 114 | 114 |  |  |  |  | 0.29996 | 34.1958
1008 | PB6GEN_7G | 6 | West | YES | 0.12924 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.29996 | 515 | 515 |  |  |  |  | 0.29996 | 154.4808
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.12932 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.30003 | 0 | 35 |  |  |  |  | 0.30003 | 10.5012
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.12932 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.30003 | 0 | 30 |  |  |  |  | 0.30003 | 9.001
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.12945 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.30016 | 0 | 112.5 |  |  |  |  | 0.30016 | 33.7683
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.12945 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 149.5 |  |  |  |  | 0.30016 | 44.8743
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.12945 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 186 |  |  |  |  | 0.30016 | 55.8303
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.12945 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 214.5 |  |  |  |  | 0.30016 | 64.3849
11147 | NOTREES_1G | 1 | West | YES | 0.12945 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.30017 | 0 | 149 |  |  |  |  | 0.30017 | 44.7256
76031 | L_GASCCR1_1N | W1 | West | YES | 0.1298 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.30052 | 0 | 150 |  |  |  |  | 0.30052 | 45.0783
1320 | BSP 1 | 1 | West | YES | 0.13011 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.30083 | 0 | 0 |  |  |  |  | 0.30083 | 0
1326 | STANTONW_8 | 1 | West | YES | 0.13024 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.30095 | 0 | 100.5 |  |  |  |  | 0.30095 | 30.2459
11020 | TIEHVSG_1G | 1 | West | YES | 0.13028 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.301 | 208.2 | 208.2 |  |  |  |  | 0.301 | 62.6681
11021 | TIEHVCG_1G | 1 | West | YES | 0.13028 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.301 | 142.1 | 142.1 |  |  |  |  | 0.301 | 42.7721
11022 | TIEHVCG_2G | 1 | West | YES | 0.13028 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.301 | 132.4 | 132.4 |  |  |  |  | 0.301 | 39.8524
11023 | TIEHVCG_3G | 1 | West | YES | 0.13028 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.301 | 137.4 | 137.4 |  |  |  |  | 0.301 | 41.3574
11024 | TIEHVCG_4G | 1 | West | YES | 0.13028 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.301 | 147 | 147 |  |  |  |  | 0.301 | 44.247
11025 | TIEHVSG_2G | 1 | West | YES | 0.13028 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.301 | 213.2 | 213.2 |  |  |  |  | 0.301 | 64.1731
11001 | NAV1CT | 1 | West | YES | 0.13029 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.30101 | 70.4 | 70.4 |  |  |  |  | 0.30101 | 21.1912
11009 | NAV2CT | 1 | West | YES | 0.13029 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.30101 | 71.4 | 71.4 |  |  |  |  | 0.30101 | 21.4922
11011 | NAV3ST | 1 | West | YES | 0.13029 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.30101 | 92.8 | 92.8 |  |  |  |  | 0.30101 | 27.9339
11012 | NAV4CT | 1 | West | YES | 0.13029 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30101 | 80 | 80 |  |  |  |  | 0.30101 | 24.0809
11013 | NAV5CT | 1 | West | YES | 0.13029 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30101 | 80 | 80 |  |  |  |  | 0.30101 | 24.0809
11014 | NAV6ST | 1 | West | YES | 0.13029 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.30101 | 115 | 115 |  |  |  |  | 0.30101 | 34.6164
1328 | OCOTILLO_1G | 1 | West | YES | 0.13036 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.30107 | 0 | 58 |  |  |  |  | 0.30107 | 17.4623
1333 | MCDDONAL_8 | 1 | West | YES | 0.13054 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.30126 | 0 | 214.2 |  |  |  |  | 0.30126 | 64.5292
1327 | WILDHRSE_1G | 1 | West | YES | 0.13076 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.30148 | 0 | 120 |  |  |  |  | 0.30148 | 36.1774
1360 | GUNSIGHT_8 | 1 | West | YES | 0.1308 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.30152 | 0 | 120 |  |  |  |  | 0.30152 | 36.1819
11320 | COYOTE_1G | 1 | West | YES | 0.13107 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.30179 | 0 | 225 |  |  |  |  | 0.30179 | 67.9034
11309 | BULLCREK_2G | 1 | West | YES | 0.13114 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.30186 | 0 | 180 |  |  |  |  | 0.30186 | 54.3348
11310 | BULLCREK_1G | 1 | West | YES | 0.13114 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.30186 | 0 | 180 |  |  |  |  | 0.30186 | 54.3348
1045 | CALENG1G_1G | 1 | West | YES | 0.13116 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.13116 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.13116 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0
1058 | LONGSHORE_5 | 1 | West | YES | 0.13136 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.30208 | 0 | 150 |  |  |  |  | 0.30208 | 45.312
1058 | LONGSHORE_5 | 2 | West | YES | 0.13136 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.30208 | 0 | 220 |  |  |  |  | 0.30208 | 66.4575
11065 | ELBOWCK_1G | 1 | West | YES | 0.13136 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.30208 | 0 | 121.9 |  |  |  |  | 0.30208 | 36.8235
60058 | BUFF_GAP1A | 1 | West | YES | 0.13142 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30214 | 0 | 120 |  |  |  |  | 0.30214 | 36.257
60060 | CIRELLO | 1 | West | YES | 0.13142 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.30214 | 0 | 233 |  |  |  |  | 0.30214 | 70.399
60063 | BUFF_GAP1B | 1 | West | YES | 0.13142 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.30214 | 0 | 170.2 |  |  |  |  | 0.30214 | 51.4245
60066 | H_HOLLOW1A | 1 | West | YES | 0.13142 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.30214 | 0 | 222 |  |  |  |  | 0.30214 | 67.0755
60068 | HHOLLOW21A | 1 | West | YES | 0.13142 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 184 |  |  |  |  | 0.30214 | 55.5941
60070 | HHOLLOW31A | 1 | West | YES | 0.13142 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 224 |  |  |  |  | 0.30214 | 67.6798
60072 | HHOLLOW41A | 1 | West | YES | 0.13142 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 115 |  |  |  |  | 0.30214 | 34.7463
1037 | MORGAN5G_5G | 5 | West | YES | 0.13148 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.3022 | 137 | 137 |  |  |  |  | 0.3022 | 41.4018
1039 | MRGNAG_1G | A | West | YES | 0.13148 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.3022 | 69 | 69 |  |  |  |  | 0.3022 | 20.852
1040 | MRGNBG_2G | B | West | YES | 0.13148 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.3022 | 71 | 71 |  |  |  |  | 0.3022 | 21.4564
1041 | MRGNCG_3G | C | West | YES | 0.13148 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.3022 | 70 | 70 |  |  |  |  | 0.3022 | 21.1542
1042 | MRGNDG_4G | D | West | YES | 0.13148 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.3022 | 68 | 68 |  |  |  |  | 0.3022 | 20.5498
1043 | MRGNEG_5G | E | West | YES | 0.13148 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.3022 | 70 | 70 |  |  |  |  | 0.3022 | 21.1542
1044 | MRGNFG_6G | F | West | YES | 0.13148 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.3022 | 66 | 66 |  |  |  |  | 0.3022 | 19.9454
6637 | SNYDERW1A | 1 | West | YES | 0.13152 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.30224 | 0 | 63 |  |  |  |  | 0.30224 | 19.0412
1068 | SCURRYCW_1G | 1 | West | YES | 0.13159 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.30231 | 0 | 141 |  |  |  |  | 0.30231 | 42.6257
1073 | SCURRYCW_2G | 2 | West | YES | 0.13159 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.30231 | 0 | 120 |  |  |  |  | 0.30231 | 36.2772
1061 | CIELOGEN_1G | 1 | West | YES | 0.1316 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.30232 | 0 | 99 |  |  |  |  | 0.30232 | 29.9298
1062 | CIELOGEN_2G | 1 | West | YES | 0.1316 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.30232 | 0 | 61 |  |  |  |  | 0.30232 | 18.4416
1069 | KINDERMG_1G | 1 | West | YES | 0.1316 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.1316 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.1316 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0
36998 | RDCNYNG1 | 1 | West | YES | 0.13178 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.3025 | 0 | 84 |  |  |  |  | 0.3025 | 25.4101
1343 | TRENTIPP_8 | 1 | West | YES | 0.13189 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.3026 | 0 | 150 |  |  |  |  | 0.3026 | 45.3907
1354 | AEPWIND_8 | 1 | West | YES | 0.13189 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.3026 | 0 | 101 |  |  |  |  | 0.3026 | 30.5631
6407 | TURKTRAK1A | 1 | West | YES | 0.13209 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.3028 | 0 | 169.5 |  |  |  |  | 0.3028 | 51.3254
71051 | L_BITTCR1_1N | W1 | West | YES | 0.13255 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 37.5 |  |  |  |  | 0.30327 | 11.3725
71054 | L_SWEETW1_1N | W1 | West | YES | 0.13255 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 107.5 |  |  |  |  | 0.30327 | 32.6012
71057 | L_SWEETW1_2N | W1 | West | YES | 0.13255 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 135 |  |  |  |  | 0.30327 | 40.941
71059 | L_SWEETW1_3N | W1 | West | YES | 0.13255 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 119 |  |  |  |  | 0.30327 | 36.0887
71060 | L_SWEETW1_4N | W1 | West | YES | 0.13255 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 105 |  |  |  |  | 0.30327 | 31.843
71061 | L_SWEETW1_5N | W1 | West | YES | 0.13255 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 80.5 |  |  |  |  | 0.30327 | 24.413
6144 | MCADOO1A | 1 | West | YES | 0.13257 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.30329 | 0 | 150 |  |  |  |  | 0.30329 | 45.4936
11056 | ROSCOE_1G | 1 | West | YES | 0.1326 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.30332 | 0 | 209 |  |  |  |  | 0.30332 | 63.3938
11057 | CHAMPION_1G | 1 | West | YES | 0.1326 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.30332 | 0 | 126.5 |  |  |  |  | 0.30332 | 38.3699
11058 | PYRON_1G | 1 | West | YES | 0.1326 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.30332 | 0 | 249 |  |  |  |  | 0.30332 | 75.5266
11059 | INADALE_1G | 1 | West | YES | 0.1326 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.30332 | 0 | 197 |  |  |  |  | 0.30332 | 59.754
1643 | SLSTR1PP_1G | 1 | North | YES | 0.13291 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.30363 | 0 | 60 | 7.9747 | 60 |  |  | 0.30363 | 18.2177
1416 | SWETWATR_1G | 1 | West | YES | 0.13308 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.3038 | 30 | 30 |  |  |  |  | 0.3038 | 9.114
1417 | SWETWATR_2G | 2 | West | YES | 0.13308 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.3038 | 72 | 72 |  |  |  |  | 0.3038 | 21.8735
1418 | SWETWATR_3G | 3 | West | YES | 0.13308 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.3038 | 68 | 68 |  |  |  |  | 0.3038 | 20.6583
1419 | SWETWATR_4G | 4 | West | YES | 0.13308 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.3038 | 61 | 61 |  |  |  |  | 0.3038 | 18.5317
60081 | WHRLWIND1A | 1 | West | YES | 0.13362 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.30433 | 0 | 60 |  |  |  |  | 0.30433 | 18.2601
1437 | MESQUITW_1G | 1 | North | YES | 0.13531 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.30602 | 0 | 400 | 54.1224 | 400 |  |  | 0.30602 | 122.4095
1438 | MESQUITW_2G | 1 | North | YES | 0.13531 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.30603 | 0 | 236 | 31.9334 | 236 |  |  | 0.30603 | 72.2228
1442 | COKFIELD_5 | 1 | North | YES | 0.13619 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.30691 | 0 | 165 | 22.4714 | 165 |  |  | 0.30691 | 50.6398
6100 | OKLA7A | EQ | West | YES | 0.13689 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.30761 | 0 | 0 |  |  |  |  | 0.30761 | 0
6752 | OKLA0A | 1 | West | YES | 0.13689 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.30761 | 0 | 649.7 |  |  |  |  | 0.30761 | 199.8541
1433 | GRHAMSES_1G | 1 | North | YES | 0.13817 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.30889 | 242 | 242 | 33.4381 | 242 |  |  | 0.30889 | 74.7518
332 | RWMILLER01 | 1 | North | YES | 0.13825 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.30897 | 73 | 73 | 10.0923 | 73 |  |  | 0.30897 | 22.5547
333 | RWMILLER02 | 2 | North | YES | 0.13825 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.30897 | 119 | 119 | 16.4519 | 119 |  |  | 0.30897 | 36.7673
334 | RWMILLER03 | 3 | North | YES | 0.13825 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.30897 | 208 | 208 | 28.7562 | 208 |  |  | 0.30897 | 64.2655
335 | RWMILLER04 | 4 | North | YES | 0.13825 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.30897 | 102 | 102 | 14.1016 | 102 |  |  | 0.30897 | 31.5148
336 | RWMILLER05 | 5 | North | YES | 0.13825 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.30897 | 101 | 101 | 13.9634 | 101 |  |  | 0.30897 | 31.2058
1432 | GRHAMSES_2G | 2 | North | YES | 0.13897 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.30969 | 366 | 366 | 50.8648 | 366 |  |  | 0.30969 | 113.3475
1479 | WFCOGEN_1G | 1 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.13909 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.13929 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.31 | 0 | 120 | 16.7143 | 120 |  |  | 0.31 | 37.2004
344 | MRSSHPRD | 1 | North | YES | 0.13949 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.13949 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.13991 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.31062 | 0 | 0 | 0 | 0 |  |  | 0.31062 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.13991 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.31062 | 0 | 0 | 0 | 0 |  |  | 0.31062 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.14077 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.31149 | 70 | 70 | 9.8542 | 70 |  |  | 0.31149 | 21.8044
1893 | DECRDOVA_3G | B | North | YES | 0.14077 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.31149 | 69 | 69 | 9.7134 | 69 |  |  | 0.31149 | 21.4929
1894 | DECRDOVA_4G | C | North | YES | 0.14077 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.31149 | 69 | 69 | 9.7134 | 69 |  |  | 0.31149 | 21.4929
1895 | DECRDOVA_5G | D | North | YES | 0.14077 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.31149 | 68 | 68 | 9.5726 | 68 |  |  | 0.31149 | 21.1814
503 | NTHTEXAS01 | 1 | North | YES | 0.14081 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.31153 | 18 | 18 | 2.5346 | 18 |  |  | 0.31153 | 5.6075
504 | NTHTEXAS02 | 2 | North | YES | 0.14081 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.31153 | 18 | 18 | 2.5346 | 18 |  |  | 0.31153 | 5.6075
505 | NTHTEXAS03 | 3 | North | YES | 0.14081 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.31153 | 38 | 38 | 5.3508 | 38 |  |  | 0.31153 | 11.8381
1898 | COMCHEPK_1G | 1 | North | YES | 0.14151 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.31222 | 0 | 0 | 0 | 0 |  |  | 0.31222 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.14151 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.31222 | 0 | 0 | 0 | 0 |  |  | 0.31222 | 0
1453 | WCPWRCO_1G | 1 | North | YES | 0.1417 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.31242 | 204 | 204 | 28.9074 | 204 |  |  | 0.31242 | 63.7338
1454 | WCPWRCO_2G | 2 | North | YES | 0.1417 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.31242 | 204 | 204 | 28.9074 | 204 |  |  | 0.31242 | 63.7338
1455 | WCPWRCO_3G | 3 | North | YES | 0.1417 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.31242 | 242 | 242 | 34.2921 | 242 |  |  | 0.31242 | 75.6058
1877 | WLFHOLW_1G | 1 | North | YES | 0.1419 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.31262 | 217.3 | 217.3 | 30.8344 | 217.3 |  |  | 0.31262 | 67.9314
1878 | WLFHOLW_2G | 2 | North | YES | 0.1419 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.31262 | 215.7 | 215.7 | 30.6074 | 215.7 |  |  | 0.31262 | 67.4312
1879 | WLFHOLW_3G | 3 | North | YES | 0.1419 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.31262 | 272.4 | 272.4 | 38.653 | 272.4 |  |  | 0.31262 | 85.1565
1889 | DECRDOVA_1G | 1 | North | YES | 0.14217 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.31289 | 779 | 779 | 110.7543 | 779 |  |  | 0.31289 | 243.7434
580 | JCKCNTY801 | 1 | North | YES | 0.14264 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.31336 | 288 | 288 | 41.0797 | 288 |  |  | 0.31336 | 90.2465
581 | JCKCNTY802 | 2 | North | YES | 0.14264 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.31336 | 147 | 147 | 20.9678 | 147 |  |  | 0.31336 | 46.0633
582 | JCKCNTY803 | 3 | North | YES | 0.14264 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.31336 | 147 | 147 | 20.9678 | 147 |  |  | 0.31336 | 46.0633
1937 | MDLTHELP_5G | 5 | North | YES | 0.14319 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.31391 | 224 | 224 | 32.0757 | 224 |  |  | 0.31391 | 70.3165
1938 | MDLTHELP_6G | 6 | North | YES | 0.14319 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.31391 | 226 | 226 | 32.3621 | 226 |  |  | 0.31391 | 70.9443
1943 | MDLTHELP_3G | 3 | North | YES | 0.14319 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.31391 | 212 | 212 | 30.3573 | 212 |  |  | 0.31391 | 66.5495
1944 | MDLTHELP_4G | 4 | North | YES | 0.14319 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.31391 | 211 | 211 | 30.2141 | 211 |  |  | 0.31391 | 66.2356
1861 | EAGLEMNT_1G | MB | North | YES | 0.1441 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.1441 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.1441 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0
728 | WOLFRIDGE801 | 1 | North | YES | 0.14468 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.3154 | 0 | 112.5 | 16.2764 | 112.5 |  |  | 0.3154 | 35.4821
1941 | MDLTHELP_1G | 1 | North | YES | 0.14469 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.31541 | 216.4 | 216.4 | 31.3113 | 216.4 |  |  | 0.31541 | 68.2547
1942 | MDLTHELP_2G | 2 | North | YES | 0.14469 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.31541 | 216.1 | 216.1 | 31.2679 | 216.1 |  |  | 0.31541 | 68.16
1947 | HANDLEY_3G | 3 | North | YES | 0.14472 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.31543 | 395 | 395 | 57.1624 | 395 |  |  | 0.31543 | 124.5959
1949 | HANDLEY_5G | 5 | North | YES | 0.14472 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31543 | 435 | 435 | 62.951 | 435 |  |  | 0.31543 | 137.2132
1948 | HANDLEY_4G | 4 | North | YES | 0.14497 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31568 | 435 | 435 | 63.0606 | 435 |  |  | 0.31568 | 137.3229
923 | SPENCER_G4 | 1 | North | YES | 0.14605 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.31677 | 61 | 61 | 8.9092 | 61 |  |  | 0.31677 | 19.323
924 | SPENCER_G5 | 1 | North | YES | 0.14605 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.31677 | 66 | 66 | 9.6395 | 66 |  |  | 0.31677 | 20.9069
12322 | ENNSTRAC_1G | 1 | North | YES | 0.14859 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.31931 | 196 | 196 | 29.1232 | 196 |  |  | 0.31931 | 62.5839
12323 | ENNSTRAC_2G | 2 | North | YES | 0.14859 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.31931 | 116 | 116 | 17.2362 | 116 |  |  | 0.31931 | 37.0395
2381 | NTHLK1_G | 1 | North | YES | 0.14864 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.31936 | 156 | 156 | 23.188 | 156 |  |  | 0.31936 | 49.82
2382 | NTHLK2_G | 2 | North | YES | 0.14864 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.31936 | 181 | 181 | 26.904 | 181 |  |  | 0.31936 | 57.8039
2383 | NTHLK3_G | 3 | North | YES | 0.14864 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.31936 | 329 | 329 | 48.9029 | 329 |  |  | 0.31936 | 105.069
2371 | COLLIN_1G | MB | North | YES | 0.14891 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.31963 | 0 | 0 | 0 | 0 |  |  | 0.31963 | 0
6948 | DENISNDM | 1 | North | YES | 0.14967 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.32039 | 0 | 0 | 0 | 0 |  |  | 0.32039 | 0
6948 | DENISNDM | 2 | North | YES | 0.14967 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.32039 | 0 | 0 | 0 | 0 |  |  | 0.32039 | 0
2413 | MTCK6_G | 6 | North | YES | 0.14991 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.32062 | 118 | 118 | 17.6889 | 118 |  |  | 0.32062 | 37.8336
2414 | MTCK7_G | 7 | North | YES | 0.14991 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.32062 | 115 | 115 | 17.2392 | 115 |  |  | 0.32062 | 36.8717
2417 | MTCK8_G | 8 | North | YES | 0.14991 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.32062 | 556 | 556 | 83.3477 | 556 |  |  | 0.32062 | 178.2668
1687 | VALLEY_1G | 1 | North | YES | 0.14992 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.32064 | 170 | 170 | 25.4866 | 170 |  |  | 0.32064 | 54.5086
1688 | VALLEY_2G | 2 | North | YES | 0.14992 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.32064 | 527 | 527 | 79.0084 | 527 |  |  | 0.32064 | 168.9766
1689 | VALLEY_3G | 3 | North | YES | 0.15023 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.32095 | 375 | 375 | 56.337 | 375 |  |  | 0.32095 | 120.3562
11691 | KMICHICT1_G | 1 | North | YES | 0.15023 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32095 | 144 | 144 | 21.6334 | 144 |  |  | 0.32095 | 46.2168
11692 | KMICHICT2_G | 2 | North | YES | 0.15023 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.32095 | 146 | 146 | 21.9339 | 146 |  |  | 0.32095 | 46.8587
11693 | KMICHIST3_G | 3 | North | YES | 0.15023 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.32095 | 312 | 312 | 46.8724 | 312 |  |  | 0.32095 | 100.1363
11694 | KMICHICT4_G | 4 | North | YES | 0.15023 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32095 | 144 | 144 | 21.6334 | 144 |  |  | 0.32095 | 46.2168
11695 | KMICHICT5_G | 5 | North | YES | 0.15023 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.32095 | 148 | 148 | 22.2343 | 148 |  |  | 0.32095 | 47.5006
11696 | KMICHIST6_G | 6 | North | YES | 0.15023 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.32095 | 310 | 310 | 46.5719 | 310 |  |  | 0.32095 | 99.4944
1678 | LAMARPWR_1G | 1 | North | YES | 0.15037 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.32109 | 160 | 160 | 24.0592 | 160 |  |  | 0.32109 | 51.374
1679 | LAMARPWR_2G | 2 | North | YES | 0.15037 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32109 | 156 | 156 | 23.4577 | 156 |  |  | 0.32109 | 50.0897
1680 | LAMARPWR_3G | 3 | North | YES | 0.15037 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.32109 | 196 | 196 | 29.4725 | 196 |  |  | 0.32109 | 62.9332
1681 | LAMARPWR_4G | 4 | North | YES | 0.15037 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32109 | 156 | 156 | 23.4577 | 156 |  |  | 0.32109 | 50.0897
1682 | LAMARPWR_5G | 5 | North | YES | 0.15037 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.32109 | 157 | 157 | 23.6081 | 157 |  |  | 0.32109 | 50.4108
1683 | LAMARPWR_6G | 6 | North | YES | 0.15037 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.32109 | 198 | 198 | 29.7733 | 198 |  |  | 0.32109 | 63.5754
1675 | PEC_1G | 1 | North | YES | 0.15046 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0
1676 | PEC_2G | 2 | North | YES | 0.15046 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0
1677 | PEC_3G | 3 | North | YES | 0.15046 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0
1701 | MOSES_1G | 1 | North | YES | 0.15062 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 558 | 84.0437 | 558 |  |  | 0.32133 | 179.3042
1702 | MOSES_2G | 2 | North | YES | 0.15062 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 579 | 87.2067 | 579 |  |  | 0.32133 | 186.0522
1703 | MOSES_3G | 3 | North | YES | 0.15062 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 808 | 121.6977 | 808 |  |  | 0.32133 | 259.6377
5925 | DCEAST | EQ | North | YES | 0.15062 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.32133 | 0 | 0 | 0 | 0 |  |  | 0.32133 | 0
842 | OLINGER_G1 | 1 | North | YES | 0.15091 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.32162 | 79 | 79 | 11.9216 | 79 |  |  | 0.32162 | 25.4083
843 | OLINGER_G2 | 1 | North | YES | 0.15091 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.32162 | 110 | 110 | 16.5997 | 110 |  |  | 0.32162 | 35.3786
844 | OLINGER_G3 | 1 | North | YES | 0.15091 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.32162 | 150 | 150 | 22.6359 | 150 |  |  | 0.32162 | 48.2436
845 | OLINGER_G4 | 1 | North | YES | 0.15091 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.32162 | 76 | 76 | 11.4689 | 76 |  |  | 0.32162 | 24.4434
837 | NEWMAN_G5 | 1 | North | YES | 0.15093 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.32165 | 40 | 40 | 6.0372 | 40 |  |  | 0.32165 | 12.8659
949 | STEAM2 | 1 | North | YES | 0.15111 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.32182 | 26 | 26 | 3.9288 | 26 |  |  | 0.32182 | 8.3674
950 | STEAM3 | 1 | North | YES | 0.15111 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.32182 | 42 | 42 | 6.3465 | 42 |  |  | 0.32182 | 13.5166
948 | STEAM1 | 1 | North | YES | 0.15111 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.32183 | 20 | 20 | 3.0222 | 20 |  |  | 0.32183 | 6.4365
12440 | PARKD_1SVC8 | 1 | North | YES | 0.15148 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.3222 | 0 | 0 | 0 | 0 |  |  | 0.3222 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.15148 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.3222 | 0 | 0 | 0 | 0 |  |  | 0.3222 | 0
2451 | LKHB1_G | 1 | North | YES | 0.15155 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.32227 | 391 | 391 | 59.2564 | 391 |  |  | 0.32227 | 126.0071
2452 | LKHB2_G | 2 | North | YES | 0.15155 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.32227 | 516 | 516 | 78.2003 | 516 |  |  | 0.32227 | 166.2907
12411 | FPLEFR1A_G | 1 | North | YES | 0.15233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32305 | 161 | 161 | 24.5248 | 161 |  |  | 0.32305 | 52.0104
12412 | FPLEFR1B_G | 2 | North | YES | 0.15233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32305 | 164 | 164 | 24.9818 | 164 |  |  | 0.32305 | 52.9795
12413 | FPLEFR1C_G | 3 | North | YES | 0.15233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32305 | 164 | 164 | 24.9818 | 164 |  |  | 0.32305 | 52.9795
12414 | FPLEFR1S_G | 4 | North | YES | 0.15233 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.32305 | 414 | 414 | 63.0638 | 414 |  |  | 0.32305 | 133.7409
12421 | FPLEFR2A_G | 1 | North | YES | 0.15233 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.32305 | 162 | 162 | 24.6771 | 162 |  |  | 0.32305 | 52.3334
12422 | FPLEFR2B_G | 2 | North | YES | 0.15233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32305 | 161 | 161 | 24.5248 | 161 |  |  | 0.32305 | 52.0104
12423 | FPLEFR2C_G | 3 | North | YES | 0.15233 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.32305 | 163 | 163 | 24.8295 | 163 |  |  | 0.32305 | 52.6565
12424 | FPLEFR2S_G | 4 | North | YES | 0.15233 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.32305 | 415 | 415 | 63.2161 | 415 |  |  | 0.32305 | 134.064
3126 | TRINIDAD_6G | 1 | North | YES | 0.15258 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.3233 | 224 | 224 | 34.1784 | 224 |  |  | 0.3233 | 72.4191
3097 | MARTLAKE_1G | 1 | North | YES | 0.15654 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 790 | 123.6634 | 790 |  |  | 0.32725 | 258.5305
3098 | MARTLAKE_2G | 2 | North | YES | 0.15654 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 795 | 124.4461 | 795 |  |  | 0.32725 | 260.1667
3099 | MARTLAKE_3G | 3 | North | YES | 0.15654 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 804 | 125.8549 | 804 |  |  | 0.32725 | 263.112
13116 | TGATEWAY_1G | 1 | North | YES | 0.15714 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.32786 | 151 | 151 | 23.7278 | 151 |  |  | 0.32786 | 49.5062
13117 | TGATEWAY_2G | 2 | North | YES | 0.15714 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.32786 | 130 | 130 | 20.4279 | 130 |  |  | 0.32786 | 42.6212
13118 | TGATEWAY_3G | 3 | North | YES | 0.15714 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.32786 | 148 | 148 | 23.2564 | 148 |  |  | 0.32786 | 48.5227
13119 | TGATEWAY_4G | 4 | North | YES | 0.15714 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.32786 | 399 | 399 | 62.6981 | 399 |  |  | 0.32786 | 130.8144
3348 | CHAMPION_1G | MB | North | YES | 0.15768 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.3284 | 0 | 0 | 0 | 0 |  |  | 0.3284 | 0
3309 | ASPN_G | 1 | North | YES | 0.15775 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.32847 | 50 | 50 | 7.8874 | 50 |  |  | 0.32847 | 16.4233
3107 | STRYKER_1G | 1 | North | YES | 0.15784 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.32856 | 182 | 182 | 28.7272 | 182 |  |  | 0.32856 | 59.7979
3108 | STRYKER_2G | 2 | North | YES | 0.15784 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.32856 | 484 | 484 | 76.3955 | 484 |  |  | 0.32856 | 159.0229
13134 | CALFREST_4G | 4 | North | YES | 0.1638 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.33452 | 151.5 | 151.5 | 24.8163 | 151.5 |  |  | 0.33452 | 50.68
13135 | CALFREST_5G | 5 | North | YES | 0.1638 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.33452 | 152.3 | 152.3 | 24.9473 | 152.3 |  |  | 0.33452 | 50.9477
13136 | CALFREST_6G | 6 | North | YES | 0.1638 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.33452 | 177.5 | 177.5 | 29.0752 | 177.5 |  |  | 0.33452 | 59.3776
13131 | CALFREST_1G | 1 | North | YES | 0.16409 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.33481 | 150.7 | 150.7 | 24.7288 | 150.7 |  |  | 0.33481 | 50.456
13132 | CALFREST_2G | 2 | North | YES | 0.16409 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.33481 | 151 | 151 | 24.778 | 151 |  |  | 0.33481 | 50.5564
13133 | CALFREST_3G | 3 | North | YES | 0.16409 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.33481 | 177.4 | 177.4 | 29.1101 | 177.4 |  |  | 0.33481 | 59.3954
3381 | BBRN_1G | 1 | North | YES | 0.16547 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.33618 | 0 | 618 | 102.258 | 618 |  |  | 0.33618 | 207.7616
3382 | BBRN_2G | 2 | North | YES | 0.16547 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.33618 | 0 | 589 | 97.4595 | 589 |  |  | 0.33618 | 198.0122
48721 | LEG_1___1 | 1 | North | YES | 0.18228 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.353 | 0 | 827 | 150.7456 | 827 |  |  | 0.353 | 291.9291
48722 | LEG_2___2 | 2 | North | YES | 0.18228 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.353 | 0 | 819 | 149.2873 | 819 |  |  | 0.353 | 289.1052
39960 | TNTNPONE_18 | 1 | North | YES | 0.19301 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.36372 | 0 | 152.3 | 29.3947 | 152.3 |  |  | 0.36372 | 55.395
39970 | TNTNPONE_28 | 1 | North | YES | 0.19301 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.36372 | 0 | 153 | 29.5298 | 153 |  |  | 0.36372 | 55.6496
48671 | FTR_GT1_5105 | 1 | North | YES | 0.19668 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.3674 | 154.2 | 154.2 | 30.3288 | 154.2 |  |  | 0.3674 | 56.6535
48672 | FTR_GT2_5110 | 2 | North | YES | 0.19668 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.3674 | 159 | 159 | 31.2729 | 159 |  |  | 0.3674 | 58.417
48673 | FTR_GT3_5085 | 3 | North | YES | 0.19668 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.3674 | 158 | 158 | 31.0762 | 158 |  |  | 0.3674 | 58.0496
48674 | FTR_CN4_5095 | 4 | North | YES | 0.19668 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.3674 | 380 | 380 | 74.7403 | 380 |  |  | 0.3674 | 139.613
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.19756 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.36828 | 48 | 48 | 9.4831 | 48 |  |  | 0.36828 | 17.6776
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.19756 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.36828 | 46 | 46 | 9.088 | 46 |  |  | 0.36828 | 16.941
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.19756 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.36828 | 105 | 105 | 20.7443 | 105 |  |  | 0.36828 | 38.6697
32886 | BRYN_ATKINS3 | MB | North | YES | 0.20233 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.20233 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.20233 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.37305 | 17 | 17 | 3.4397 | 17 |  |  | 0.37305 | 6.3419
32890 | BRYN_ATKINS4 | MB | North | YES | 0.20233 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.20233 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.20478 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.3755 | 32 | 32 | 6.5531 | 32 |  |  | 0.3755 | 12.0161
990 | GIBN_CREK_G1 | 1 | North | YES | 0.2205 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.39121 | 0 | 463 | 102.0896 | 463 |  |  | 0.39121 | 181.132
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Bound Gen
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | max of zone correlation | 0.10737 |  |  | Neg PTDF weight | Pos PTDF weight
13432 | SANDOW_5G | 5 | South | YES | 0.044563 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.10737 | 0 | 581 |  |  |  |  | -0.10737 | 0 |  |  |  |  | 0 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.025209 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.12673 | 0 | 580 |  |  |  |  | -0.12673 | 0 |  |  |  |  | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.009199 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 |  |  |  |  | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.009199 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 |  |  | Weighted Shift Factors |  | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.009199 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.14274 | 0 | 0 |  |  |  |  | -0.14274 | 0 |  |  | North | 0.15194 | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.008542 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.14339 | 0 | 0 |  |  |  |  | -0.14339 | 0 |  |  | Houston | -0.17072 | 0 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.002445 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 |  |  |  |  | 0 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.002445 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 | Houston |  |  |  | 0 | 0
88253 | HAMILTON | F | South | YES | 0.002445 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.14949 | 0 | 0 |  |  |  |  | -0.14949 | 0 | Line Rating |  | 1793 |  | 0 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.15194 | 15 | 15 |  |  |  |  | -0.15194 | -2.2791 | Impact Counter to Zone: |  | 0 |  | 0 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 |  |  | 0% |  | 0 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 |  |  |  |  | 0 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | North |  |  |  | 0 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | Line Rating |  | 1793 |  | 0 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 | Impact Counter to Zone: |  | 0 |  | 0 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 |  |  | 0% |  | 0 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 |  |  |  |  | 0 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.15194 | 0 | 0 |  |  |  |  | -0.15194 | 0 |  |  |  |  | 0 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.15194 | 0 | 0 |  |  | 0 | 0 | -0.15194 | 0 |  |  |  |  | 0 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.000339 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.15228 | 0 | 0 |  |  |  |  | -0.15228 | 0 |  |  |  |  | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.000339 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.15228 | 0 | 0 |  |  |  |  | -0.15228 | 0 |  |  |  |  | 0 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.000571 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.15251 | 423.3 | 423.3 |  |  |  |  | -0.15251 | -64.5566 |  |  |  |  | 0 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.003309 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.15525 | 0 | 0 |  |  |  |  | -0.15525 | 0 |  |  |  |  | 0 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.003309 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.15525 | 0 | 0 |  |  |  |  | -0.15525 | 0 |  |  |  |  | 0 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.008971 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 |  |  |  |  | 0 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.008971 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 |  |  |  |  | 0 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.008971 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.16091 | 0 | 0 |  |  |  |  | -0.16091 | 0 |  |  |  |  | 0 | 0
9005 | DECKR_G6 | 6 | South | YES | -0.01105 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.16299 | 47 | 47 |  |  |  |  | -0.16299 | -7.6604 |  |  |  |  | 0 | 0
9003 | DECKR_G4 | 4 | South | YES | -0.01105 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.16299 | 44 | 44 |  |  |  |  | -0.16299 | -7.1714 |  |  |  |  | 0 | 0
9004 | DECKR_G5 | 5 | South | YES | -0.01105 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.16299 | 44 | 44 |  |  |  |  | -0.16299 | -7.1714 |  |  |  |  | 0 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.01105 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.16299 | 42 | 42 |  |  |  |  | -0.16299 | -6.8455 |  |  |  |  | 0 | 0
9001 | DECKR_G2 | 2 | South | YES | -0.012116 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.16405 | 426 | 426 |  |  |  |  | -0.16405 | -69.8865 |  |  |  |  | 0 | 0
9000 | DECKR_G1 | 1 | South | YES | -0.012116 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.16405 | 321 | 321 |  |  |  |  | -0.16405 | -52.661 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.012215 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.16415 | 0 | 0 |  |  |  |  | -0.16415 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.012215 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.16415 | 0 | 0 |  |  |  |  | -0.16415 | 0 |  |  |  |  | 0 | 0
9020 | SANDHG5A | 5A | South | YES | -0.013615 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.16555 | 155 | 155 |  |  |  |  | -0.16555 | -25.6605 |  |  |  |  | 0 | 0
9021 | SANDHG5C | 5C | South | YES | -0.013615 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.16555 | 148 | 148 |  |  |  |  | -0.16555 | -24.5017 |  |  |  |  | 0 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.013615 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.16555 | 49 | 49 |  |  |  |  | -0.16555 | -8.112 |  |  |  |  | 0 | 0
9019 | SANDH_G4 | 4 | South | YES | -0.013615 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.16555 | 47 | 47 |  |  |  |  | -0.16555 | -7.7809 |  |  |  |  | 0 | 0
9017 | SANDH_G2 | 2 | South | YES | -0.013615 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.16555 | 46 | 46 |  |  |  |  | -0.16555 | -7.6154 |  |  |  |  | 0 | 0
9018 | SANDH_G3 | 3 | South | YES | -0.013615 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.16555 | 46 | 46 |  |  |  |  | -0.16555 | -7.6154 |  |  |  |  | 0 | 0
8262 | ELPS | 1 | South | YES | -0.014069 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.16601 | 0 | 0 |  |  |  |  | -0.16601 | 0 |  |  |  |  | 0 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.017461 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.1694 | 232.6 | 232.6 |  |  |  |  | -0.1694 | -39.402 |  |  |  |  | 0 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.017461 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.1694 | 152.5 | 152.5 |  |  |  |  | -0.1694 | -25.8332 |  |  |  |  | 0 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.017461 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.1694 | 149.5 | 149.5 |  |  |  |  | -0.1694 | -25.325 |  |  |  |  | 0 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.019922 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.17186 | 175 | 175 |  |  |  |  | -0.17186 | -30.0753 |  |  |  |  | 0 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.019922 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.17186 | 160 | 160 |  |  |  |  | -0.17186 | -27.4974 |  |  |  |  | 0 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.019922 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.17186 | 158 | 158 |  |  |  |  | -0.17186 | -27.1537 |  |  |  |  | 0 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.022083 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.17402 | 329 | 329 |  |  |  |  | -0.17402 | -57.2526 |  |  |  |  | 0 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.022083 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.17402 | 139 | 139 |  |  |  |  | -0.17402 | -24.1888 |  |  |  |  | 0 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.022083 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.17402 | 132 | 132 |  |  |  |  | -0.17402 | -22.9706 |  |  |  |  | 0 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.031678 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.18361 | 0 | 0 |  |  |  |  | -0.18361 | 0 |  |  |  |  | 0 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.036626 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.18856 | 226.7 | 226.7 |  |  |  |  | -0.18856 | -42.7472 |  |  |  |  | 0 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.036626 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.18856 | 225 | 225 |  |  |  |  | -0.18856 | -42.4267 |  |  |  |  | 0 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.036626 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.18856 | 224.6 | 224.6 |  |  |  |  | -0.18856 | -42.3512 |  |  |  |  | 0 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.036626 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.18856 | 223.9 | 223.9 |  |  |  |  | -0.18856 | -42.2192 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.039201 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.19114 | 50 | 50 |  |  |  |  | -0.19114 | -9.5569 |  |  |  |  | 0 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.039706 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.19164 | 0 | 606 |  |  |  |  | -0.19164 | 0 |  |  |  |  | 0 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.039706 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.19164 | 0 | 598 |  |  |  |  | -0.19164 | 0 |  |  |  |  | 0 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.039835 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.19177 | 0 | 436 |  |  |  |  | -0.19177 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.041131 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.041131 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.041131 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.19307 | 0 | 0 |  |  |  |  | -0.19307 | 0 |  |  |  |  | 0 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.041424 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.19336 | 293 | 293 |  |  |  |  | -0.19336 | -56.6547 |  |  |  |  | 0 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.041424 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.19336 | 154 | 154 |  |  |  |  | -0.19336 | -29.7776 |  |  |  |  | 0 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.041424 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.19336 | 148 | 148 |  |  |  |  | -0.19336 | -28.6174 |  |  |  |  | 0 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.041424 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.19336 | 148 | 148 |  |  |  |  | -0.19336 | -28.6174 |  |  |  |  | 0 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.042126 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.19406 | 0 | 0 |  |  |  |  | -0.19406 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.044521 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.19646 | 0 | 0 |  |  |  |  | -0.19646 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.044521 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.19646 | 0 | 0 |  |  |  |  | -0.19646 | 0 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.044585 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.19652 | 8.4 | 8.4 |  |  |  |  | -0.19652 | -1.6508 |  |  |  |  | 0 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.045929 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.19787 | 203 | 203 |  |  |  |  | -0.19787 | -40.1668 |  |  |  |  | 0 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.045929 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.19787 | 182 | 182 |  |  |  |  | -0.19787 | -36.0116 |  |  |  |  | 0 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.045929 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.19787 | 149 | 149 |  |  |  |  | -0.19787 | -29.482 |  |  |  |  | 0 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.045929 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.19787 | 147 | 147 |  |  |  |  | -0.19787 | -29.0863 |  |  |  |  | 0 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.045929 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.19787 | 146 | 146 |  |  |  |  | -0.19787 | -28.8884 |  |  |  |  | 0 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.045929 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.19787 | 138 | 138 |  |  |  |  | -0.19787 | -27.3055 |  |  |  |  | 0 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.046913 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.19885 | 407 | 407 |  |  |  |  | -0.19885 | -80.9319 |  |  |  |  | 0 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.046925 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.19886 | 24.3 | 24.3 |  |  |  |  | -0.19886 | -4.8323 |  |  |  |  | 0 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.046925 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.19886 | 24 | 24 |  |  |  |  | -0.19886 | -4.7727 |  |  |  |  | 0 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.046925 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.19886 | 23.9 | 23.9 |  |  |  |  | -0.19886 | -4.7528 |  |  |  |  | 0 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | -0.046951 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.19889 | 0 | 430 |  |  |  |  | -0.19889 | 0 |  |  |  |  | 0 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.046951 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.19889 | 0 | 430 |  |  |  |  | -0.19889 | 0 |  |  |  |  | 0 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.046953 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.19889 | 418 | 418 |  |  |  |  | -0.19889 | -83.136 |  |  |  |  | 0 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | -0.046953 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.19889 | 400 | 400 |  |  |  |  | -0.19889 | -79.556 |  |  |  |  | 0 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | -0.046973 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.19891 | 89 | 89 |  |  |  |  | -0.19891 | -17.703 |  |  |  |  | 0 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.046973 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.19891 | 58 | 58 |  |  |  |  | -0.19891 | -11.5368 |  |  |  |  | 0 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | -0.046973 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.19891 | 45 | 45 |  |  |  |  | -0.19891 | -8.9509 |  |  |  |  | 0 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | -0.046973 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.19891 | 44 | 44 |  |  |  |  | -0.19891 | -8.752 |  |  |  |  | 0 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | -0.046973 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.19891 | 44 | 44 |  |  |  |  | -0.19891 | -8.752 |  |  |  |  | 0 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | -0.046973 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.19891 | 43 | 43 |  |  |  |  | -0.19891 | -8.5531 |  |  |  |  | 0 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.046999 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.19894 | 151 | 151 |  |  |  |  | -0.19894 | -30.0393 |  |  |  |  | 0 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.046999 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.19894 | 95 | 95 |  |  |  |  | -0.19894 | -18.8989 |  |  |  |  | 0 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.046999 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.19894 | 61 | 61 |  |  |  |  | -0.19894 | -12.1351 |  |  |  |  | 0 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.047121 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.19906 | 216 | 216 |  |  |  |  | -0.19906 | -42.9965 |  |  |  |  | 0 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.047121 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.19906 | 215 | 215 |  |  |  |  | -0.19906 | -42.7975 |  |  |  |  | 0 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | -0.04861 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.20055 | 174 | 174 |  |  |  |  | -0.20055 | -34.8952 |  |  |  |  | 0 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.04861 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.20055 | 155 | 155 |  |  |  |  | -0.20055 | -31.0848 |  |  |  |  | 0 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.04861 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.20055 | 155 | 155 |  |  |  |  | -0.20055 | -31.0848 |  |  |  |  | 0 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.04973 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.20167 | 0 | 562 |  |  |  |  | -0.20167 | 0 |  |  |  |  | 0 | 0
8189 | CUECPL2A | 1 | South | YES | -0.053362 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.2053 | 0 | 0 |  |  |  |  | -0.2053 | 0 |  |  |  |  | 0 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.055475 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.20741 | 0 | 396.3 |  |  |  |  | -0.20741 | 0 |  |  |  |  | 0 | 0
80265 | LARECU40A | 4 | South | YES | -0.055804 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.20774 | 100 | 100 |  |  |  |  | -0.20774 | -20.7741 |  |  |  |  | 0 | 0
80266 | LARECU50A | 5 | South | YES | -0.055804 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.20774 | 100 | 100 |  |  |  |  | -0.20774 | -20.7741 |  |  |  |  | 0 | 0
80012 | LAR | F | South | YES | -0.055808 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.20774 | 0 | 0 |  |  |  |  | -0.20774 | 0 |  |  |  |  | 0 | 0
88299 | ZAPATA | F | South | YES | -0.062149 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.21409 | 0 | 0 |  |  |  |  | -0.21409 | 0 |  |  |  |  | 0 | 0
88198 | BEEVILLE | F | South | YES | -0.065317 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.21725 | 0 | 0 |  |  |  |  | -0.21725 | 0 |  |  |  |  | 0 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.066451 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0 |  |  |  |  | 0 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.066451 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0 |  |  |  |  | 0 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.066451 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.21839 | 0 | 0 |  |  |  |  | -0.21839 | 0 |  |  |  |  | 0 | 0
88508 | FALFURRI | F | South | YES | -0.067258 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.21919 | 0 | 0 |  |  |  |  | -0.21919 | 0 |  |  |  |  | 0 | 0
8161 | COLETO0A | 1 | South | YES | -0.068894 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.22083 | 0 | 633 |  |  |  |  | -0.22083 | 0 |  |  |  |  | 0 | 0
8935 | FGNTS201 | 3 | South | YES | -0.070946 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.22288 | 173 | 173 |  |  |  |  | -0.22288 | -38.5587 |  |  |  |  | 0 | 0
8934 | FGNTS101 | 2 | South | YES | -0.070946 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.22288 | 147.9 | 147.9 |  |  |  |  | -0.22288 | -32.9644 |  |  |  |  | 0 | 0
8933 | FGNTS001 | 1 | South | YES | -0.070946 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.22288 | 146.5 | 146.5 |  |  |  |  | -0.22288 | -32.6523 |  |  |  |  | 0 | 0
8983 | HECN3 | 3 | South | YES | -0.071702 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.22364 | 171.9 | 171.9 |  |  |  |  | -0.22364 | -38.4435 |  |  |  |  | 0 | 0
8981 | HECN1 | 1 | South | YES | -0.071702 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.22364 | 144.8 | 144.8 |  |  |  |  | -0.22364 | -32.3829 |  |  |  |  | 0 | 0
8982 | HECN2 | 2 | South | YES | -0.071702 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.22364 | 144.1 | 144.1 |  |  |  |  | -0.22364 | -32.2264 |  |  |  |  | 0 | 0
8938 | MVGN#3 | 3 | South | YES | -0.071704 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.22364 | 250.9 | 250.9 |  |  |  |  | -0.22364 | -56.1115 |  |  |  |  | 0 | 0
8937 | MVGN#2 | 2 | South | YES | -0.071704 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.22364 | 216.7 | 216.7 |  |  |  |  | -0.22364 | -48.463 |  |  |  |  | 0 | 0
8936 | MVGN#1 | 1 | South | YES | -0.071704 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.22364 | 216.6 | 216.6 |  |  |  |  | -0.22364 | -48.4406 |  |  |  |  | 0 | 0
80003 | MILHWYS | F | South | YES | -0.072035 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.22397 | 0 | 0 |  |  |  |  | -0.22397 | 0 |  |  |  |  | 0 | 0
5935 | SI_RAY10 | 10 | South | YES | -0.072036 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.22397 | 47 | 47 |  |  |  |  | -0.22397 | -10.5267 |  |  |  |  | 0 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.072036 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.22397 | 38 | 38 |  |  |  |  | -0.22397 | -8.511 |  |  |  |  | 0 | 0
5933 | SI_RAY6 | 6 | South | YES | -0.072036 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.22397 | 19.3 | 19.3 |  |  |  |  | -0.22397 | -4.3227 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 1 | South | YES | -0.072238 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 94 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 2 | South | YES | -0.072238 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 41 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 3 | South | YES | -0.072238 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 38 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 4 | South | YES | -0.072238 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 19 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 1 | South | YES | -0.072238 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 94 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 2 | South | YES | -0.072238 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 36 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 3 | South | YES | -0.072238 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 43 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 4 | South | YES | -0.072238 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 22 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.072238 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 148 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.072238 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 50 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.072238 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 55 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.072238 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.22417 | 0 | 50 |  |  |  |  | -0.22417 | 0 |  |  |  |  | 0 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.072335 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.22427 | 0 | 0 |  |  |  |  | -0.22427 | 0 |  |  |  |  | 0 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.072936 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.22487 | 0 | 0 |  |  |  |  | -0.22487 | 0 |  |  |  |  | 0 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.07299 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.22493 | 0 | 0 |  |  |  |  | -0.22493 | 0 |  |  |  |  | 0 | 0
8506 | VAL #1 | 1 | South | YES | -0.073101 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.22504 | 0 | 0 |  |  |  |  | -0.22504 | 0 |  |  |  |  | 0 | 0
8507 | VAL #2 | 2 | South | YES | -0.073101 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.22504 | 0 | 0 |  |  |  |  | -0.22504 | 0 |  |  |  |  | 0 | 0
80263 | B_DAVIS31A | 3 | South | YES | -0.073242 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.22518 | 180 | 180 |  |  |  |  | -0.22518 | -40.5322 |  |  |  |  | 0 | 0
80264 | B_DAVIS41A | 4 | South | YES | -0.073242 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.22518 | 180 | 180 |  |  |  |  | -0.22518 | -40.5322 |  |  |  |  | 0 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.073242 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.22518 | 0 | 0 |  |  |  |  | -0.22518 | 0 |  |  |  |  | 0 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.073242 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.22518 | 0 | 0 |  |  |  |  | -0.22518 | 0 |  |  |  |  | 0 | 0
8456 | COSW#1 | 1 | South | YES | -0.07341 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.22535 | 0 | 0 |  |  |  |  | -0.22535 | 0 |  |  |  |  | 0 | 0
8457 | COSW#2 | 2 | South | YES | -0.07341 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.22535 | 0 | 0 |  |  |  |  | -0.22535 | 0 |  |  |  |  | 0 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.07349 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0 |  |  |  |  | 0 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.07349 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0 |  |  |  |  | 0 | 0
8562 | CNOPST1 | 3 | South | YES | -0.07349 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.22543 | 0 | 0 |  |  |  |  | -0.22543 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | 7 | South | YES | -0.073507 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.22544 | 367 | 367 |  |  |  |  | -0.22544 | -82.7379 |  |  |  |  | 0 | 0
8442 | NBEC7 | MB | South | YES | -0.073507 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.22544 | 0 | 0 |  |  |  |  | -0.22544 | 0 |  |  |  |  | 0 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.074954 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 |  |  |  |  | 0 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.074954 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 |  |  |  |  | 0 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.074954 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 |  |  |  |  | 0 | 0
8930 | ICPGN10A | 1 | South | YES | -0.074954 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 |  |  |  |  | 0 | 0
8931 | ICPGN20A | 2 | South | YES | -0.074954 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 |  |  |  |  | 0 | 0
8932 | ICPGN30A | 3 | South | YES | -0.074954 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 |  |  |  |  | 0 | 0
80223 | REYSHR G | 1 | South | YES | -0.074954 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.22689 | 0 | 0 |  |  |  |  | -0.22689 | 0 |  |  |  |  | 0 | 0
8174 | VICEC61A | 6 | South | YES | -0.075848 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.22778 | 188 | 188 |  |  |  |  | -0.22778 | -42.8236 |  |  |  |  | 0 | 0
8173 | VICEC51A | 5 | South | YES | -0.075848 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.22778 | 144 | 144 |  |  |  |  | -0.22778 | -32.801 |  |  |  |  | 0 | 0
5512 | RAYBURNCC8 | 1 | South | YES | -0.077106 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.22904 | 49.3 | 49.3 |  |  |  |  | -0.22904 | -11.2918 |  |  |  |  | 0 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.077106 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.22904 | 47.7 | 47.7 |  |  |  |  | -0.22904 | -10.9253 |  |  |  |  | 0 | 0
5511 | RAYBURNCC7 | 1 | South | YES | -0.077106 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.22904 | 47.5 | 47.5 |  |  |  |  | -0.22904 | -10.8795 |  |  |  |  | 0 | 0
5509 | RAYBURNCC10 | 1 | South | YES | -0.077106 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.22904 | 37.3 | 37.3 |  |  |  |  | -0.22904 | -8.5433 |  |  |  |  | 0 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.077236 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.22917 | 0 | 0 |  |  |  |  | -0.22917 | 0 |  |  |  |  | 0 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.077767 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.2297 | 22 | 22 |  |  |  |  | -0.2297 | -5.0535 |  |  |  |  | 0 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | -0.077767 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.2297 | 11 | 11 |  |  |  |  | -0.2297 | -2.5267 |  |  |  |  | 0 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | -0.077767 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.2297 | 11 | 11 |  |  |  |  | -0.2297 | -2.5267 |  |  |  |  | 0 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.079573 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.23151 | 0 | 0 |  |  |  |  | -0.23151 | 0 |  |  |  |  | 0 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.079573 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.23151 | 0 | 0 |  |  |  |  | -0.23151 | 0 |  |  |  |  | 0 | 0
80227 | AIRCO G | 1 | South | YES | -0.080386 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.23232 | 0 | 0 |  |  |  |  | -0.23232 | 0 |  |  |  |  | 0 | 0
8147 | UCAR #2 | 10 | South | YES | -0.080967 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 |  |  |  |  | 0 | 0
8148 | UCAR #1 | 2 | South | YES | -0.080967 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 8 | South | YES | -0.080967 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 9 | South | YES | -0.080967 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 |  |  |  |  | 0 | 0
80138 | CSDR7 | 7 | South | YES | -0.080967 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 5 | South | YES | -0.080967 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 6 | South | YES | -0.080967 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 |  |  |  |  | 0 | 0
80140 | CSDR11 | 11 | South | YES | -0.080967 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.2329 | 0 | 0 |  |  |  |  | -0.2329 | 0 |  |  |  |  | 0 | 0
80226 | ALCOA G | 1 | South | YES | -0.084515 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.23645 | 0 | 0 |  |  |  |  | -0.23645 | 0 |  |  |  |  | 0 | 0
8134 | FOR #1 | 1 | South | YES | -0.085582 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
8138 | FOR #2 | 2 | South | YES | -0.085582 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
8153 | FOR #3 | 3 | South | YES | -0.085582 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
8154 | FOR #4 | 4 | South | YES | -0.085582 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
8155 | FOR #5 | 5 | South | YES | -0.085582 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
8156 | FOR #6 | 6 | South | YES | -0.085582 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
8157 | FOR #7 | 7 | South | YES | -0.085582 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
80051 | FOR #8 | 8 | South | YES | -0.085582 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
80052 | FOR #9 | 9 | South | YES | -0.085582 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
80053 | FOR #10 | 10 | South | YES | -0.085582 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.23752 | 0 | 0 |  |  |  |  | -0.23752 | 0 |  |  |  |  | 0 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.12209 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.27403 | 0 | 0 |  |  | 0 | 0 | -0.27403 | 0 |  |  |  |  | 0 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.12209 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.27403 | 0 | 0 |  |  | 0 | 0 | -0.27403 | 0 |  |  |  |  | 0 | 0
60202 | FRNDDRCS | F | West | YES | 0.1063 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.27701 | 0 | 0 |  |  |  |  | 0.27701 | 0 |  |  |  |  | 0 | 0
48733 | CBE_ST12 | 1 | Houston | YES | -0.12734 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.27928 | 105 | 105 |  |  | -13.371 | 105 | -0.27928 | -29.3244 |  |  |  |  | 0 | 0
48736 | CBE_ST34 | 1 | Houston | YES | -0.12734 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.27928 | 105 | 105 |  |  | -13.371 | 105 | -0.27928 | -29.3244 |  |  |  |  | 0 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253 |  |  |  |  | 0 | 0
48732 | CBE_GT2 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253 |  |  |  |  | 0 | 0
48734 | CBE_GT3 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253 |  |  |  |  | 0 | 0
48735 | CBE_GT4 | 1 | Houston | YES | -0.12734 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.27928 | 76 | 76 |  |  | -9.6781 | 76 | -0.27928 | -21.2253 |  |  |  |  | 0 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.13008 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.28202 | 0 | 0 |  |  | 0 | 0 | -0.28202 | 0 |  |  |  |  | 0 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | 0.11148 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.28219 | 75 | 75 | 8.3608 | 75 |  |  | 0.28219 | 21.1646 |  |  |  |  | 0 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | 0.11148 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.28219 | 222 | 222 | 24.7479 | 222 |  |  | 0.28219 | 62.6472 |  |  |  |  | 0 | 0
3403 | THOUSE_1G | 1 | North | YES | 0.11301 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.28372 | 563 | 563 | 63.6224 | 563 |  |  | 0.28372 | 159.7365 |  |  |  |  | 0 | 0
3404 | THOUSE_2G | 2 | North | YES | 0.11301 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.28372 | 807 | 807 | 91.1958 | 807 |  |  | 0.28372 | 228.9651 |  |  |  |  | 0 | 0
239 | BOSQUESW502 | 1 | North | YES | 0.11477 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.28549 | 149 | 149 | 17.1013 | 149 |  |  | 0.28549 | 42.5383 |  |  |  |  | 0 | 0
247 | BOSQUESW501 | 2 | North | YES | 0.11477 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.28549 | 156 | 156 | 17.9047 | 156 |  |  | 0.28549 | 44.5367 |  |  |  |  | 0 | 0
238 | BOSQUESW505 | 1 | North | YES | 0.11477 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.28549 | 255 | 255 | 29.2674 | 255 |  |  | 0.28549 | 72.8004 |  |  |  |  | 0 | 0
253 | BOSQUESW804 | 2 | North | YES | 0.11786 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.28857 | 80 | 80 | 9.4284 | 80 |  |  | 0.28857 | 23.0858 |  |  |  |  | 0 | 0
251 | BOSQUESW803 | 2 | North | YES | 0.11786 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.28857 | 150 | 150 | 17.6782 | 150 |  |  | 0.28857 | 43.2859 |  |  |  |  | 0 | 0
60018 | DSKY1 | 1 | West | YES | 0.11862 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.28934 | 0 | 84 |  |  |  |  | 0.28934 | 24.3045 |  |  |  |  | 0 | 0
60000 | DSKY2 | 1 | West | YES | 0.11883 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.28955 | 0 | 76.5 |  |  |  |  | 0.28955 | 22.1502 |  |  |  |  | 0 | 0
60017 | ORNNWP1 | 1 | West | YES | 0.11942 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.29014 | 0 | 80 |  |  |  |  | 0.29014 | 23.2109 |  |  |  |  | 0 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | 0.12178 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.2925 | 0 | 150 |  |  |  |  | 0.2925 | 43.8744 |  |  |  |  | 0 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.12184 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.29256 | 0 | 80 |  |  |  |  | 0.29256 | 23.405 |  |  |  |  | 0 | 0
60016 | WOODWRD11A | 1 | West | YES | 0.12186 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.29258 | 0 | 80 |  |  |  |  | 0.29258 | 23.4063 |  |  |  |  | 0 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.14065 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.14065 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.14065 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.14065 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.14065 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.14065 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.14065 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.14065 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.14065 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.14065 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.14065 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.14065 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.14065 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.14065 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.14065 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.14065 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.14065 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.14065 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.14065 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.14065 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.29259 | 0 | 0 |  |  | 0 | 0 | -0.29259 | 0 |  |  |  |  | 0 | 0
60005 | KING_SE1A | 1 | West | YES | 0.12194 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.29266 | 0 | 40 |  |  |  |  | 0.29266 | 11.7065 |  |  |  |  | 0 | 0
6016 | SWMESA | 1 | West | YES | 0.12194 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.29266 | 0 | 75 |  |  |  |  | 0.29266 | 21.9496 |  |  |  |  | 0 | 0
60003 | KING_NE1A | 1 | West | YES | 0.12194 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29266 | 0 | 80 |  |  |  |  | 0.29266 | 23.4129 |  |  |  |  | 0 | 0
60201 | RIO DRCS | F | West | YES | 0.12207 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.29279 | 0 | 0 |  |  |  |  | 0.29279 | 0 |  |  |  |  | 0 | 0
244 | WHITNYDM01 | 1 | North | YES | 0.12239 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.2931 | 0 | 0 | 0 | 0 |  |  | 0.2931 | 0 |  |  |  |  | 0 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.12239 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.2931 | 0 | 0 | 0 | 0 |  |  | 0.2931 | 0 |  |  |  |  | 0 | 0
60007 | KING_SW1A | 1 | West | YES | 0.12239 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29311 | 0 | 80 |  |  |  |  | 0.29311 | 23.4485 |  |  |  |  | 0 | 0
60019 | KING_NW1A | 1 | West | YES | 0.12239 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29311 | 0 | 80 |  |  |  |  | 0.29311 | 23.4485 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.14503 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.29697 | 0 | 0 |  |  | 0 | 0 | -0.29697 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.14503 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.29697 | 0 | 0 |  |  | 0 | 0 | -0.29697 | 0 |  |  |  |  | 0 | 0
1349 | WESTXWIN_1G | 1 | West | YES | 0.12878 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.2995 | 0 | 6.6 |  |  |  |  | 0.2995 | 1.9767 |  |  |  |  | 0 | 0
1350 | NWPWRG1_1G | 1 | West | YES | 0.12878 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.2995 | 0 | 34.3 |  |  |  |  | 0.2995 | 10.2727 |  |  |  |  | 0 | 0
60057 | CALLAHAN1A | 1 | West | YES | 0.12912 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.29984 | 0 | 114 |  |  |  |  | 0.29984 | 34.1821 |  |  |  |  | 0 | 0
1002 | PBCTAGE_1G | A | West | YES | 0.12924 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.29996 | 66 | 66 |  |  |  |  | 0.29996 | 19.7975 |  |  |  |  | 0 | 0
1003 | PBCTBGE_2G | B | West | YES | 0.12924 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.29996 | 66 | 66 |  |  |  |  | 0.29996 | 19.7975 |  |  |  |  | 0 | 0
1004 | PBCTCGE_3G | C | West | YES | 0.12924 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.29996 | 67 | 67 |  |  |  |  | 0.29996 | 20.0975 |  |  |  |  | 0 | 0
1006 | PBCTEGE_5G | E | West | YES | 0.12924 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.29996 | 67 | 67 |  |  |  |  | 0.29996 | 20.0975 |  |  |  |  | 0 | 0
1005 | PBCTDGE_4G | D | West | YES | 0.12924 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.29996 | 68 | 68 |  |  |  |  | 0.29996 | 20.3975 |  |  |  |  | 0 | 0
1007 | PB5GEN_6G | 5 | West | YES | 0.12924 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.29996 | 114 | 114 |  |  |  |  | 0.29996 | 34.1958 |  |  |  |  | 0 | 0
1008 | PB6GEN_7G | 6 | West | YES | 0.12924 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.29996 | 515 | 515 |  |  |  |  | 0.29996 | 154.4808 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.12932 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.30003 | 0 | 30 |  |  |  |  | 0.30003 | 9.001 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.12932 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.30003 | 0 | 35 |  |  |  |  | 0.30003 | 10.5012 |  |  |  |  | 0 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.12945 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.30016 | 0 | 112.5 |  |  |  |  | 0.30016 | 33.7683 |  |  |  |  | 0 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.12945 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 149.5 |  |  |  |  | 0.30016 | 44.8743 |  |  |  |  | 0 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.12945 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 186 |  |  |  |  | 0.30016 | 55.8303 |  |  |  |  | 0 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.12945 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.30016 | 0 | 214.5 |  |  |  |  | 0.30016 | 64.3849 |  |  |  |  | 0 | 0
11147 | NOTREES_1G | 1 | West | YES | 0.12945 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.30017 | 0 | 149 |  |  |  |  | 0.30017 | 44.7256 |  |  |  |  | 0 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | 0.1298 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.30052 | 0 | 150 |  |  |  |  | 0.30052 | 45.0783 |  |  |  |  | 0 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.14876 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0 |  |  |  |  | 0 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.14876 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0 |  |  |  |  | 0 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.14876 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0 |  |  |  |  | 0 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.14876 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.30069 | 0 | 0 |  |  | 0 | 0 | -0.30069 | 0 |  |  |  |  | 0 | 0
1320 | BSP 1 | 1 | West | YES | 0.13011 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.30083 | 0 | 0 |  |  |  |  | 0.30083 | 0 |  |  |  |  | 0 | 0
1326 | STANTONW_8 | 1 | West | YES | 0.13024 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.30095 | 0 | 100.5 |  |  |  |  | 0.30095 | 30.2459 |  |  |  |  | 0 | 0
11022 | TIEHVCG_2G | 1 | West | YES | 0.13028 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.301 | 132.4 | 132.4 |  |  |  |  | 0.301 | 39.8524 |  |  |  |  | 0 | 0
11023 | TIEHVCG_3G | 1 | West | YES | 0.13028 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.301 | 137.4 | 137.4 |  |  |  |  | 0.301 | 41.3574 |  |  |  |  | 0 | 0
11021 | TIEHVCG_1G | 1 | West | YES | 0.13028 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.301 | 142.1 | 142.1 |  |  |  |  | 0.301 | 42.7721 |  |  |  |  | 0 | 0
11024 | TIEHVCG_4G | 1 | West | YES | 0.13028 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.301 | 147 | 147 |  |  |  |  | 0.301 | 44.247 |  |  |  |  | 0 | 0
11020 | TIEHVSG_1G | 1 | West | YES | 0.13028 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.301 | 208.2 | 208.2 |  |  |  |  | 0.301 | 62.6681 |  |  |  |  | 0 | 0
11025 | TIEHVSG_2G | 1 | West | YES | 0.13028 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.301 | 213.2 | 213.2 |  |  |  |  | 0.301 | 64.1731 |  |  |  |  | 0 | 0
11001 | NAV1CT | 1 | West | YES | 0.13029 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.30101 | 70.4 | 70.4 |  |  |  |  | 0.30101 | 21.1912 |  |  |  |  | 0 | 0
11009 | NAV2CT | 1 | West | YES | 0.13029 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.30101 | 71.4 | 71.4 |  |  |  |  | 0.30101 | 21.4922 |  |  |  |  | 0 | 0
11012 | NAV4CT | 1 | West | YES | 0.13029 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30101 | 80 | 80 |  |  |  |  | 0.30101 | 24.0809 |  |  |  |  | 0 | 0
11013 | NAV5CT | 1 | West | YES | 0.13029 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30101 | 80 | 80 |  |  |  |  | 0.30101 | 24.0809 |  |  |  |  | 0 | 0
11011 | NAV3ST | 1 | West | YES | 0.13029 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.30101 | 92.8 | 92.8 |  |  |  |  | 0.30101 | 27.9339 |  |  |  |  | 0 | 0
11014 | NAV6ST | 1 | West | YES | 0.13029 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.30101 | 115 | 115 |  |  |  |  | 0.30101 | 34.6164 |  |  |  |  | 0 | 0
1328 | OCOTILLO_1G | 1 | West | YES | 0.13036 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.30107 | 0 | 58 |  |  |  |  | 0.30107 | 17.4623 |  |  |  |  | 0 | 0
1333 | MCDDONAL_8 | 1 | West | YES | 0.13054 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.30126 | 0 | 214.2 |  |  |  |  | 0.30126 | 64.5292 |  |  |  |  | 0 | 0
1327 | WILDHRSE_1G | 1 | West | YES | 0.13076 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.30148 | 0 | 120 |  |  |  |  | 0.30148 | 36.1774 |  |  |  |  | 0 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | 0.1308 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.30152 | 0 | 120 |  |  |  |  | 0.30152 | 36.1819 |  |  |  |  | 0 | 0
11320 | COYOTE_1G | 1 | West | YES | 0.13107 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.30179 | 0 | 225 |  |  |  |  | 0.30179 | 67.9034 |  |  |  |  | 0 | 0
11309 | BULLCREK_2G | 1 | West | YES | 0.13114 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.30186 | 0 | 180 |  |  |  |  | 0.30186 | 54.3348 |  |  |  |  | 0 | 0
11310 | BULLCREK_1G | 1 | West | YES | 0.13114 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.30186 | 0 | 180 |  |  |  |  | 0.30186 | 54.3348 |  |  |  |  | 0 | 0
1045 | CALENG1G_1G | 1 | West | YES | 0.13116 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0 |  |  |  |  | 0 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.13116 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0 |  |  |  |  | 0 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.13116 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.30188 | 0 | 0 |  |  |  |  | 0.30188 | 0 |  |  |  |  | 0 | 0
11065 | ELBOWCK_1G | 1 | West | YES | 0.13136 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.30208 | 0 | 121.9 |  |  |  |  | 0.30208 | 36.8235 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 1 | West | YES | 0.13136 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.30208 | 0 | 150 |  |  |  |  | 0.30208 | 45.312 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 2 | West | YES | 0.13136 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.30208 | 0 | 220 |  |  |  |  | 0.30208 | 66.4575 |  |  |  |  | 0 | 0
60072 | HHOLLOW41A | 1 | West | YES | 0.13142 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 115 |  |  |  |  | 0.30214 | 34.7463 |  |  |  |  | 0 | 0
60058 | BUFF_GAP1A | 1 | West | YES | 0.13142 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30214 | 0 | 120 |  |  |  |  | 0.30214 | 36.257 |  |  |  |  | 0 | 0
60063 | BUFF_GAP1B | 1 | West | YES | 0.13142 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.30214 | 0 | 170.2 |  |  |  |  | 0.30214 | 51.4245 |  |  |  |  | 0 | 0
60068 | HHOLLOW21A | 1 | West | YES | 0.13142 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 184 |  |  |  |  | 0.30214 | 55.5941 |  |  |  |  | 0 | 0
60066 | H_HOLLOW1A | 1 | West | YES | 0.13142 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.30214 | 0 | 222 |  |  |  |  | 0.30214 | 67.0755 |  |  |  |  | 0 | 0
60070 | HHOLLOW31A | 1 | West | YES | 0.13142 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.30214 | 0 | 224 |  |  |  |  | 0.30214 | 67.6798 |  |  |  |  | 0 | 0
60060 | CIRELLO | 1 | West | YES | 0.13142 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.30214 | 0 | 233 |  |  |  |  | 0.30214 | 70.399 |  |  |  |  | 0 | 0
1044 | MRGNFG_6G | F | West | YES | 0.13148 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.3022 | 66 | 66 |  |  |  |  | 0.3022 | 19.9454 |  |  |  |  | 0 | 0
1042 | MRGNDG_4G | D | West | YES | 0.13148 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.3022 | 68 | 68 |  |  |  |  | 0.3022 | 20.5498 |  |  |  |  | 0 | 0
1039 | MRGNAG_1G | A | West | YES | 0.13148 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.3022 | 69 | 69 |  |  |  |  | 0.3022 | 20.852 |  |  |  |  | 0 | 0
1041 | MRGNCG_3G | C | West | YES | 0.13148 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.3022 | 70 | 70 |  |  |  |  | 0.3022 | 21.1542 |  |  |  |  | 0 | 0
1043 | MRGNEG_5G | E | West | YES | 0.13148 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.3022 | 70 | 70 |  |  |  |  | 0.3022 | 21.1542 |  |  |  |  | 0 | 0
1040 | MRGNBG_2G | B | West | YES | 0.13148 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.3022 | 71 | 71 |  |  |  |  | 0.3022 | 21.4564 |  |  |  |  | 0 | 0
1037 | MORGAN5G_5G | 5 | West | YES | 0.13148 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.3022 | 137 | 137 |  |  |  |  | 0.3022 | 41.4018 |  |  |  |  | 0 | 0
6637 | SNYDERW1A | 1 | West | YES | 0.13152 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.30224 | 0 | 63 |  |  |  |  | 0.30224 | 19.0412 |  |  |  |  | 0 | 0
1073 | SCURRYCW_2G | 2 | West | YES | 0.13159 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.30231 | 0 | 120 |  |  |  |  | 0.30231 | 36.2772 |  |  |  |  | 0 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.13159 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.30231 | 0 | 141 |  |  |  |  | 0.30231 | 42.6257 |  |  |  |  | 0 | 0
1069 | KINDERMG_1G | 1 | West | YES | 0.1316 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0 |  |  |  |  | 0 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.1316 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0 |  |  |  |  | 0 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.1316 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30232 | 0 | 0 |  |  |  |  | 0.30232 | 0 |  |  |  |  | 0 | 0
1062 | CIELOGEN_2G | 1 | West | YES | 0.1316 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.30232 | 0 | 61 |  |  |  |  | 0.30232 | 18.4416 |  |  |  |  | 0 | 0
1061 | CIELOGEN_1G | 1 | West | YES | 0.1316 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.30232 | 0 | 99 |  |  |  |  | 0.30232 | 29.9298 |  |  |  |  | 0 | 0
36998 | RDCNYNG1 | 1 | West | YES | 0.13178 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.3025 | 0 | 84 |  |  |  |  | 0.3025 | 25.4101 |  |  |  |  | 0 | 0
1354 | AEPWIND_8 | 1 | West | YES | 0.13189 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.3026 | 0 | 101 |  |  |  |  | 0.3026 | 30.5631 |  |  |  |  | 0 | 0
1343 | TRENTIPP_8 | 1 | West | YES | 0.13189 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.3026 | 0 | 150 |  |  |  |  | 0.3026 | 45.3907 |  |  |  |  | 0 | 0
6407 | TURKTRAK1A | 1 | West | YES | 0.13209 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.3028 | 0 | 169.5 |  |  |  |  | 0.3028 | 51.3254 |  |  |  |  | 0 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | 0.13255 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 37.5 |  |  |  |  | 0.30327 | 11.3725 |  |  |  |  | 0 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | 0.13255 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 80.5 |  |  |  |  | 0.30327 | 24.413 |  |  |  |  | 0 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | 0.13255 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 105 |  |  |  |  | 0.30327 | 31.843 |  |  |  |  | 0 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | 0.13255 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 107.5 |  |  |  |  | 0.30327 | 32.6012 |  |  |  |  | 0 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | 0.13255 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.30327 | 0 | 119 |  |  |  |  | 0.30327 | 36.0887 |  |  |  |  | 0 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | 0.13255 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.30327 | 0 | 135 |  |  |  |  | 0.30327 | 40.941 |  |  |  |  | 0 | 0
6144 | MCADOO1A | 1 | West | YES | 0.13257 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.30329 | 0 | 150 |  |  |  |  | 0.30329 | 45.4936 |  |  |  |  | 0 | 0
11057 | CHAMPION_1G | 1 | West | YES | 0.1326 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.30332 | 0 | 126.5 |  |  |  |  | 0.30332 | 38.3699 |  |  |  |  | 0 | 0
11059 | INADALE_1G | 1 | West | YES | 0.1326 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.30332 | 0 | 197 |  |  |  |  | 0.30332 | 59.754 |  |  |  |  | 0 | 0
11056 | ROSCOE_1G | 1 | West | YES | 0.1326 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.30332 | 0 | 209 |  |  |  |  | 0.30332 | 63.3938 |  |  |  |  | 0 | 0
11058 | PYRON_1G | 1 | West | YES | 0.1326 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.30332 | 0 | 249 |  |  |  |  | 0.30332 | 75.5266 |  |  |  |  | 0 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.13291 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.30363 | 0 | 60 | 7.9747 | 60 |  |  | 0.30363 | 18.2177 |  |  |  |  | 0 | 0
1416 | SWETWATR_1G | 1 | West | YES | 0.13308 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.3038 | 30 | 30 |  |  |  |  | 0.3038 | 9.114 |  |  |  |  | 0 | 0
1419 | SWETWATR_4G | 4 | West | YES | 0.13308 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.3038 | 61 | 61 |  |  |  |  | 0.3038 | 18.5317 |  |  |  |  | 0 | 0
1418 | SWETWATR_3G | 3 | West | YES | 0.13308 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.3038 | 68 | 68 |  |  |  |  | 0.3038 | 20.6583 |  |  |  |  | 0 | 0
1417 | SWETWATR_2G | 2 | West | YES | 0.13308 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.3038 | 72 | 72 |  |  |  |  | 0.3038 | 21.8735 |  |  |  |  | 0 | 0
60081 | WHRLWIND1A | 1 | West | YES | 0.13362 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.30433 | 0 | 60 |  |  |  |  | 0.30433 | 18.2601 |  |  |  |  | 0 | 0
1437 | MESQUITW_1G | 1 | North | YES | 0.13531 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.30602 | 0 | 400 | 54.1224 | 400 |  |  | 0.30602 | 122.4095 |  |  |  |  | 0 | 0
1438 | MESQUITW_2G | 1 | North | YES | 0.13531 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.30603 | 0 | 236 | 31.9334 | 236 |  |  | 0.30603 | 72.2228 |  |  |  |  | 0 | 0
1442 | COKFIELD_5 | 1 | North | YES | 0.13619 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.30691 | 0 | 165 | 22.4714 | 165 |  |  | 0.30691 | 50.6398 |  |  |  |  | 0 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.1554 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 651 |  |  | 0 | 0 | -0.30733 | 0 |  |  |  |  | 0 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.1554 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 564 |  |  | 0 | 0 | -0.30733 | 0 |  |  |  |  | 0 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.1554 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.30733 | 0 | 603 |  |  | 0 | 0 | -0.30733 | 0 |  |  |  |  | 0 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.1555 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.30744 | 252.4 | 252.4 |  |  | -39.2482 | 252.4 | -0.30744 | -77.5971 |  |  |  |  | 0 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.1555 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.30744 | 167.7 | 167.7 |  |  | -26.0773 | 167.7 | -0.30744 | -51.5572 |  |  |  |  | 0 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.1555 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.30744 | 166.4 | 166.4 |  |  | -25.8752 | 166.4 | -0.30744 | -51.1575 |  |  |  |  | 0 | 0
6100 | OKLA7A | EQ | West | YES | 0.13689 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.30761 | 0 | 0 |  |  |  |  | 0.30761 | 0 |  |  |  |  | 0 | 0
6752 | OKLA0A | 1 | West | YES | 0.13689 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.30761 | 0 | 649.7 |  |  |  |  | 0.30761 | 199.8541 |  |  |  |  | 0 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.13817 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.30889 | 242 | 242 | 33.4381 | 242 |  |  | 0.30889 | 74.7518 |  |  |  |  | 0 | 0
332 | RWMILLER01 | 1 | North | YES | 0.13825 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.30897 | 73 | 73 | 10.0923 | 73 |  |  | 0.30897 | 22.5547 |  |  |  |  | 0 | 0
336 | RWMILLER05 | 5 | North | YES | 0.13825 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.30897 | 101 | 101 | 13.9634 | 101 |  |  | 0.30897 | 31.2058 |  |  |  |  | 0 | 0
335 | RWMILLER04 | 4 | North | YES | 0.13825 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.30897 | 102 | 102 | 14.1016 | 102 |  |  | 0.30897 | 31.5148 |  |  |  |  | 0 | 0
333 | RWMILLER02 | 2 | North | YES | 0.13825 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.30897 | 119 | 119 | 16.4519 | 119 |  |  | 0.30897 | 36.7673 |  |  |  |  | 0 | 0
334 | RWMILLER03 | 3 | North | YES | 0.13825 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.30897 | 208 | 208 | 28.7562 | 208 |  |  | 0.30897 | 64.2655 |  |  |  |  | 0 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.13897 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.30969 | 366 | 366 | 50.8648 | 366 |  |  | 0.30969 | 113.3475 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.13909 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.13909 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.30981 | 0 | 0 | 0 | 0 |  |  | 0.30981 | 0 |  |  |  |  | 0 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.13929 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.31 | 0 | 120 | 16.7143 | 120 |  |  | 0.31 | 37.2004 |  |  |  |  | 0 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.15817 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.3101 | 0 | 0 |  |  | 0 | 0 | -0.3101 | 0 |  |  |  |  | 0 | 0
344 | MRSSHPRD | 1 | North | YES | 0.13949 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0 |  |  |  |  | 0 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.13949 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.31021 | 0 | 0 | 0 | 0 |  |  | 0.31021 | 0 |  |  |  |  | 0 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.13991 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.31062 | 0 | 0 | 0 | 0 |  |  | 0.31062 | 0 |  |  |  |  | 0 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.13991 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.31062 | 0 | 0 | 0 | 0 |  |  | 0.31062 | 0 |  |  |  |  | 0 | 0
1895 | DECRDOVA_5G | D | North | YES | 0.14077 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.31149 | 68 | 68 | 9.5726 | 68 |  |  | 0.31149 | 21.1814 |  |  |  |  | 0 | 0
1893 | DECRDOVA_3G | B | North | YES | 0.14077 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.31149 | 69 | 69 | 9.7134 | 69 |  |  | 0.31149 | 21.4929 |  |  |  |  | 0 | 0
1894 | DECRDOVA_4G | C | North | YES | 0.14077 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.31149 | 69 | 69 | 9.7134 | 69 |  |  | 0.31149 | 21.4929 |  |  |  |  | 0 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.14077 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.31149 | 70 | 70 | 9.8542 | 70 |  |  | 0.31149 | 21.8044 |  |  |  |  | 0 | 0
503 | NTHTEXAS01 | 1 | North | YES | 0.14081 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.31153 | 18 | 18 | 2.5346 | 18 |  |  | 0.31153 | 5.6075 |  |  |  |  | 0 | 0
504 | NTHTEXAS02 | 2 | North | YES | 0.14081 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.31153 | 18 | 18 | 2.5346 | 18 |  |  | 0.31153 | 5.6075 |  |  |  |  | 0 | 0
505 | NTHTEXAS03 | 3 | North | YES | 0.14081 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.31153 | 38 | 38 | 5.3508 | 38 |  |  | 0.31153 | 11.8381 |  |  |  |  | 0 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.15966 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.31159 | 0 | 0 |  |  | 0 | 0 | -0.31159 | 0 |  |  |  |  | 0 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.14151 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.31222 | 0 | 0 | 0 | 0 |  |  | 0.31222 | 0 |  |  |  |  | 0 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.14151 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.31222 | 0 | 0 | 0 | 0 |  |  | 0.31222 | 0 |  |  |  |  | 0 | 0
1453 | WCPWRCO_1G | 1 | North | YES | 0.1417 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.31242 | 204 | 204 | 28.9074 | 204 |  |  | 0.31242 | 63.7338 |  |  |  |  | 0 | 0
1454 | WCPWRCO_2G | 2 | North | YES | 0.1417 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.31242 | 204 | 204 | 28.9074 | 204 |  |  | 0.31242 | 63.7338 |  |  |  |  | 0 | 0
1455 | WCPWRCO_3G | 3 | North | YES | 0.1417 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.31242 | 242 | 242 | 34.2921 | 242 |  |  | 0.31242 | 75.6058 |  |  |  |  | 0 | 0
1878 | WLFHOLW_2G | 2 | North | YES | 0.1419 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.31262 | 215.7 | 215.7 | 30.6074 | 215.7 |  |  | 0.31262 | 67.4312 |  |  |  |  | 0 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.1419 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.31262 | 217.3 | 217.3 | 30.8344 | 217.3 |  |  | 0.31262 | 67.9314 |  |  |  |  | 0 | 0
1879 | WLFHOLW_3G | 3 | North | YES | 0.1419 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.31262 | 272.4 | 272.4 | 38.653 | 272.4 |  |  | 0.31262 | 85.1565 |  |  |  |  | 0 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.1608 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.31274 | 546 | 546 |  |  | -87.7984 | 546 | -0.31274 | -170.756 |  |  |  |  | 0 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.1608 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.31274 | 248 | 248 |  |  | -39.8791 | 248 | -0.31274 | -77.5595 |  |  |  |  | 0 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.1608 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.31274 | 166 | 166 |  |  | -26.6933 | 166 | -0.31274 | -51.9148 |  |  |  |  | 0 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.1608 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.31274 | 166 | 166 |  |  | -26.6933 | 166 | -0.31274 | -51.9148 |  |  |  |  | 0 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.1608 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.31274 | 13 | 13 |  |  | -2.0904 | 13 | -0.31274 | -4.0656 |  |  |  |  | 0 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.1608 | 607.1 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.31274 | 0 | 654 |  |  | 0 | 0 | -0.31274 | 0 |  |  |  |  | 0 | 0
1889 | DECRDOVA_1G | 1 | North | YES | 0.14217 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.31289 | 779 | 779 | 110.7543 | 779 |  |  | 0.31289 | 243.7434 |  |  |  |  | 0 | 0
581 | JCKCNTY802 | 2 | North | YES | 0.14264 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.31336 | 147 | 147 | 20.9678 | 147 |  |  | 0.31336 | 46.0633 |  |  |  |  | 0 | 0
582 | JCKCNTY803 | 3 | North | YES | 0.14264 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.31336 | 147 | 147 | 20.9678 | 147 |  |  | 0.31336 | 46.0633 |  |  |  |  | 0 | 0
580 | JCKCNTY801 | 1 | North | YES | 0.14264 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.31336 | 288 | 288 | 41.0797 | 288 |  |  | 0.31336 | 90.2465 |  |  |  |  | 0 | 0
1944 | MDLTHELP_4G | 4 | North | YES | 0.14319 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.31391 | 211 | 211 | 30.2141 | 211 |  |  | 0.31391 | 66.2356 |  |  |  |  | 0 | 0
1943 | MDLTHELP_3G | 3 | North | YES | 0.14319 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.31391 | 212 | 212 | 30.3573 | 212 |  |  | 0.31391 | 66.5495 |  |  |  |  | 0 | 0
1937 | MDLTHELP_5G | 5 | North | YES | 0.14319 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.31391 | 224 | 224 | 32.0757 | 224 |  |  | 0.31391 | 70.3165 |  |  |  |  | 0 | 0
1938 | MDLTHELP_6G | 6 | North | YES | 0.14319 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.31391 | 226 | 226 | 32.3621 | 226 |  |  | 0.31391 | 70.9443 |  |  |  |  | 0 | 0
1861 | EAGLEMNT_1G | MB | North | YES | 0.1441 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0 |  |  |  |  | 0 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.1441 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0 |  |  |  |  | 0 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.1441 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.31482 | 0 | 0 | 0 | 0 |  |  | 0.31482 | 0 |  |  |  |  | 0 | 0
728 | WOLFRIDGE801 | 1 | North | YES | 0.14468 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.3154 | 0 | 112.5 | 16.2764 | 112.5 |  |  | 0.3154 | 35.4821 |  |  |  |  | 0 | 0
1942 | MDLTHELP_2G | 2 | North | YES | 0.14469 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.31541 | 216.1 | 216.1 | 31.2679 | 216.1 |  |  | 0.31541 | 68.16 |  |  |  |  | 0 | 0
1941 | MDLTHELP_1G | 1 | North | YES | 0.14469 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.31541 | 216.4 | 216.4 | 31.3113 | 216.4 |  |  | 0.31541 | 68.2547 |  |  |  |  | 0 | 0
1947 | HANDLEY_3G | 3 | North | YES | 0.14472 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.31543 | 395 | 395 | 57.1624 | 395 |  |  | 0.31543 | 124.5959 |  |  |  |  | 0 | 0
1949 | HANDLEY_5G | 5 | North | YES | 0.14472 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31543 | 435 | 435 | 62.951 | 435 |  |  | 0.31543 | 137.2132 |  |  |  |  | 0 | 0
1948 | HANDLEY_4G | 4 | North | YES | 0.14497 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31568 | 435 | 435 | 63.0606 | 435 |  |  | 0.31568 | 137.3229 |  |  |  |  | 0 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.14605 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.31677 | 61 | 61 | 8.9092 | 61 |  |  | 0.31677 | 19.323 |  |  |  |  | 0 | 0
924 | SPENCER_G5 | 1 | North | YES | 0.14605 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.31677 | 66 | 66 | 9.6395 | 66 |  |  | 0.31677 | 20.9069 |  |  |  |  | 0 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.16573 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.16573 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.16573 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.16573 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.16573 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.16573 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.16573 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.16573 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.16573 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.16573 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.16573 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.16573 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.16573 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.16573 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.16573 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.31766 | 0 | 0 |  |  | 0 | 0 | -0.31766 | 0 |  |  |  |  | 0 | 0
12323 | ENNSTRAC_2G | 2 | North | YES | 0.14859 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.31931 | 116 | 116 | 17.2362 | 116 |  |  | 0.31931 | 37.0395 |  |  |  |  | 0 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | 0.14859 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.31931 | 196 | 196 | 29.1232 | 196 |  |  | 0.31931 | 62.5839 |  |  |  |  | 0 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.14864 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.31936 | 156 | 156 | 23.188 | 156 |  |  | 0.31936 | 49.82 |  |  |  |  | 0 | 0
2382 | NTHLK2_G | 2 | North | YES | 0.14864 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.31936 | 181 | 181 | 26.904 | 181 |  |  | 0.31936 | 57.8039 |  |  |  |  | 0 | 0
2383 | NTHLK3_G | 3 | North | YES | 0.14864 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.31936 | 329 | 329 | 48.9029 | 329 |  |  | 0.31936 | 105.069 |  |  |  |  | 0 | 0
2371 | COLLIN_1G | MB | North | YES | 0.14891 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.31963 | 0 | 0 | 0 | 0 |  |  | 0.31963 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 1 | North | YES | 0.14967 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.32039 | 0 | 0 | 0 | 0 |  |  | 0.32039 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 2 | North | YES | 0.14967 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.32039 | 0 | 0 | 0 | 0 |  |  | 0.32039 | 0 |  |  |  |  | 0 | 0
2414 | MTCK7_G | 7 | North | YES | 0.14991 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.32062 | 115 | 115 | 17.2392 | 115 |  |  | 0.32062 | 36.8717 |  |  |  |  | 0 | 0
2413 | MTCK6_G | 6 | North | YES | 0.14991 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.32062 | 118 | 118 | 17.6889 | 118 |  |  | 0.32062 | 37.8336 |  |  |  |  | 0 | 0
2417 | MTCK8_G | 8 | North | YES | 0.14991 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.32062 | 556 | 556 | 83.3477 | 556 |  |  | 0.32062 | 178.2668 |  |  |  |  | 0 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.14992 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.32064 | 170 | 170 | 25.4866 | 170 |  |  | 0.32064 | 54.5086 |  |  |  |  | 0 | 0
1688 | VALLEY_2G | 2 | North | YES | 0.14992 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.32064 | 527 | 527 | 79.0084 | 527 |  |  | 0.32064 | 168.9766 |  |  |  |  | 0 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.169 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.32093 | 0 | 0 |  |  | 0 | 0 | -0.32093 | 0 |  |  |  |  | 0 | 0
11691 | KMICHICT1_G | 1 | North | YES | 0.15023 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32095 | 144 | 144 | 21.6334 | 144 |  |  | 0.32095 | 46.2168 |  |  |  |  | 0 | 0
11694 | KMICHICT4_G | 4 | North | YES | 0.15023 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32095 | 144 | 144 | 21.6334 | 144 |  |  | 0.32095 | 46.2168 |  |  |  |  | 0 | 0
11692 | KMICHICT2_G | 2 | North | YES | 0.15023 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.32095 | 146 | 146 | 21.9339 | 146 |  |  | 0.32095 | 46.8587 |  |  |  |  | 0 | 0
11695 | KMICHICT5_G | 5 | North | YES | 0.15023 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.32095 | 148 | 148 | 22.2343 | 148 |  |  | 0.32095 | 47.5006 |  |  |  |  | 0 | 0
11696 | KMICHIST6_G | 6 | North | YES | 0.15023 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.32095 | 310 | 310 | 46.5719 | 310 |  |  | 0.32095 | 99.4944 |  |  |  |  | 0 | 0
11693 | KMICHIST3_G | 3 | North | YES | 0.15023 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.32095 | 312 | 312 | 46.8724 | 312 |  |  | 0.32095 | 100.1363 |  |  |  |  | 0 | 0
1689 | VALLEY_3G | 3 | North | YES | 0.15023 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.32095 | 375 | 375 | 56.337 | 375 |  |  | 0.32095 | 120.3562 |  |  |  |  | 0 | 0
1679 | LAMARPWR_2G | 2 | North | YES | 0.15037 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32109 | 156 | 156 | 23.4577 | 156 |  |  | 0.32109 | 50.0897 |  |  |  |  | 0 | 0
1681 | LAMARPWR_4G | 4 | North | YES | 0.15037 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32109 | 156 | 156 | 23.4577 | 156 |  |  | 0.32109 | 50.0897 |  |  |  |  | 0 | 0
1682 | LAMARPWR_5G | 5 | North | YES | 0.15037 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.32109 | 157 | 157 | 23.6081 | 157 |  |  | 0.32109 | 50.4108 |  |  |  |  | 0 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.15037 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.32109 | 160 | 160 | 24.0592 | 160 |  |  | 0.32109 | 51.374 |  |  |  |  | 0 | 0
1680 | LAMARPWR_3G | 3 | North | YES | 0.15037 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.32109 | 196 | 196 | 29.4725 | 196 |  |  | 0.32109 | 62.9332 |  |  |  |  | 0 | 0
1683 | LAMARPWR_6G | 6 | North | YES | 0.15037 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.32109 | 198 | 198 | 29.7733 | 198 |  |  | 0.32109 | 63.5754 |  |  |  |  | 0 | 0
1675 | PEC_1G | 1 | North | YES | 0.15046 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0 |  |  |  |  | 0 | 0
1676 | PEC_2G | 2 | North | YES | 0.15046 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0 |  |  |  |  | 0 | 0
1677 | PEC_3G | 3 | North | YES | 0.15046 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.32118 | 0 | 0 | 0 | 0 |  |  | 0.32118 | 0 |  |  |  |  | 0 | 0
5925 | DCEAST | EQ | North | YES | 0.15062 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.32133 | 0 | 0 | 0 | 0 |  |  | 0.32133 | 0 |  |  |  |  | 0 | 0
1701 | MOSES_1G | 1 | North | YES | 0.15062 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 558 | 84.0437 | 558 |  |  | 0.32133 | 179.3042 |  |  |  |  | 0 | 0
1702 | MOSES_2G | 2 | North | YES | 0.15062 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 579 | 87.2067 | 579 |  |  | 0.32133 | 186.0522 |  |  |  |  | 0 | 0
1703 | MOSES_3G | 3 | North | YES | 0.15062 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.32133 | 0 | 808 | 121.6977 | 808 |  |  | 0.32133 | 259.6377 |  |  |  |  | 0 | 0
845 | OLINGER_G4 | 1 | North | YES | 0.15091 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.32162 | 76 | 76 | 11.4689 | 76 |  |  | 0.32162 | 24.4434 |  |  |  |  | 0 | 0
842 | OLINGER_G1 | 1 | North | YES | 0.15091 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.32162 | 79 | 79 | 11.9216 | 79 |  |  | 0.32162 | 25.4083 |  |  |  |  | 0 | 0
843 | OLINGER_G2 | 1 | North | YES | 0.15091 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.32162 | 110 | 110 | 16.5997 | 110 |  |  | 0.32162 | 35.3786 |  |  |  |  | 0 | 0
844 | OLINGER_G3 | 1 | North | YES | 0.15091 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.32162 | 150 | 150 | 22.6359 | 150 |  |  | 0.32162 | 48.2436 |  |  |  |  | 0 | 0
837 | NEWMAN_G5 | 1 | North | YES | 0.15093 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.32165 | 40 | 40 | 6.0372 | 40 |  |  | 0.32165 | 12.8659 |  |  |  |  | 0 | 0
949 | STEAM2 | 1 | North | YES | 0.15111 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.32182 | 26 | 26 | 3.9288 | 26 |  |  | 0.32182 | 8.3674 |  |  |  |  | 0 | 0
950 | STEAM3 | 1 | North | YES | 0.15111 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.32182 | 42 | 42 | 6.3465 | 42 |  |  | 0.32182 | 13.5166 |  |  |  |  | 0 | 0
948 | STEAM1 | 1 | North | YES | 0.15111 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.32183 | 20 | 20 | 3.0222 | 20 |  |  | 0.32183 | 6.4365 |  |  |  |  | 0 | 0
12440 | PARKD_1SVC8 | 1 | North | YES | 0.15148 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.3222 | 0 | 0 | 0 | 0 |  |  | 0.3222 | 0 |  |  |  |  | 0 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.15148 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.3222 | 0 | 0 | 0 | 0 |  |  | 0.3222 | 0 |  |  |  |  | 0 | 0
2451 | LKHB1_G | 1 | North | YES | 0.15155 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.32227 | 391 | 391 | 59.2564 | 391 |  |  | 0.32227 | 126.0071 |  |  |  |  | 0 | 0
2452 | LKHB2_G | 2 | North | YES | 0.15155 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.32227 | 516 | 516 | 78.2003 | 516 |  |  | 0.32227 | 166.2907 |  |  |  |  | 0 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.15233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32305 | 161 | 161 | 24.5248 | 161 |  |  | 0.32305 | 52.0104 |  |  |  |  | 0 | 0
12422 | FPLEFR2B_G | 2 | North | YES | 0.15233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32305 | 161 | 161 | 24.5248 | 161 |  |  | 0.32305 | 52.0104 |  |  |  |  | 0 | 0
12421 | FPLEFR2A_G | 1 | North | YES | 0.15233 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.32305 | 162 | 162 | 24.6771 | 162 |  |  | 0.32305 | 52.3334 |  |  |  |  | 0 | 0
12423 | FPLEFR2C_G | 3 | North | YES | 0.15233 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.32305 | 163 | 163 | 24.8295 | 163 |  |  | 0.32305 | 52.6565 |  |  |  |  | 0 | 0
12412 | FPLEFR1B_G | 2 | North | YES | 0.15233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32305 | 164 | 164 | 24.9818 | 164 |  |  | 0.32305 | 52.9795 |  |  |  |  | 0 | 0
12413 | FPLEFR1C_G | 3 | North | YES | 0.15233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32305 | 164 | 164 | 24.9818 | 164 |  |  | 0.32305 | 52.9795 |  |  |  |  | 0 | 0
12414 | FPLEFR1S_G | 4 | North | YES | 0.15233 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.32305 | 414 | 414 | 63.0638 | 414 |  |  | 0.32305 | 133.7409 |  |  |  |  | 0 | 0
12424 | FPLEFR2S_G | 4 | North | YES | 0.15233 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.32305 | 415 | 415 | 63.2161 | 415 |  |  | 0.32305 | 134.064 |  |  |  |  | 0 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.17133 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 |  |  |  |  | 0 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.17133 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 |  |  |  |  | 0 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.17133 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 |  |  |  |  | 0 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.17133 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 |  |  |  |  | 0 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.17133 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.32326 | 0 | 0 |  |  | 0 | 0 | -0.32326 | 0 |  |  |  |  | 0 | 0
3126 | TRINIDAD_6G | 1 | North | YES | 0.15258 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.3233 | 224 | 224 | 34.1784 | 224 |  |  | 0.3233 | 72.4191 |  |  |  |  | 0 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.17223 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0 |  |  |  |  | 0 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.17223 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0 |  |  |  |  | 0 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.17223 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0 |  |  |  |  | 0 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.17223 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.32417 | 0 | 0 |  |  | 0 | 0 | -0.32417 | 0 |  |  |  |  | 0 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.1726 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.32454 | 282 | 282 |  |  | -48.6735 | 282 | -0.32454 | -91.5197 |  |  |  |  | 0 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.1726 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.32454 | 163.2 | 163.2 |  |  | -28.1685 | 163.2 | -0.32454 | -52.9646 |  |  |  |  | 0 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.1726 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.32454 | 157.5 | 157.5 |  |  | -27.1847 | 157.5 | -0.32454 | -51.1147 |  |  |  |  | 0 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.1726 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.32454 | 157.1 | 157.1 |  |  | -27.1156 | 157.1 | -0.32454 | -50.9849 |  |  |  |  | 0 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.1726 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.32454 | 157 | 157 |  |  | -27.0984 | 157 | -0.32454 | -50.9525 |  |  |  |  | 0 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.17391 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.32585 | 0 | 0 |  |  | 0 | 0 | -0.32585 | 0 |  |  |  |  | 0 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.17391 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.32585 | 0 | 0 |  |  | 0 | 0 | -0.32585 | 0 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | E | Houston | YES | -0.17398 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.32591 | 57 | 57 |  |  | -9.9166 | 57 | -0.32591 | -18.577 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | D | Houston | YES | -0.17398 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.32591 | 55 | 55 |  |  | -9.5687 | 55 | -0.32591 | -17.9252 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | F | Houston | YES | -0.17398 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.32591 | 54 | 54 |  |  | -9.3947 | 54 | -0.32591 | -17.5993 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | C | Houston | YES | -0.17398 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.32591 | 47 | 47 |  |  | -8.1769 | 47 | -0.32591 | -15.3179 |  |  |  |  | 0 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.17439 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.32633 | 0 | 0 |  |  | 0 | 0 | -0.32633 | 0 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.17481 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.32675 | 18 | 18 |  |  | -3.1466 | 18 | -0.32675 | -5.8814 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | -0.17481 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.32675 | 12 | 12 |  |  | -2.0977 | 12 | -0.32675 | -3.921 |  |  |  |  | 0 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.17481 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.32675 | 0 | 0 |  |  | 0 | 0 | -0.32675 | 0 |  |  |  |  | 0 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.17481 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.32675 | 0 | 0 |  |  | 0 | 0 | -0.32675 | 0 |  |  |  |  | 0 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.17483 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.32677 | 176 | 176 |  |  | -30.7706 | 176 | -0.32677 | -57.5115 |  |  |  |  | 0 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.17486 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.3268 | 165 | 165 |  |  | -28.8517 | 165 | -0.3268 | -53.9213 |  |  |  |  | 0 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.17488 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0 |  |  |  |  | 0 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.17488 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0 |  |  |  |  | 0 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.17488 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.32681 | 0 | 0 |  |  | 0 | 0 | -0.32681 | 0 |  |  |  |  | 0 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.17495 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.32688 | 228 | 228 |  |  | -39.8877 | 228 | -0.32688 | -74.5293 |  |  |  |  | 0 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.17496 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0 |  |  |  |  | 0 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.17496 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0 |  |  |  |  | 0 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.17496 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0 |  |  |  |  | 0 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.17496 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.3269 | 0 | 0 |  |  | 0 | 0 | -0.3269 | 0 |  |  |  |  | 0 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.17497 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.3269 | 16.2 | 16.2 |  |  | -2.8345 | 16.2 | -0.3269 | -5.2958 |  |  |  |  | 0 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.17498 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.32691 | 213 | 213 |  |  | -37.2701 | 213 | -0.32691 | -69.6327 |  |  |  |  | 0 | 0
3097 | MARTLAKE_1G | 1 | North | YES | 0.15654 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 790 | 123.6634 | 790 |  |  | 0.32725 | 258.5305 |  |  |  |  | 0 | 0
3098 | MARTLAKE_2G | 2 | North | YES | 0.15654 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 795 | 124.4461 | 795 |  |  | 0.32725 | 260.1667 |  |  |  |  | 0 | 0
3099 | MARTLAKE_3G | 3 | North | YES | 0.15654 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.32725 | 0 | 804 | 125.8549 | 804 |  |  | 0.32725 | 263.112 |  |  |  |  | 0 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.17533 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0 |  |  |  |  | 0 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.17533 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.17533 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.17533 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.32726 | 0 | 0 |  |  | 0 | 0 | -0.32726 | 0 |  |  |  |  | 0 | 0
13117 | TGATEWAY_2G | 2 | North | YES | 0.15714 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.32786 | 130 | 130 | 20.4279 | 130 |  |  | 0.32786 | 42.6212 |  |  |  |  | 0 | 0
13118 | TGATEWAY_3G | 3 | North | YES | 0.15714 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.32786 | 148 | 148 | 23.2564 | 148 |  |  | 0.32786 | 48.5227 |  |  |  |  | 0 | 0
13116 | TGATEWAY_1G | 1 | North | YES | 0.15714 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.32786 | 151 | 151 | 23.7278 | 151 |  |  | 0.32786 | 49.5062 |  |  |  |  | 0 | 0
13119 | TGATEWAY_4G | 4 | North | YES | 0.15714 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.32786 | 399 | 399 | 62.6981 | 399 |  |  | 0.32786 | 130.8144 |  |  |  |  | 0 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.17606 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.328 | 42 | 42 |  |  | -7.3946 | 42 | -0.328 | -13.776 |  |  |  |  | 0 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.17606 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.328 | 42 | 42 |  |  | -7.3946 | 42 | -0.328 | -13.776 |  |  |  |  | 0 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.17606 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.328 | 39 | 39 |  |  | -6.8665 | 39 | -0.328 | -12.792 |  |  |  |  | 0 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.17606 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.328 | 39 | 39 |  |  | -6.8665 | 39 | -0.328 | -12.792 |  |  |  |  | 0 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.1763 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.32823 | 0 | 0 |  |  | 0 | 0 | -0.32823 | 0 |  |  |  |  | 0 | 0
3348 | CHAMPION_1G | MB | North | YES | 0.15768 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.3284 | 0 | 0 | 0 | 0 |  |  | 0.3284 | 0 |  |  |  |  | 0 | 0
3309 | ASPN_G | 1 | North | YES | 0.15775 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.32847 | 50 | 50 | 7.8874 | 50 |  |  | 0.32847 | 16.4233 |  |  |  |  | 0 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.17653 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.32847 | 0 | 0 |  |  | 0 | 0 | -0.32847 | 0 |  |  |  |  | 0 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.17653 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.32847 | 0 | 0 |  |  | 0 | 0 | -0.32847 | 0 |  |  |  |  | 0 | 0
3107 | STRYKER_1G | 1 | North | YES | 0.15784 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.32856 | 182 | 182 | 28.7272 | 182 |  |  | 0.32856 | 59.7979 |  |  |  |  | 0 | 0
3108 | STRYKER_2G | 2 | North | YES | 0.15784 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.32856 | 484 | 484 | 76.3955 | 484 |  |  | 0.32856 | 159.0229 |  |  |  |  | 0 | 0
48885 | THW_5152 | B | Houston | YES | -0.17751 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.32945 | 59 | 59 |  |  | -10.4733 | 59 | -0.32945 | -19.4375 |  |  |  |  | 0 | 0
48887 | THW_5556 | E | Houston | YES | -0.17751 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.32945 | 59 | 59 |  |  | -10.4733 | 59 | -0.32945 | -19.4375 |  |  |  |  | 0 | 0
48885 | THW_5152 | A | Houston | YES | -0.17751 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.32945 | 58 | 58 |  |  | -10.2958 | 58 | -0.32945 | -19.1081 |  |  |  |  | 0 | 0
48886 | THW_5354 | D | Houston | YES | -0.17751 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.32945 | 58 | 58 |  |  | -10.2958 | 58 | -0.32945 | -19.1081 |  |  |  |  | 0 | 0
48886 | THW_5354 | C | Houston | YES | -0.17751 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.32945 | 57 | 57 |  |  | -10.1182 | 57 | -0.32945 | -18.7786 |  |  |  |  | 0 | 0
48887 | THW_5556 | F | Houston | YES | -0.17751 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.32945 | 57 | 57 |  |  | -10.1182 | 57 | -0.32945 | -18.7786 |  |  |  |  | 0 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.17776 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.32969 | 746 | 746 |  |  | -132.6067 | 746 | -0.32969 | -245.9517 |  |  |  |  | 0 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782 |  |  |  |  | 0 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782 |  |  |  |  | 0 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.17819 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.33013 | 172 | 172 |  |  | -30.6489 | 172 | -0.33013 | -56.782 |  |  |  |  | 0 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.1787 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.33064 | 269.2 | 269.2 |  |  | -48.1058 | 269.2 | -0.33064 | -89.0072 |  |  |  |  | 0 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.1787 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.33064 | 162.8 | 162.8 |  |  | -29.0922 | 162.8 | -0.33064 | -53.8275 |  |  |  |  | 0 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.1787 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.33064 | 161.4 | 161.4 |  |  | -28.842 | 161.4 | -0.33064 | -53.3646 |  |  |  |  | 0 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.1787 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.33064 | 158.9 | 158.9 |  |  | -28.3953 | 158.9 | -0.33064 | -52.538 |  |  |  |  | 0 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.17885 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.33079 | 744 | 744 |  |  | -133.0644 | 744 | -0.33079 | -246.1055 |  |  |  |  | 0 | 0
49803 | EXN_15GT | 1 | Houston | YES | -0.17913 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.17913 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.17913 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.17913 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.17913 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.17913 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.17913 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.17913 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.17913 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.17913 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.17913 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.33107 | 0 | 0 |  |  | 0 | 0 | -0.33107 | 0 |  |  |  |  | 0 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.17979 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.33173 | 0 | 0 |  |  | 0 | 0 | -0.33173 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.18065 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.33259 | 0 | 0 |  |  | 0 | 0 | -0.33259 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.18065 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.33259 | 0 | 0 |  |  | 0 | 0 | -0.33259 | 0 |  |  |  |  | 0 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.18088 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.33282 | 108 | 108 |  |  | -19.5349 | 108 | -0.33282 | -35.9441 |  |  |  |  | 0 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.18088 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.33282 | 107 | 107 |  |  | -19.3541 | 107 | -0.33282 | -35.6113 |  |  |  |  | 0 | 0
48881 | THW_4344 | G | Houston | YES | -0.18088 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.33282 | 58 | 58 |  |  | -10.491 | 58 | -0.33282 | -19.3033 |  |  |  |  | 0 | 0
48881 | THW_4344 | H | Houston | YES | -0.18088 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.33282 | 58 | 58 |  |  | -10.491 | 58 | -0.33282 | -19.3033 |  |  |  |  | 0 | 0
48877 | THW_3334 | D | Houston | YES | -0.18088 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.33282 | 57 | 57 |  |  | -10.3101 | 57 | -0.33282 | -18.9705 |  |  |  |  | 0 | 0
48879 | THW_4142 | E | Houston | YES | -0.18088 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.33282 | 56 | 56 |  |  | -10.1292 | 56 | -0.33282 | -18.6377 |  |  |  |  | 0 | 0
48875 | THW_3132 | A | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049 |  |  |  |  | 0 | 0
48877 | THW_3334 | C | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049 |  |  |  |  | 0 | 0
48879 | THW_4142 | F | Houston | YES | -0.18088 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.33282 | 55 | 55 |  |  | -9.9483 | 55 | -0.33282 | -18.3049 |  |  |  |  | 0 | 0
48875 | THW_3132 | B | Houston | YES | -0.18088 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.33282 | 53 | 53 |  |  | -9.5866 | 53 | -0.33282 | -17.6392 |  |  |  |  | 0 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.18206 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 |  |  |  |  | 0 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.18206 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 |  |  |  |  | 0 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.18206 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 |  |  |  |  | 0 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.18206 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 |  |  |  |  | 0 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.18206 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 |  |  |  |  | 0 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.18206 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 |  |  |  |  | 0 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.18206 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.33399 | 0 | 0 |  |  | 0 | 0 | -0.33399 | 0 |  |  |  |  | 0 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.18229 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.33422 | 0 | 0 |  |  | 0 | 0 | -0.33422 | 0 |  |  |  |  | 0 | 0
13134 | CALFREST_4G | 4 | North | YES | 0.1638 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.33452 | 151.5 | 151.5 | 24.8163 | 151.5 |  |  | 0.33452 | 50.68 |  |  |  |  | 0 | 0
13135 | CALFREST_5G | 5 | North | YES | 0.1638 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.33452 | 152.3 | 152.3 | 24.9473 | 152.3 |  |  | 0.33452 | 50.9477 |  |  |  |  | 0 | 0
13136 | CALFREST_6G | 6 | North | YES | 0.1638 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.33452 | 177.5 | 177.5 | 29.0752 | 177.5 |  |  | 0.33452 | 59.3776 |  |  |  |  | 0 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.18272 | 173 | 50 | 173 |  | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 |  |  |  |  | 0 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.18272 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 |  |  |  |  | 0 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.18272 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 |  |  |  |  | 0 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.18272 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 |  |  |  |  | 0 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.18272 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.33466 | 0 | 0 |  |  | 0 | 0 | -0.33466 | 0 |  |  |  |  | 0 | 0
13131 | CALFREST_1G | 1 | North | YES | 0.16409 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.33481 | 150.7 | 150.7 | 24.7288 | 150.7 |  |  | 0.33481 | 50.456 |  |  |  |  | 0 | 0
13132 | CALFREST_2G | 2 | North | YES | 0.16409 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.33481 | 151 | 151 | 24.778 | 151 |  |  | 0.33481 | 50.5564 |  |  |  |  | 0 | 0
13133 | CALFREST_3G | 3 | North | YES | 0.16409 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.33481 | 177.4 | 177.4 | 29.1101 | 177.4 |  |  | 0.33481 | 59.3954 |  |  |  |  | 0 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.18335 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.33529 | 398 | 398 |  |  | -72.9749 | 398 | -0.33529 | -133.4458 |  |  |  |  | 0 | 0
3382 | BBRN_2G | 2 | North | YES | 0.16547 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.33618 | 0 | 589 | 97.4595 | 589 |  |  | 0.33618 | 198.0122 |  |  |  |  | 0 | 0
3381 | BBRN_1G | 1 | North | YES | 0.16547 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.33618 | 0 | 618 | 102.258 | 618 |  |  | 0.33618 | 207.7616 |  |  |  |  | 0 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.1846 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.33654 | 12 | 12 |  |  | -2.2152 | 12 | -0.33654 | -4.0385 |  |  |  |  | 0 | 0
48722 | LEG_2___2 | 2 | North | YES | 0.18228 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.353 | 0 | 819 | 149.2873 | 819 |  |  | 0.353 | 289.1052 |  |  |  |  | 0 | 0
48721 | LEG_1___1 | 1 | North | YES | 0.18228 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.353 | 0 | 827 | 150.7456 | 827 |  |  | 0.353 | 291.9291 |  |  |  |  | 0 | 0
39960 | TNTNPONE_18 | 1 | North | YES | 0.19301 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.36372 | 0 | 152.3 | 29.3947 | 152.3 |  |  | 0.36372 | 55.395 |  |  |  |  | 0 | 0
39970 | TNTNPONE_28 | 1 | North | YES | 0.19301 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.36372 | 0 | 153 | 29.5298 | 153 |  |  | 0.36372 | 55.6496 |  |  |  |  | 0 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.19668 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.3674 | 154.2 | 154.2 | 30.3288 | 154.2 |  |  | 0.3674 | 56.6535 |  |  |  |  | 0 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | 0.19668 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.3674 | 158 | 158 | 31.0762 | 158 |  |  | 0.3674 | 58.0496 |  |  |  |  | 0 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | 0.19668 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.3674 | 159 | 159 | 31.2729 | 159 |  |  | 0.3674 | 58.417 |  |  |  |  | 0 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | 0.19668 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.3674 | 380 | 380 | 74.7403 | 380 |  |  | 0.3674 | 139.613 |  |  |  |  | 0 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.19756 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.36828 | 46 | 46 | 9.088 | 46 |  |  | 0.36828 | 16.941 |  |  |  |  | 0 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.19756 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.36828 | 48 | 48 | 9.4831 | 48 |  |  | 0.36828 | 17.6776 |  |  |  |  | 0 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.19756 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.36828 | 105 | 105 | 20.7443 | 105 |  |  | 0.36828 | 38.6697 |  |  |  |  | 0 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | 0.20233 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0 |  |  |  |  | 0 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.20233 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0 |  |  |  |  | 0 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | 0.20233 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0 |  |  |  |  | 0 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.20233 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.37305 | 0 | 0 | 0 | 0 |  |  | 0.37305 | 0 |  |  |  |  | 0 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.20233 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.37305 | 17 | 17 | 3.4397 | 17 |  |  | 0.37305 | 6.3419 |  |  |  |  | 0 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.20478 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.3755 | 32 | 32 | 6.5531 | 32 |  |  | 0.3755 | 12.0161 |  |  |  |  | 0 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | 0.2205 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.39121 | 0 | 463 | 102.0896 | 463 |  |  | 0.39121 | 181.132 |  |  |  |  | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0

## Zones
Houston | -1
North | 1
South | -1
West | 1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | Houston | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1073 | SCURRYCW_2G | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3126 | TRINIDAD_6G | GST
3309 | ASPN_G | Bio
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5920 | WELSHDC1 | DCTie
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6096 | NORTHDC7 | DCTie
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NBEC7 | GST
8442 | NBEC7 | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11056 | ROSCOE_1G | Wind
11057 | CHAMPION_1G | Wind
11058 | PYRON_1G | Wind
11059 | INADALE_1G | Wind
11065 | ELBOWCK_1G | Wind
11147 | NOTREES_1G | Wind
11309 | BULLCREK_2G | Wind
11310 | BULLCREK_1G | Wind
11320 | COYOTE_1G | Wind
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
48940 | WARVUE_GT1 | Cogen
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
71061 | L_SWEETW1_5N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
76095 | L_CAPRSI1_1N | Wind
76096 | L_CAPRSI1_2N | Wind
76097 | L_CAPRGE1_1N | Wind
80003 | MILHWYS | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80263 | B_DAVIS31A | CC
80264 | B_DAVIS41A | CC
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
86104 | CID-138 | DCTie
86105 | CID-230 | DCTie
86106 | CUF-230 | DCTie
86107 | CUF-138 | DCTie
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR