## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  | Summary of Key Data points | Value
File Description: Cont_ Tradinghouse to TemplePEC OL_ TempleSS to LakeCreek
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K27 |  | Number of units | 645
|  |  | Dec PTDF cutoff point | 258
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  | Dec PTDF cutoff unit | BRYN_DNSBY14
|  |  | Dec 10% unit | HANDLEY_5G
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  | Dec max cumltv zone impact - cumltv zone share | 0.027191
|  |  | Dec max cumltv zone impact - cumltv zone share pt | 126
Step 5 | Enter Dennis' file name into cell K27 |  | Dec max cumltv zone impact - cumltv zone share unit | STRYKER_2G
|  |  | North Zonal weighted AWGSF | 0.13903
Step 6 | click the step one button |  | South Zonal weighted AWGSF | -0.17994
|  |  | Inc PTDF cutoff point | 387
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  | Inc PTDF cutoff unit | TNSLCGN1__8
| X6:X30, or to the end of the selected list. |  | Inc 10% unit | SANDH_G4
|  |  | Inc max cumltv zone impact - cumltv zone share | 0.13728
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  | Inc max cumltv zone impact - cumltv zone share pt | 182
| of the formulas in columns L:V (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  | Inc max cumltv zone impact - cumltv zone share unit | RAYBURNGEN2
| If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct leng |  | North Zonal weighted AWGSF | 0.13903
| It is only necessary to match the Distributed Slack - Dec worksheet. |  | South Zonal weighted AWGSF | -0.17994
|  |  | Min of zone correlation | 0.13903
Step 9 | Click the step 2 button |  | Bounary gen in South Zone | 0
| The last file saved will still be open, yopu will need to close this file. |  | Bounary gen in soucre zone as % of line | 0%
| This sheet willno longer be open. |  | Bounary gen in North Zone | 0
|  |  | Bounary gen in soucre zone as % of line | 0
|  |  | OL element line rating | 1072
|  |  | North Zonal weighted AWGSF | 0.13903
|  | NS_043009automation.xls | South Zonal weighted AWGSF | -0.17994
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ Tradinghouse to TemplePEC OL_ TempleSS to LakeCreek |  | i_PTDF_DEC_pt | 258 |  | STRYKER_2G | Unit at max
3403 | THOUSE_1G | 1 | North | YES | 0.23807 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.41801 | 563 | 563 | 134.0345 | 563 |  |  | 0.41801 | 235.3389 | 0.013399 | 0.017835 |  |  | i_10pctunit | 15 |  | 126 | # units @ max
3404 | THOUSE_2G | 2 | North | YES | 0.23807 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.41801 | 807 | 807 | 192.1241 | 807 |  |  | 0.41801 | 337.333 | 0.032606 | 0.0434 |  |  | # units | 645 |  | 0.027191 | delta max
238 | BOSQUESW505 | 1 | North | YES | 0.197 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.37693 | 255 | 255 | 50.2342 | 255 |  |  | 0.37693 | 96.1181 | 0.038675 | 0.050685 | [5 empty] | Delta
239 | BOSQUESW502 | 1 | North | YES | 0.197 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.37693 | 149 | 149 | 29.3526 | 149 |  |  | 0.37693 | 56.1631 | 0.042221 | 0.054941 | Weighted Shift Factors |  |  |  | 1 | 0.0044359
247 | BOSQUESW501 | 2 | North | YES | 0.197 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.37693 | 156 | 156 | 30.7315 | 156 |  |  | 0.37693 | 58.8016 | 0.045934 | 0.059397 | North | 0.13903 |  |  | 2 | 0.010794
3416 | LAKE_CRK1_G | 1 | North | YES | 0.16701 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.34695 | 75 | 75 | 12.5258 | 75 |  |  | 0.34695 | 26.0211 | 0.047719 | 0.061369 | South | -0.17994 |  |  | 3 | 0.01201
3417 | LAKE_CRK2_G | 2 | North | YES | 0.16701 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.34695 | 222 | 222 | 37.0764 | 222 |  |  | 0.34695 | 77.0224 | 0.053002 | 0.067206 |  |  |  |  | 4 | 0.01272
1941 | MDLTHELP_1G | 1 | North | YES | 0.15582 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.33575 | 216.4 | 216.4 | 33.7186 | 216.4 |  |  | 0.33575 | 72.6569 | 0.058153 | 0.072713 |  |  |  |  | 5 | 0.013463
1942 | MDLTHELP_2G | 2 | North | YES | 0.15582 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.33575 | 216.1 | 216.1 | 33.6718 | 216.1 |  |  | 0.33575 | 72.5561 | 0.063296 | 0.078211 |  |  |  |  | 6 | 0.013651
1937 | MDLTHELP_5G | 5 | North | YES | 0.15515 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.33509 | 224 | 224 | 34.754 | 224 |  |  | 0.33509 | 75.0599 | 0.068627 | 0.0839 |  |  |  |  | 7 | 0.014204
1938 | MDLTHELP_6G | 6 | North | YES | 0.15515 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.33509 | 226 | 226 | 35.0644 | 226 |  |  | 0.33509 | 75.73 | 0.074006 | 0.089639 |  |  |  |  | 8 | 0.01456
1943 | MDLTHELP_3G | 3 | North | YES | 0.15515 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.33509 | 212 | 212 | 32.8922 | 212 |  |  | 0.33509 | 71.0388 | 0.079051 | 0.095023 |  |  |  |  | 9 | 0.014916
1944 | MDLTHELP_4G | 4 | North | YES | 0.15515 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.33509 | 211 | 211 | 32.7371 | 211 |  |  | 0.33509 | 70.7037 | 0.084073 | 0.10038 |  |  |  |  | 10 | 0.015273
1947 | HANDLEY_3G | 3 | North | YES | 0.14804 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.32798 | 395 | 395 | 58.4766 | 395 |  |  | 0.32798 | 129.5516 | 0.093474 | 0.1102 |  |  |  |  | 11 | 0.015633
1949 | HANDLEY_5G | 5 | North | YES | 0.14804 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.32798 | 435 | 435 | 64.3983 | 435 |  |  | 0.32798 | 142.6707 | 0.10383 | 0.12101 |  |  |  |  | 12 | 0.015972
1948 | HANDLEY_4G | 4 | North | YES | 0.14783 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.32777 | 435 | 435 | 64.3069 | 435 |  |  | 0.32777 | 142.5794 | 0.11418 | 0.13182 |  |  |  |  | 13 | 0.016308
366 | JNSNCNTY802 | 1 | North | YES | 0.14753 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.32747 | 0 | 0 | 0 | 0 |  |  | 0.32747 | 0 | 0.11418 | 0.13182 |  |  |  |  | 14 | 0.016725
367 | JNSNCNTY802 | 2 | North | YES | 0.14753 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.32747 | 0 | 0 | 0 | 0 |  |  | 0.32747 | 0 | 0.11418 | 0.13182 |  |  |  |  | 15 | 0.017185
251 | BOSQUESW803 | 2 | North | YES | 0.14734 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.32728 | 150 | 150 | 22.1012 | 150 |  |  | 0.32728 | 49.0916 | 0.11775 | 0.13554 |  |  |  |  | 16 | 0.017637
253 | BOSQUESW804 | 2 | North | YES | 0.14734 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.32728 | 80 | 80 | 11.7873 | 80 |  |  | 0.32728 | 26.1822 | 0.11965 | 0.13752 |  |  |  |  | 17 | 0.017637
244 | WHITNYDM01 | 1 | North | YES | 0.14569 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32562 | 0 | 0 | 0 | 0 |  |  | 0.32562 | 0 | 0.11965 | 0.13752 |  |  |  |  | 18 | 0.017637
245 | WHITNYDM02 | 2 | North | YES | 0.14569 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32562 | 0 | 0 | 0 | 0 |  |  | 0.32562 | 0 | 0.11965 | 0.13752 |  |  |  |  | 19 | 0.017788
1889 | DECRDOVA_1G | 1 | North | YES | 0.14553 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.32546 | 779 | 779 | 113.3648 | 779 |  |  | 0.32546 | 253.5354 | 0.13819 | 0.15674 |  |  |  |  | 20 | 0.017868
1877 | WLFHOLW_1G | 1 | North | YES | 0.14509 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.32503 | 217.3 | 217.3 | 31.5281 | 217.3 |  |  | 0.32503 | 70.6283 | 0.14337 | 0.16209 |  |  |  |  | 21 | 0.017868
1878 | WLFHOLW_2G | 2 | North | YES | 0.14509 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.32503 | 215.7 | 215.7 | 31.2959 | 215.7 |  |  | 0.32503 | 70.1082 | 0.1485 | 0.1674 |  |  |  |  | 22 | 0.017868
1879 | WLFHOLW_3G | 3 | North | YES | 0.14509 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.32503 | 272.4 | 272.4 | 39.5225 | 272.4 |  |  | 0.32503 | 88.5373 | 0.15498 | 0.17411 |  |  |  |  | 23 | 0.018542
1861 | EAGLEMNT_1G | MB | North | YES | 0.1447 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0 | 0.15498 | 0.17411 |  |  |  |  | 24 | 0.018723
1862 | EAGLEMNT_2G | MB | North | YES | 0.1447 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0 | 0.15498 | 0.17411 |  |  |  |  | 25 | 0.018903
1863 | EAGLEMNT_3G | MB | North | YES | 0.1447 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0 | 0.15498 | 0.17411 |  |  |  |  | 26 | 0.019129
1892 | DECRDOVA_2G | A | North | YES | 0.14465 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.32458 | 70 | 70 | 10.1254 | 70 |  |  | 0.32458 | 22.7209 | 0.15665 | 0.17583 |  |  |  |  | 27 | 0.019129
1893 | DECRDOVA_3G | B | North | YES | 0.14465 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.32458 | 69 | 69 | 9.9807 | 69 |  |  | 0.32458 | 22.3963 | 0.15829 | 0.17753 |  |  |  |  | 28 | 0.019129
1894 | DECRDOVA_4G | C | North | YES | 0.14465 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.32458 | 69 | 69 | 9.9807 | 69 |  |  | 0.32458 | 22.3963 | 0.15993 | 0.17923 |  |  |  |  | 29 | 0.019129
1895 | DECRDOVA_5G | D | North | YES | 0.14465 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.32458 | 68 | 68 | 9.8361 | 68 |  |  | 0.32458 | 22.0718 | 0.16155 | 0.1809 |  |  |  |  | 30 | 0.019185
1898 | COMCHEPK_1G | 1 | North | YES | 0.14433 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.32427 | 0 | 0 | 0 | 0 |  |  | 0.32427 | 0 | 0.16155 | 0.1809 |  |  |  |  | 31 | 0.01924
1899 | COMCHEPK_2G | 2 | North | YES | 0.14433 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.32427 | 0 | 0 | 0 | 0 |  |  | 0.32427 | 0 | 0.16155 | 0.1809 |  |  |  |  | 32 | 0.019296
2381 | NTHLK1_G | 1 | North | YES | 0.14425 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.32419 | 156 | 156 | 22.5032 | 156 |  |  | 0.32419 | 50.5733 | 0.16526 | 0.18473 |  |  |  |  | 33 | 0.01935
2382 | NTHLK2_G | 2 | North | YES | 0.14425 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.32419 | 181 | 181 | 26.1094 | 181 |  |  | 0.32419 | 58.678 | 0.16957 | 0.18918 |  |  |  |  | 34 | 0.01935
2383 | NTHLK3_G | 3 | North | YES | 0.14425 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.32419 | 329 | 329 | 47.4586 | 329 |  |  | 0.32419 | 106.6577 | 0.1774 | 0.19726 |  |  |  |  | 35 | 0.01935
2413 | MTCK6_G | 6 | North | YES | 0.14399 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.32392 | 118 | 118 | 16.9905 | 118 |  |  | 0.32392 | 38.223 | 0.18021 | 0.20016 |  |  |  |  | 36 | 0.01947
2414 | MTCK7_G | 7 | North | YES | 0.14399 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.32392 | 115 | 115 | 16.5585 | 115 |  |  | 0.32392 | 37.2512 | 0.18295 | 0.20298 |  |  |  |  | 37 | 0.019609
2417 | MTCK8_G | 8 | North | YES | 0.14399 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.32392 | 556 | 556 | 80.0568 | 556 |  |  | 0.32392 | 180.1015 | 0.19618 | 0.21663 |  |  |  |  | 38 | 0.019862
2371 | COLLIN_1G | MB | North | YES | 0.14311 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.32304 | 0 | 0 | 0 | 0 |  |  | 0.32304 | 0 | 0.19618 | 0.21663 |  |  |  |  | 39 | 0.01995
12322 | ENNSTRAC_1G | 1 | North | YES | 0.14304 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.32298 | 196 | 196 | 28.0358 | 196 |  |  | 0.32298 | 63.3034 | 0.20084 | 0.22143 |  |  |  |  | 40 | 0.020036
12323 | ENNSTRAC_2G | 2 | North | YES | 0.14304 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.32298 | 116 | 116 | 16.5926 | 116 |  |  | 0.32298 | 37.4653 | 0.20361 | 0.22427 |  |  |  |  | 41 | 0.020453
923 | SPENCER_G4 | 1 | North | YES | 0.14294 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.32287 | 61 | 61 | 8.7191 | 61 |  |  | 0.32287 | 19.6952 | 0.20506 | 0.22576 |  |  |  |  | 42 | 0.020453
924 | SPENCER_G5 | 1 | North | YES | 0.14294 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.32287 | 66 | 66 | 9.4338 | 66 |  |  | 0.32287 | 21.3096 | 0.20663 | 0.22738 |  |  |  |  | 43 | 0.020585
6948 | DENISNDM | 1 | North | YES | 0.14236 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.3223 | 0 | 0 | 0 | 0 |  |  | 0.3223 | 0 | 0.20663 | 0.22738 |  |  |  |  | 44 | 0.020664
6948 | DENISNDM | 2 | North | YES | 0.14236 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.3223 | 0 | 0 | 0 | 0 |  |  | 0.3223 | 0 | 0.20663 | 0.22738 |  |  |  |  | 45 | 0.020705
1687 | VALLEY_1G | 1 | North | YES | 0.14226 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.3222 | 170 | 170 | 24.1849 | 170 |  |  | 0.3222 | 54.7741 | 0.21067 | 0.23153 |  |  |  |  | 46 | 0.020749
1688 | VALLEY_2G | 2 | North | YES | 0.14226 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.3222 | 527 | 527 | 74.9731 | 527 |  |  | 0.3222 | 169.7997 | 0.22322 | 0.2444 |  |  |  |  | 47 | 0.020749
1689 | VALLEY_3G | 3 | North | YES | 0.14218 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.32212 | 375 | 375 | 53.3182 | 375 |  |  | 0.32212 | 120.7945 | 0.23214 | 0.25355 |  |  |  |  | 48 | 0.020749
11691 | KMICHICT1_G | 1 | North | YES | 0.14218 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32212 | 144 | 144 | 20.4742 | 144 |  |  | 0.32212 | 46.3851 | 0.23557 | 0.25707 |  |  |  |  | 49 | 0.020854
11692 | KMICHICT2_G | 2 | North | YES | 0.14218 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.32212 | 146 | 146 | 20.7586 | 146 |  |  | 0.32212 | 47.0293 | 0.23904 | 0.26063 |  |  |  |  | 50 | 0.02118
11693 | KMICHIST3_G | 3 | North | YES | 0.14218 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.32212 | 312 | 312 | 44.3608 | 312 |  |  | 0.32212 | 100.501 | 0.24647 | 0.26825 |  |  |  |  | 51 | 0.021409
11694 | KMICHICT4_G | 4 | North | YES | 0.14218 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32212 | 144 | 144 | 20.4742 | 144 |  |  | 0.32212 | 46.3851 | 0.2499 | 0.27176 |  |  |  |  | 52 | 0.021498
11695 | KMICHICT5_G | 5 | North | YES | 0.14218 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.32212 | 148 | 148 | 21.0429 | 148 |  |  | 0.32212 | 47.6736 | 0.25342 | 0.27537 |  |  |  |  | 53 | 0.021587
11696 | KMICHIST6_G | 6 | North | YES | 0.14218 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.32212 | 310 | 310 | 44.0764 | 310 |  |  | 0.32212 | 99.8568 | 0.2608 | 0.28294 |  |  |  |  | 54 | 0.021778
1678 | LAMARPWR_1G | 1 | North | YES | 0.14207 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.32201 | 160 | 160 | 22.7318 | 160 |  |  | 0.32201 | 51.5217 | 0.2646 | 0.28685 |  |  |  |  | 55 | 0.021866
1679 | LAMARPWR_2G | 2 | North | YES | 0.14207 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32201 | 156 | 156 | 22.1635 | 156 |  |  | 0.32201 | 50.2337 | 0.26832 | 0.29065 |  |  |  |  | 56 | 0.021957
1680 | LAMARPWR_3G | 3 | North | YES | 0.14207 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.32201 | 196 | 196 | 27.8465 | 196 |  |  | 0.32201 | 63.1141 | 0.27298 | 0.29544 |  |  |  |  | 57 | 0.022146
1681 | LAMARPWR_4G | 4 | North | YES | 0.14207 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32201 | 156 | 156 | 22.1635 | 156 |  |  | 0.32201 | 50.2337 | 0.27669 | 0.29924 |  |  |  |  | 58 | 0.022243
1682 | LAMARPWR_5G | 5 | North | YES | 0.14207 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.32201 | 157 | 157 | 22.3056 | 157 |  |  | 0.32201 | 50.5557 | 0.28043 | 0.30308 |  |  |  |  | 59 | 0.022337
1683 | LAMARPWR_6G | 6 | North | YES | 0.14207 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.32201 | 198 | 198 | 28.1307 | 198 |  |  | 0.32201 | 63.7581 | 0.28514 | 0.30791 |  |  |  |  | 60 | 0.022456
1675 | PEC_1G | 1 | North | YES | 0.14196 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0 | 0.28514 | 0.30791 |  |  |  |  | 61 | 0.02255
1676 | PEC_2G | 2 | North | YES | 0.14196 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0 | 0.28514 | 0.30791 |  |  |  |  | 62 | 0.022645
1677 | PEC_3G | 3 | North | YES | 0.14196 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0 | 0.28514 | 0.30791 |  |  |  |  | 63 | 0.022764
1701 | MOSES_1G | 1 | North | YES | 0.14191 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 558 | 79.1875 | 558 |  |  | 0.32185 | 179.5921 | 0.29842 | 0.32152 |  |  |  |  | 64 | 0.022764
1702 | MOSES_2G | 2 | North | YES | 0.14191 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 579 | 82.1676 | 579 |  |  | 0.32185 | 186.3509 | 0.3122 | 0.33564 |  |  |  |  | 65 | 0.022764
1703 | MOSES_3G | 3 | North | YES | 0.14191 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 808 | 114.6657 | 808 |  |  | 0.32185 | 260.0545 | 0.33143 | 0.35535 |  |  |  |  | 66 | 0.022764
5925 | DCEAST | EQ | North | YES | 0.14191 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.32185 | 0 | 0 | 0 | 0 |  |  | 0.32185 | 0 | 0.33143 | 0.35535 |  |  |  |  | 67 | 0.023094
12440 | PARKD_1SVC8 | 1 | North | YES | 0.1418 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.32173 | 0 | 0 | 0 | 0 |  |  | 0.32173 | 0 | 0.33143 | 0.35535 |  |  |  |  | 68 | 0.023437
12449 | PARKD_2SVC8 | 1 | North | YES | 0.1418 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.32173 | 0 | 0 | 0 | 0 |  |  | 0.32173 | 0 | 0.33143 | 0.35535 |  |  |  |  | 69 | 0.023915
842 | OLINGER_G1 | 1 | North | YES | 0.14177 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.3217 | 79 | 79 | 11.1996 | 79 |  |  | 0.3217 | 25.4146 | 0.33331 | 0.35728 |  |  |  |  | 70 | 0.023915
843 | OLINGER_G2 | 1 | North | YES | 0.14177 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.3217 | 110 | 110 | 15.5944 | 110 |  |  | 0.3217 | 35.3874 | 0.33593 | 0.35996 |  |  |  |  | 71 | 0.023915
844 | OLINGER_G3 | 1 | North | YES | 0.14177 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.3217 | 150 | 150 | 21.265 | 150 |  |  | 0.3217 | 48.2555 | 0.3395 | 0.36361 |  |  |  |  | 72 | 0.023915
845 | OLINGER_G4 | 1 | North | YES | 0.14177 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.3217 | 76 | 76 | 10.7743 | 76 |  |  | 0.3217 | 24.4495 | 0.34131 | 0.36547 |  |  |  |  | 73 | 0.023961
728 | WOLFRIDGE801 | 1 | North | YES | 0.14175 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.32169 | 0 | 112.5 | 15.947 | 112.5 |  |  | 0.32169 | 36.1899 | 0.34399 | 0.36821 |  |  |  |  | 74 | 0.024025
837 | NEWMAN_G5 | 1 | North | YES | 0.14174 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.32167 | 40 | 40 | 5.6695 | 40 |  |  | 0.32167 | 12.8669 | 0.34494 | 0.36918 |  |  |  |  | 75 | 0.024112
949 | STEAM2 | 1 | North | YES | 0.14158 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.32152 | 26 | 26 | 3.6811 | 26 |  |  | 0.32152 | 8.3594 | 0.34556 | 0.36982 |  |  |  |  | 76 | 0.024156
950 | STEAM3 | 1 | North | YES | 0.14158 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.32152 | 42 | 42 | 5.9463 | 42 |  |  | 0.32152 | 13.5037 | 0.34656 | 0.37084 |  |  |  |  | 77 | 0.024221
948 | STEAM1 | 1 | North | YES | 0.14158 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.32151 | 20 | 20 | 2.8316 | 20 |  |  | 0.32151 | 6.4303 | 0.34703 | 0.37133 |  |  |  |  | 78 | 0.024244
2451 | LKHB1_G | 1 | North | YES | 0.14151 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.32145 | 391 | 391 | 55.332 | 391 |  |  | 0.32145 | 125.6872 | 0.35634 | 0.38085 |  |  |  |  | 79 | 0.024259
2452 | LKHB2_G | 2 | North | YES | 0.14151 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.32145 | 516 | 516 | 73.0212 | 516 |  |  | 0.32145 | 165.8685 | 0.36862 | 0.39342 |  |  |  |  | 80 | 0.024283
580 | JCKCNTY801 | 1 | North | YES | 0.14141 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.32135 | 288 | 288 | 40.7267 | 288 |  |  | 0.32135 | 92.5484 | 0.37548 | 0.40044 |  |  |  |  | 81 | 0.024294
581 | JCKCNTY802 | 2 | North | YES | 0.14141 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32135 | 147 | 147 | 20.7876 | 147 |  |  | 0.32135 | 47.2382 | 0.37897 | 0.40402 |  |  |  |  | 82 | 0.024514
582 | JCKCNTY803 | 3 | North | YES | 0.14141 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32135 | 147 | 147 | 20.7876 | 147 |  |  | 0.32135 | 47.2382 | 0.38247 | 0.4076 |  |  |  |  | 83 | 0.024803
12411 | FPLEFR1A_G | 1 | North | YES | 0.14061 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32054 | 161 | 161 | 22.6379 | 161 |  |  | 0.32054 | 51.6077 | 0.3863 | 0.41151 |  |  |  |  | 84 | 0.024963
12412 | FPLEFR1B_G | 2 | North | YES | 0.14061 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32054 | 164 | 164 | 23.0597 | 164 |  |  | 0.32054 | 52.5693 | 0.39021 | 0.41549 |  |  |  |  | 85 | 0.025044
12413 | FPLEFR1C_G | 3 | North | YES | 0.14061 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32054 | 164 | 164 | 23.0597 | 164 |  |  | 0.32054 | 52.5693 | 0.39411 | 0.41948 |  |  |  |  | 86 | 0.025125
12414 | FPLEFR1S_G | 4 | North | YES | 0.14061 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.32054 | 414 | 414 | 58.2117 | 414 |  |  | 0.32054 | 132.7055 | 0.40396 | 0.42953 |  |  |  |  | 87 | 0.025205
12421 | FPLEFR2A_G | 1 | North | YES | 0.14061 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.32054 | 162 | 162 | 22.7785 | 162 |  |  | 0.32054 | 51.9282 | 0.40782 | 0.43347 |  |  |  |  | 88 | 0.025286
12422 | FPLEFR2B_G | 2 | North | YES | 0.14061 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32054 | 161 | 161 | 22.6379 | 161 |  |  | 0.32054 | 51.6077 | 0.41165 | 0.43738 |  |  |  |  | 89 | 0.025366
12423 | FPLEFR2C_G | 3 | North | YES | 0.14061 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.32054 | 163 | 163 | 22.9191 | 163 |  |  | 0.32054 | 52.2488 | 0.41553 | 0.44134 |  |  |  |  | 90 | 0.02557
12424 | FPLEFR2S_G | 4 | North | YES | 0.14061 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.32054 | 415 | 415 | 58.3523 | 415 |  |  | 0.32054 | 133.026 | 0.42541 | 0.45142 |  |  |  |  | 91 | 0.02565
503 | NTHTEXAS01 | 1 | North | YES | 0.14048 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.32042 | 18 | 18 | 2.5286 | 18 |  |  | 0.32042 | 5.7675 | 0.42584 | 0.45186 |  |  |  |  | 92 | 0.02573
504 | NTHTEXAS02 | 2 | North | YES | 0.14048 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.32042 | 18 | 18 | 2.5286 | 18 |  |  | 0.32042 | 5.7675 | 0.42626 | 0.4523 |  |  |  |  | 93 | 0.02581
505 | NTHTEXAS03 | 3 | North | YES | 0.14048 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.32042 | 38 | 38 | 5.3382 | 38 |  |  | 0.32042 | 12.1758 | 0.42717 | 0.45322 |  |  |  |  | 94 | 0.026014
1453 | WCPWRCO_1G | 1 | North | YES | 0.14048 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.32041 | 204 | 204 | 28.6571 | 204 |  |  | 0.32041 | 65.3642 | 0.43202 | 0.45817 |  |  |  |  | 95 | 0.026023
1454 | WCPWRCO_2G | 2 | North | YES | 0.14048 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.32041 | 204 | 204 | 28.6571 | 204 |  |  | 0.32041 | 65.3642 | 0.43688 | 0.46313 |  |  |  |  | 96 | 0.026032
1455 | WCPWRCO_3G | 3 | North | YES | 0.14048 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.32041 | 242 | 242 | 33.9952 | 242 |  |  | 0.32041 | 77.5399 | 0.44264 | 0.469 |  |  |  |  | 97 | 0.02605
332 | RWMILLER01 | 1 | North | YES | 0.13821 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.31814 | 73 | 73 | 10.0892 | 73 |  |  | 0.31814 | 23.2246 | 0.44438 | 0.47076 |  |  |  |  | 98 | 0.026149
333 | RWMILLER02 | 2 | North | YES | 0.13821 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.31814 | 119 | 119 | 16.4468 | 119 |  |  | 0.31814 | 37.8592 | 0.44721 | 0.47363 |  |  |  |  | 99 | 0.026247
334 | RWMILLER03 | 3 | North | YES | 0.13821 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.31814 | 208 | 208 | 28.7473 | 208 |  |  | 0.31814 | 66.1741 | 0.45216 | 0.47865 |  |  |  |  | 100 | 0.026364
335 | RWMILLER04 | 4 | North | YES | 0.13821 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.31814 | 102 | 102 | 14.0972 | 102 |  |  | 0.31814 | 32.4508 | 0.45459 | 0.48111 |  |  |  |  | 101 | 0.026387
336 | RWMILLER05 | 5 | North | YES | 0.13821 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.31814 | 101 | 101 | 13.959 | 101 |  |  | 0.31814 | 32.1326 | 0.45699 | 0.48354 |  |  |  |  | 102 | 0.026424
344 | MRSSHPRD | 1 | North | YES | 0.13746 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.3174 | 0 | 0 | 0 | 0 |  |  | 0.3174 | 0 | 0.45699 | 0.48354 |  |  |  |  | 103 | 0.026488
345 | MRSSHPRD01 | 2 | North | YES | 0.13746 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.3174 | 0 | 0 | 0 | 0 |  |  | 0.3174 | 0 | 0.45699 | 0.48354 |  |  |  |  | 104 | 0.02652
1600 | BARTNWND_1G | 1 | North | YES | 0.13725 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.31718 | 0 | 120 | 16.4696 | 120 |  |  | 0.31718 | 38.062 | 0.45985 | 0.48643 |  |  |  |  | 105 | 0.026551
3126 | TRINIDAD_6G | 1 | North | YES | 0.13717 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.31711 | 224 | 224 | 30.727 | 224 |  |  | 0.31711 | 71.0328 | 0.46518 | 0.49181 |  |  |  |  | 106 | 0.026551
3097 | MARTLAKE_1G | 1 | North | YES | 0.13627 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 790 | 107.6549 | 790 |  |  | 0.31621 | 249.8048 | 0.48398 | 0.51074 |  |  |  |  | 107 | 0.026551
3098 | MARTLAKE_2G | 2 | North | YES | 0.13627 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 795 | 108.3362 | 795 |  |  | 0.31621 | 251.3859 | 0.5029 | 0.52979 |  |  |  |  | 108 | 0.02658
3099 | MARTLAKE_3G | 3 | North | YES | 0.13627 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 804 | 109.5627 | 804 |  |  | 0.31621 | 254.2317 | 0.52204 | 0.54906 |  |  |  |  | 109 | 0.026632
13116 | TGATEWAY_1G | 1 | North | YES | 0.13575 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.31569 | 151 | 151 | 20.4986 | 151 |  |  | 0.31569 | 47.669 | 0.52563 | 0.55267 |  |  |  |  | 110 | 0.026762
13117 | TGATEWAY_2G | 2 | North | YES | 0.13575 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.31569 | 130 | 130 | 17.6478 | 130 |  |  | 0.31569 | 41.0395 | 0.52872 | 0.55578 |  |  |  |  | 111 | 0.026892
13118 | TGATEWAY_3G | 3 | North | YES | 0.13575 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.31569 | 148 | 148 | 20.0913 | 148 |  |  | 0.31569 | 46.7219 | 0.53225 | 0.55932 |  |  |  |  | 112 | 0.027024
13119 | TGATEWAY_4G | 4 | North | YES | 0.13575 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.31569 | 399 | 399 | 54.165 | 399 |  |  | 0.31569 | 125.9598 | 0.54174 | 0.56887 |  |  |  |  | 113 | 0.027043
1432 | GRHAMSES_2G | 2 | North | YES | 0.1357 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.31563 | 366 | 366 | 49.6655 | 366 |  |  | 0.31563 | 115.5223 | 0.55045 | 0.57762 |  |  |  |  | 114 | 0.027059
1479 | WFCOGEN_1G | 1 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0 | 0.55045 | 0.57762 |  |  |  |  | 115 | 0.027078
1479 | WFCOGEN_1G | 2 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0 | 0.55045 | 0.57762 |  |  |  |  | 116 | 0.027128
1482 | WFCOGEN_2G | 2 | North | YES | 0.13562 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0 | 0.55045 | 0.57762 |  |  |  |  | 117 | 0.027172
1482 | WFCOGEN_2G | 1 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0 | 0.55045 | 0.57762 |  |  |  |  | 118 | 0.027172
3348 | CHAMPION_1G | MB | North | YES | 0.13501 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.31495 | 0 | 0 | 0 | 0 |  |  | 0.31495 | 0 | 0.55045 | 0.57762 |  |  |  |  | 119 | 0.027172
3309 | ASPN_G | 1 | North | YES | 0.13498 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.31491 | 50 | 50 | 6.7489 | 50 |  |  | 0.31491 | 15.7457 | 0.55164 | 0.57882 |  |  |  |  | 120 | 0.027172
1433 | GRHAMSES_1G | 1 | North | YES | 0.13454 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.31448 | 242 | 242 | 32.5592 | 242 |  |  | 0.31448 | 76.1038 | 0.5574 | 0.58458 |  |  |  |  | 121 | 0.027172
3107 | STRYKER_1G | 1 | North | YES | 0.13427 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.31421 | 182 | 182 | 24.4371 | 182 |  |  | 0.31421 | 57.1856 | 0.56173 | 0.58892 |  |  |  |  | 122 | 0.027172
3108 | STRYKER_2G | 2 | North | YES | 0.13427 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.31421 | 484 | 484 | 64.9867 | 484 |  |  | 0.31421 | 152.076 | 0.57325 | 0.60044 |  |  |  |  | 123 | 0.027175
6100 | OKLA7A | EQ | West | YES | 0.13155 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.31148 | 0 | 0 |  |  |  |  | 0.31148 | 0 | 0.57325 | 0.60044 |  |  |  |  | 124 | 0.027183
6752 | OKLA0A | 1 | West | YES | 0.13155 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.31148 | 0 | 649.7 |  |  |  |  | 0.31148 | 202.3709 | 0.58872 | 0.61578 |  |  |  |  | 125 | 0.027185
1442 | COKFIELD_5 | 1 | North | YES | 0.13041 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.31035 | 0 | 165 | 21.5178 | 165 |  |  | 0.31035 | 51.2074 | 0.59264 | 0.61966 |  |  |  |  | 126 | 0.027191
13134 | CALFREST_4G | 4 | North | YES | 0.1302 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.31014 | 151.5 | 151.5 | 19.7255 | 151.5 |  |  | 0.31014 | 46.9859 | 0.59625 | 0.62322 |  |  |  |  | 127 | 0.027191
13135 | CALFREST_5G | 5 | North | YES | 0.1302 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.31014 | 152.3 | 152.3 | 19.8296 | 152.3 |  |  | 0.31014 | 47.234 | 0.59987 | 0.6268 |  |  |  |  | 128 | 0.027065
13136 | CALFREST_6G | 6 | North | YES | 0.1302 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.31014 | 177.5 | 177.5 | 23.1107 | 177.5 |  |  | 0.31014 | 55.0494 | 0.6041 | 0.63097 |  |  |  |  | 129 | 0.027019
13131 | CALFREST_1G | 1 | North | YES | 0.13002 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.30996 | 150.7 | 150.7 | 19.5945 | 150.7 |  |  | 0.30996 | 46.7109 | 0.60768 | 0.63451 |  |  |  |  | 130 | 0.026974
13132 | CALFREST_2G | 2 | North | YES | 0.13002 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.30996 | 151 | 151 | 19.6335 | 151 |  |  | 0.30996 | 46.8039 | 0.61128 | 0.63806 |  |  |  |  | 131 | 0.026929
13133 | CALFREST_3G | 3 | North | YES | 0.13002 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.30996 | 177.4 | 177.4 | 23.0661 | 177.4 |  |  | 0.30996 | 54.9868 | 0.6155 | 0.64223 |  |  |  |  | 132 | 0.026877
1643 | SLSTR1PP_1G | 1 | North | YES | 0.12968 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.30961 | 0 | 60 | 7.7806 | 60 |  |  | 0.30961 | 18.5768 | 0.61693 | 0.64364 |  |  |  |  | 133 | 0.02683
3381 | BBRN_1G | 1 | North | YES | 0.12876 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.30869 | 0 | 618 | 79.5718 | 618 |  |  | 0.30869 | 190.7727 | 0.63164 | 0.65809 |  |  |  |  | 134 | 0.026783
3382 | BBRN_2G | 2 | North | YES | 0.12876 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.30869 | 0 | 589 | 75.8379 | 589 |  |  | 0.30869 | 181.8206 | 0.64565 | 0.67187 |  |  |  |  | 135 | 0.026728
1438 | MESQUITW_2G | 1 | North | YES | 0.12874 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.30868 | 0 | 236 | 30.3829 | 236 |  |  | 0.30868 | 72.8479 | 0.65127 | 0.67739 |  |  |  |  | 136 | 0.026708
1437 | MESQUITW_1G | 1 | North | YES | 0.12873 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.30867 | 0 | 400 | 51.4928 | 400 |  |  | 0.30867 | 123.4675 | 0.66079 | 0.68675 |  |  |  |  | 137 | 0.026458
60081 | WHRLWIND1A | 1 | West | YES | 0.12555 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.30549 | 0 | 60 |  |  |  |  | 0.30549 | 18.3291 | 0.66222 | 0.68814 |  |  |  |  | 138 | 0.026219
1416 | SWETWATR_1G | 1 | West | YES | 0.12461 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.30455 | 30 | 30 |  |  |  |  | 0.30455 | 9.1364 | 0.66293 | 0.68883 |  |  |  |  | 139 | 0.026123
1417 | SWETWATR_2G | 2 | West | YES | 0.12461 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.30455 | 72 | 72 |  |  |  |  | 0.30455 | 21.9274 | 0.66465 | 0.69049 |  |  |  |  | 140 | 0.02596
1418 | SWETWATR_3G | 3 | West | YES | 0.12461 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.30455 | 68 | 68 |  |  |  |  | 0.30455 | 20.7092 | 0.66626 | 0.69206 |  |  |  |  | 141 | 0.025921
1419 | SWETWATR_4G | 4 | West | YES | 0.12461 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.30455 | 61 | 61 |  |  |  |  | 0.30455 | 18.5773 | 0.66772 | 0.69347 |  |  |  |  | 142 | 0.0259
11056 | ROSCOE_1G | 1 | West | YES | 0.12374 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.30368 | 0 | 209 |  |  |  |  | 0.30368 | 63.4693 | 0.67269 | 0.69828 |  |  |  |  | 143 | 0.025848
11057 | CHAMPION_1G | 1 | West | YES | 0.12374 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.30368 | 0 | 126.5 |  |  |  |  | 0.30368 | 38.4156 | 0.6757 | 0.70119 |  |  |  |  | 144 | 0.025799
11058 | PYRON_1G | 1 | West | YES | 0.12374 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.30368 | 0 | 249 |  |  |  |  | 0.30368 | 75.6165 | 0.68163 | 0.70692 |  |  |  |  | 145 | 0.025755
11059 | INADALE_1G | 1 | West | YES | 0.12374 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.30368 | 0 | 197 |  |  |  |  | 0.30368 | 59.8251 | 0.68632 | 0.71146 |  |  |  |  | 146 | 0.025591
6144 | MCADOO1A | 1 | West | YES | 0.12365 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.30358 | 0 | 150 |  |  |  |  | 0.30358 | 45.5372 | 0.68989 | 0.71491 |  |  |  |  | 147 | 0.025492
71051 | L_BITTCR1_1N | W1 | West | YES | 0.12356 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 37.5 |  |  |  |  | 0.3035 | 11.3812 | 0.69078 | 0.71577 |  |  |  |  | 148 | 0.025296
71054 | L_SWEETW1_1N | W1 | West | YES | 0.12356 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 107.5 |  |  |  |  | 0.3035 | 32.6262 | 0.69334 | 0.71824 |  |  |  |  | 149 | 0.025141
71057 | L_SWEETW1_2N | W1 | West | YES | 0.12356 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 135 |  |  |  |  | 0.3035 | 40.9725 | 0.69655 | 0.72135 |  |  |  |  | 150 | 0.025022
71059 | L_SWEETW1_3N | W1 | West | YES | 0.12356 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 119 |  |  |  |  | 0.3035 | 36.1165 | 0.69938 | 0.72409 |  |  |  |  | 151 | 0.024992
71060 | L_SWEETW1_4N | W1 | West | YES | 0.12356 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 105 |  |  |  |  | 0.3035 | 31.8675 | 0.70188 | 0.7265 |  |  |  |  | 152 | 0.024907
71061 | L_SWEETW1_5N | W1 | West | YES | 0.12356 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 80.5 |  |  |  |  | 0.3035 | 24.4317 | 0.7038 | 0.72835 |  |  |  |  | 153 | 0.024799
6407 | TURKTRAK1A | 1 | West | YES | 0.12258 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.30252 | 0 | 169.5 |  |  |  |  | 0.30252 | 51.2771 | 0.70783 | 0.73224 |  |  |  |  | 154 | 0.024704
1343 | TRENTIPP_8 | 1 | West | YES | 0.12229 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.30223 | 0 | 150 |  |  |  |  | 0.30223 | 45.3338 | 0.7114 | 0.73567 |  |  |  |  | 155 | 0.02462
1354 | AEPWIND_8 | 1 | West | YES | 0.12229 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.30223 | 0 | 101 |  |  |  |  | 0.30223 | 30.5248 | 0.7138 | 0.73799 |  |  |  |  | 156 | 0.024555
36998 | RDCNYNG1 | 1 | West | YES | 0.12222 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.30215 | 0 | 84 |  |  |  |  | 0.30215 | 25.381 | 0.7158 | 0.73991 |  |  |  |  | 157 | 0.024407
1061 | CIELOGEN_1G | 1 | West | YES | 0.12189 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.30183 | 0 | 99 |  |  |  |  | 0.30183 | 29.8811 | 0.71816 | 0.74218 |  |  |  |  | 158 | 0.024273
1062 | CIELOGEN_2G | 1 | West | YES | 0.12189 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.30183 | 0 | 61 |  |  |  |  | 0.30183 | 18.4116 | 0.71961 | 0.74357 |  |  |  |  | 159 | 0.024183
1069 | KINDERMG_1G | 1 | West | YES | 0.12189 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0 | 0.71961 | 0.74357 |  |  |  |  | 160 | 0.024107
1070 | KINDERMG_2G | 1 | West | YES | 0.12189 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0 | 0.71961 | 0.74357 |  |  |  |  | 161 | 0.024015
1071 | KINDERMG_3G | 1 | West | YES | 0.12189 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0 | 0.71961 | 0.74357 |  |  |  |  | 162 | 0.023959
1068 | SCURRYCW_1G | 1 | West | YES | 0.12187 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.30181 | 0 | 141 |  |  |  |  | 0.30181 | 42.5553 | 0.72297 | 0.7468 |  |  |  |  | 163 | 0.023959
1073 | SCURRYCW_2G | 2 | West | YES | 0.12187 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.30181 | 0 | 120 |  |  |  |  | 0.30181 | 36.2173 | 0.72582 | 0.74954 |  |  |  |  | 164 | 0.023959
6637 | SNYDERW1A | 1 | West | YES | 0.12174 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.30168 | 0 | 63 |  |  |  |  | 0.30168 | 19.0059 | 0.72732 | 0.75098 |  |  |  |  | 165 | 0.023959
1037 | MORGAN5G_5G | 5 | West | YES | 0.12167 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.3016 | 137 | 137 |  |  |  |  | 0.3016 | 41.3198 | 0.73058 | 0.75411 |  |  |  |  | 166 | 0.023828
1039 | MRGNAG_1G | A | West | YES | 0.12167 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.3016 | 69 | 69 |  |  |  |  | 0.3016 | 20.8107 | 0.73223 | 0.75569 |  |  |  |  | 167 | 0.023717
1040 | MRGNBG_2G | B | West | YES | 0.12167 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.3016 | 71 | 71 |  |  |  |  | 0.3016 | 21.4139 | 0.73392 | 0.75731 |  |  |  |  | 168 | 0.023658
1041 | MRGNCG_3G | C | West | YES | 0.12167 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.3016 | 70 | 70 |  |  |  |  | 0.3016 | 21.1123 | 0.73558 | 0.75891 |  |  |  |  | 169 | 0.023529
1042 | MRGNDG_4G | D | West | YES | 0.12167 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.3016 | 68 | 68 |  |  |  |  | 0.3016 | 20.5091 | 0.7372 | 0.76047 |  |  |  |  | 170 | 0.023464
1043 | MRGNEG_5G | E | West | YES | 0.12167 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.3016 | 70 | 70 |  |  |  |  | 0.3016 | 21.1123 | 0.73887 | 0.76207 |  |  |  |  | 171 | 0.023397
1044 | MRGNFG_6G | F | West | YES | 0.12167 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.3016 | 66 | 66 |  |  |  |  | 0.3016 | 19.9059 | 0.74044 | 0.76358 |  |  |  |  | 172 | 0.023331
1058 | LONGSHORE_5 | 1 | West | YES | 0.12148 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.30141 | 0 | 150 |  |  |  |  | 0.30141 | 45.212 | 0.74401 | 0.767 |  |  |  |  | 173 | 0.023267
1058 | LONGSHORE_5 | 2 | West | YES | 0.12148 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.30141 | 0 | 220 |  |  |  |  | 0.30141 | 66.311 | 0.74924 | 0.77203 |  |  |  |  | 174 | 0.023201
11065 | ELBOWCK_1G | 1 | West | YES | 0.12148 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.30141 | 0 | 121.9 |  |  |  |  | 0.30141 | 36.7423 | 0.75214 | 0.77481 |  |  |  |  | 175 | 0.023139
60058 | BUFF_GAP1A | 1 | West | YES | 0.12125 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30118 | 0 | 120 |  |  |  |  | 0.30118 | 36.1418 | 0.755 | 0.77755 |  |  |  |  | 176 | 0.022995
60060 | CIRELLO | 1 | West | YES | 0.12125 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.30118 | 0 | 233 |  |  |  |  | 0.30118 | 70.1753 | 0.76055 | 0.78287 |  |  |  |  | 177 | 0.022784
60063 | BUFF_GAP1B | 1 | West | YES | 0.12125 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.30118 | 0 | 170.2 |  |  |  |  | 0.30118 | 51.2611 | 0.7646 | 0.78675 |  |  |  |  | 178 | 0.022668
60066 | H_HOLLOW1A | 1 | West | YES | 0.12125 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.30118 | 0 | 222 |  |  |  |  | 0.30118 | 66.8623 | 0.76988 | 0.79182 |  |  |  |  | 179 | 0.022551
60068 | HHOLLOW21A | 1 | West | YES | 0.12125 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 184 |  |  |  |  | 0.30118 | 55.4174 | 0.77426 | 0.79602 |  |  |  |  | 180 | 0.022324
60070 | HHOLLOW31A | 1 | West | YES | 0.12125 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 224 |  |  |  |  | 0.30118 | 67.4647 | 0.77959 | 0.80113 |  |  |  |  | 181 | 0.022158
60072 | HHOLLOW41A | 1 | West | YES | 0.12125 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 115 |  |  |  |  | 0.30118 | 34.6359 | 0.78233 | 0.80376 |  |  |  |  | 182 | 0.021941
1045 | CALENG1G_1G | 1 | West | YES | 0.12114 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0 | 0.78233 | 0.80376 |  |  |  |  | 183 | 0.021762
1046 | CALENG2G_2G | 2 | West | YES | 0.12114 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0 | 0.78233 | 0.80376 |  |  |  |  | 184 | 0.021544
1047 | CALENG3G_3G | 3 | West | YES | 0.12114 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0 | 0.78233 | 0.80376 |  |  |  |  | 185 | 0.021432
11309 | BULLCREK_2G | 1 | West | YES | 0.1211 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.30104 | 0 | 180 |  |  |  |  | 0.30104 | 54.1866 | 0.78661 | 0.80786 |  |  |  |  | 186 | 0.021432
11310 | BULLCREK_1G | 1 | West | YES | 0.1211 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.30104 | 0 | 180 |  |  |  |  | 0.30104 | 54.1866 | 0.79089 | 0.81197 |  |  |  |  | 187 | 0.021432
11320 | COYOTE_1G | 1 | West | YES | 0.12099 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.30092 | 0 | 225 |  |  |  |  | 0.30092 | 67.708 | 0.79625 | 0.8171 |  |  |  |  | 188 | 0.021432
1360 | GUNSIGHT_8 | 1 | West | YES | 0.12046 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.30039 | 0 | 120 |  |  |  |  | 0.30039 | 36.047 | 0.79911 | 0.81983 |  |  |  |  | 189 | 0.021254
1327 | WILDHRSE_1G | 1 | West | YES | 0.1204 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.30033 | 0 | 120 |  |  |  |  | 0.30033 | 36.0398 | 0.80196 | 0.82257 |  |  |  |  | 190 | 0.021077
1333 | MCDDONAL_8 | 1 | West | YES | 0.12004 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.29998 | 0 | 214.2 |  |  |  |  | 0.29998 | 64.2561 | 0.80706 | 0.82744 |  |  |  |  | 191 | 0.020853
1328 | OCOTILLO_1G | 1 | West | YES | 0.11975 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.29968 | 0 | 58 |  |  |  |  | 0.29968 | 17.3815 | 0.80844 | 0.82875 |  |  |  |  | 192 | 0.020729
11001 | NAV1CT | 1 | West | YES | 0.11969 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.29963 | 70.4 | 70.4 |  |  |  |  | 0.29963 | 21.0938 | 0.81012 | 0.83035 |  |  |  |  | 193 | 0.020604
11009 | NAV2CT | 1 | West | YES | 0.11969 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.29963 | 71.4 | 71.4 |  |  |  |  | 0.29963 | 21.3934 | 0.81181 | 0.83197 |  |  |  |  | 194 | 0.020376
11011 | NAV3ST | 1 | West | YES | 0.11969 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.29963 | 92.8 | 92.8 |  |  |  |  | 0.29963 | 27.8054 | 0.81402 | 0.83408 |  |  |  |  | 195 | 0.020313
11012 | NAV4CT | 1 | West | YES | 0.11969 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.29963 | 80 | 80 |  |  |  |  | 0.29963 | 23.9702 | 0.81593 | 0.8359 |  |  |  |  | 196 | 0.020236
11013 | NAV5CT | 1 | West | YES | 0.11969 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.29963 | 80 | 80 |  |  |  |  | 0.29963 | 23.9702 | 0.81783 | 0.83771 |  |  |  |  | 197 | 0.020158
11014 | NAV6ST | 1 | West | YES | 0.11969 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.29963 | 115 | 115 |  |  |  |  | 0.29963 | 34.4572 | 0.82057 | 0.84032 |  |  |  |  | 198 | 0.020057
11020 | TIEHVSG_1G | 1 | West | YES | 0.11967 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.29961 | 208.2 | 208.2 |  |  |  |  | 0.29961 | 62.3783 | 0.82552 | 0.84505 |  |  |  |  | 199 | 0.019969
11021 | TIEHVCG_1G | 1 | West | YES | 0.11967 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.29961 | 142.1 | 142.1 |  |  |  |  | 0.29961 | 42.5742 | 0.82891 | 0.84828 |  |  |  |  | 200 | 0.019882
11022 | TIEHVCG_2G | 1 | West | YES | 0.11967 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.29961 | 132.4 | 132.4 |  |  |  |  | 0.29961 | 39.6681 | 0.83206 | 0.85128 |  |  |  |  | 201 | 0.019756
11023 | TIEHVCG_3G | 1 | West | YES | 0.11967 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.29961 | 137.4 | 137.4 |  |  |  |  | 0.29961 | 41.1661 | 0.83533 | 0.8544 |  |  |  |  | 202 | 0.019528
11024 | TIEHVCG_4G | 1 | West | YES | 0.11967 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.29961 | 147 | 147 |  |  |  |  | 0.29961 | 44.0423 | 0.83883 | 0.85774 |  |  |  |  | 203 | 0.019373
11025 | TIEHVSG_2G | 1 | West | YES | 0.11967 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.29961 | 213.2 | 213.2 |  |  |  |  | 0.29961 | 63.8763 | 0.8439 | 0.86258 |  |  |  |  | 204 | 0.019228
1326 | STANTONW_8 | 1 | West | YES | 0.11955 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.29948 | 0 | 100.5 |  |  |  |  | 0.29948 | 30.0982 | 0.84629 | 0.86486 |  |  |  |  | 205 | 0.019078
1320 | BSP 1 | 1 | West | YES | 0.11914 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.29908 | 0 | 0 |  |  |  |  | 0.29908 | 0 | 0.84629 | 0.86486 |  |  |  |  | 206 | 0.018917
76031 | L_GASCCR1_1N | W1 | West | YES | 0.11831 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.29825 | 0 | 150 |  |  |  |  | 0.29825 | 44.7374 | 0.84986 | 0.86825 |  |  |  |  | 207 | 0.018684
11147 | NOTREES_1G | 1 | West | YES | 0.11829 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.29823 | 0 | 149 |  |  |  |  | 0.29823 | 44.4359 | 0.85341 | 0.87162 |  |  |  |  | 208 | 0.018573
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.11806 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.298 | 0 | 35 |  |  |  |  | 0.298 | 10.43 | 0.85424 | 0.87241 |  |  |  |  | 209 | 0.018573
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.11806 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.298 | 0 | 30 |  |  |  |  | 0.298 | 8.94 | 0.85495 | 0.87309 |  |  |  |  | 210 | 0.018393
1002 | PBCTAGE_1G | A | West | YES | 0.11795 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.29788 | 66 | 66 |  |  |  |  | 0.29788 | 19.6603 | 0.85653 | 0.87458 |  |  |  |  | 211 | 0.018215
1003 | PBCTBGE_2G | B | West | YES | 0.11795 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.29788 | 66 | 66 |  |  |  |  | 0.29788 | 19.6603 | 0.8581 | 0.87607 |  |  |  |  | 212 | 0.018172
1004 | PBCTCGE_3G | C | West | YES | 0.11795 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.29788 | 67 | 67 |  |  |  |  | 0.29788 | 19.9581 | 0.85969 | 0.87758 |  |  |  |  | 213 | 0.018136
1005 | PBCTDGE_4G | D | West | YES | 0.11795 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.29788 | 68 | 68 |  |  |  |  | 0.29788 | 20.256 | 0.86131 | 0.87912 |  |  |  |  | 214 | 0.018055
1006 | PBCTEGE_5G | E | West | YES | 0.11795 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.29788 | 67 | 67 |  |  |  |  | 0.29788 | 19.9581 | 0.8629 | 0.88063 |  |  |  |  | 215 | 0.017974
1007 | PB5GEN_6G | 5 | West | YES | 0.11795 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.29788 | 114 | 114 |  |  |  |  | 0.29788 | 33.9586 | 0.86562 | 0.8832 |  |  |  |  | 216 | 0.017892
1008 | PB6GEN_7G | 6 | West | YES | 0.11795 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.29788 | 515 | 515 |  |  |  |  | 0.29788 | 153.4096 | 0.87787 | 0.89483 |  |  |  |  | 217 | 0.017809
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.1176 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.29754 | 0 | 112.5 |  |  |  |  | 0.29754 | 33.4732 | 0.88055 | 0.89737 |  |  |  |  | 218 | 0.017727
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.1176 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 149.5 |  |  |  |  | 0.29754 | 44.4822 | 0.88411 | 0.90074 |  |  |  |  | 219 | 0.017587
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.1176 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 186 |  |  |  |  | 0.29754 | 55.3424 | 0.88854 | 0.90493 |  |  |  |  | 220 | 0.016956
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.1176 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 214.5 |  |  |  |  | 0.29754 | 63.8223 | 0.89364 | 0.90977 |  |  |  |  | 221 | 0.016816
1349 | WESTXWIN_1G | 1 | West | YES | 0.11655 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.29649 | 0 | 6.6 |  |  |  |  | 0.29649 | 1.9568 | 0.8938 | 0.90992 |  |  |  |  | 222 | 0.016629
1350 | NWPWRG1_1G | 1 | West | YES | 0.11655 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.29649 | 0 | 34.3 |  |  |  |  | 0.29649 | 10.1695 | 0.89461 | 0.91069 |  |  |  |  | 223 | 0.016396
60057 | CALLAHAN1A | 1 | West | YES | 0.11624 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.29618 | 0 | 114 |  |  |  |  | 0.29618 | 33.7646 | 0.89733 | 0.91325 |  |  |  |  | 224 | 0.016128
48721 | LEG_1___1 | 1 | North | YES | 0.10828 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.28822 | 0 | 827 | 89.55 | 827 |  |  | 0.28822 | 238.3576 | 0.91701 | 0.93131 |  |  |  |  | 225 | 0.016119
48722 | LEG_2___2 | 2 | North | YES | 0.10828 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.28822 | 0 | 819 | 88.6838 | 819 |  |  | 0.28822 | 236.0519 | 0.9365 | 0.9492 |  |  |  |  | 226 | 0.016073
60007 | KING_SW1A | 1 | West | YES | 0.10656 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.2865 | 0 | 80 |  |  |  |  | 0.2865 | 22.9199 | 0.93841 | 0.95094 |  |  |  |  | 227 | 0.015919
60019 | KING_NW1A | 1 | West | YES | 0.10656 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.2865 | 0 | 80 |  |  |  |  | 0.2865 | 22.9199 | 0.94031 | 0.95267 |  |  |  |  | 228 | 0.014301
60201 | RIO DRCS | F | West | YES | 0.10605 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.28599 | 0 | 0 |  |  |  |  | 0.28599 | 0 | 0.94031 | 0.95267 |  |  |  |  | 229 | 0.012698
6016 | SWMESA | 1 | West | YES | 0.10584 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.28577 | 0 | 75 |  |  |  |  | 0.28577 | 21.433 | 0.9421 | 0.9543 |  |  |  |  | 230 | 0.012531
60003 | KING_NE1A | 1 | West | YES | 0.10584 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28577 | 0 | 80 |  |  |  |  | 0.28577 | 22.8619 | 0.944 | 0.95603 |  |  |  |  | 231 | 0.012364
60005 | KING_SE1A | 1 | West | YES | 0.10584 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.28577 | 0 | 40 |  |  |  |  | 0.28577 | 11.4309 | 0.94495 | 0.9569 |  |  |  |  | 232 | 0.012364
60016 | WOODWRD11A | 1 | West | YES | 0.1057 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.28564 | 0 | 80 |  |  |  |  | 0.28564 | 22.8513 | 0.94685 | 0.95863 |  |  |  |  | 233 | 0.012203
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.10568 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.28562 | 0 | 80 |  |  |  |  | 0.28562 | 22.8493 | 0.94876 | 0.96036 |  |  |  |  | 234 | 0.012032
38437 | TNSRBNMESA9 | 1 | West | YES | 0.10557 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.2855 | 0 | 150 |  |  |  |  | 0.2855 | 42.8254 | 0.95233 | 0.96361 |  |  |  |  | 235 | 0.011946
60017 | ORNNWP1 | 1 | West | YES | 0.10169 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.28163 | 0 | 80 |  |  |  |  | 0.28163 | 22.5305 | 0.95423 | 0.96531 |  |  |  |  | 236 | 0.011774
60000 | DSKY2 | 1 | West | YES | 0.10065 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.28059 | 0 | 76.5 |  |  |  |  | 0.28059 | 21.4653 | 0.95605 | 0.96694 |  |  |  |  | 237 | 0.011602
60018 | DSKY1 | 1 | West | YES | 0.10039 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.28032 | 0 | 84 |  |  |  |  | 0.28032 | 23.5472 | 0.95805 | 0.96872 |  |  |  |  | 238 | 0.011277
39960 | TNTNPONE_18 | 1 | North | YES | 0.091914 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.27185 | 0 | 152.3 | 13.9985 | 152.3 |  |  | 0.27185 | 41.4029 | 0.96168 | 0.97186 |  |  |  |  | 239 | 0.011081
39970 | TNTNPONE_28 | 1 | North | YES | 0.091914 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.27185 | 0 | 153 | 14.0628 | 153 |  |  | 0.27185 | 41.5931 | 0.96532 | 0.97501 |  |  |  |  | 240 | 0.010887
60202 | FRNDDRCS | F | West | YES | 0.080216 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.26015 | 0 | 0 |  |  |  |  | 0.26015 | 0 | 0.96532 | 0.97501 |  |  |  |  | 241 | 0.010672
990 | GIBN_CREK_G1 | 1 | North | YES | 0.054087 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.23402 | 0 | 463 | 25.0423 | 463 |  |  | 0.23402 | 108.3529 | 0.97634 | 0.98323 |  |  |  |  | 242 | 0.010185
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.043803 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.22374 | 32 | 32 | 1.4017 | 32 |  |  | 0.22374 | 7.1597 | 0.9771 | 0.98377 |  |  |  |  | 243 | 0.0096959
48671 | FTR_GT1_5105 | 1 | North | YES | 0.043221 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.22316 | 154.2 | 154.2 | 6.6647 | 154.2 |  |  | 0.22316 | 34.4109 | 0.98077 | 0.98638 |  |  |  |  | 244 | 0.0096959
48672 | FTR_GT2_5110 | 2 | North | YES | 0.043221 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.22316 | 159 | 159 | 6.8721 | 159 |  |  | 0.22316 | 35.4821 | 0.98455 | 0.98907 |  |  |  |  | 245 | 0.0068881
48673 | FTR_GT3_5085 | 3 | North | YES | 0.043221 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.22316 | 158 | 158 | 6.8289 | 158 |  |  | 0.22316 | 35.2589 | 0.98831 | 0.99174 |  |  |  |  | 246 | 0.0066691
48674 | FTR_CN4_5095 | 4 | North | YES | 0.043221 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.22316 | 380 | 380 | 16.424 | 380 |  |  | 0.22316 | 84.7999 | 0.99736 | 0.99816 |  |  |  |  | 247 | 0.0056071
32886 | BRYN_ATKINS3 | MB | North | YES | 0.042125 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 | 0.99736 | 0.99816 |  |  |  |  | 248 | 0.0045119
32887 | BRYN_ATKINS6 | MB | North | YES | 0.042125 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 | 0.99736 | 0.99816 |  |  |  |  | 249 | 0.0034236
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.042125 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.22206 | 17 | 17 | 0.71613 | 17 |  |  | 0.22206 | 3.775 | 0.99776 | 0.99845 |  |  |  |  | 250 | 0.00080629
32890 | BRYN_ATKINS4 | MB | North | YES | 0.042125 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 | 0.99776 | 0.99845 |  |  |  |  | 251 | 0.00080629
32891 | BRYN_ATKINS5 | MB | North | YES | 0.042125 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 | 0.99776 | 0.99845 |  |  |  |  | 252 | 0.00080629
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.037558 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.21749 | 48 | 48 | 1.8028 | 48 |  |  | 0.21749 | 10.4397 | 0.99891 | 0.99924 |  |  |  |  | 253 | 0.00068779
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.037558 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.21749 | 46 | 46 | 1.7277 | 46 |  |  | 0.21749 | 10.0048 | 1 | 1 |  |  |  |  | 254 | 0.00068779
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.037558 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.21749 | 105 | 105 | 3.9436 | 105 |  |  | 0.21749 | 22.8369 | 1.0025 | 1.0017 |  |  |  |  | 255 | 0.00068779
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.13903 | 15 | 15 |  |  | 0 | 15 | -0.13903 | -2.0854 | [6 empty] | 256 | 0.00033658
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | [6 empty] | 257 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | [6 empty] | 258 | -0.00076828
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | [6 empty] | 259 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | [6 empty] | 260 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | [6 empty] | 261 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | [6 empty] | 262 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | [6 empty] | 263 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | [6 empty] | 264 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.13903 | 0 | 0 |  |  |  |  | -0.13903 | 0 | [6 empty] | 265 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.014605 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | [6 empty] | 266 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.014605 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | [6 empty] | 267 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.014605 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | [6 empty] | 268 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.014605 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | [6 empty] | 269 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.014605 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | [6 empty] | 270 | 0
48885 | THW_5152 | B | Houston | YES | -0.020999 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16003 | 59 | 59 |  |  |  |  | -0.16003 | -9.4416 | [6 empty] | 271 | 0
48885 | THW_5152 | A | Houston | YES | -0.020999 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16003 | 58 | 58 |  |  |  |  | -0.16003 | -9.2816 | [6 empty] | 272 | 0
48886 | THW_5354 | D | Houston | YES | -0.020999 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16003 | 58 | 58 |  |  |  |  | -0.16003 | -9.2816 | [6 empty] | 273 | 0
48886 | THW_5354 | C | Houston | YES | -0.020999 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16003 | 57 | 57 |  |  |  |  | -0.16003 | -9.1215 | [6 empty] | 274 | 0
48887 | THW_5556 | E | Houston | YES | -0.020999 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16003 | 59 | 59 |  |  |  |  | -0.16003 | -9.4416 | [6 empty] | 275 | 0
48887 | THW_5556 | F | Houston | YES | -0.020999 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16003 | 57 | 57 |  |  |  |  | -0.16003 | -9.1215 | [6 empty] | 276 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.021457 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.16048 | 398 | 398 |  |  |  |  | -0.16048 | -63.8729 | [6 empty] | 277 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.021791 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.16082 | 162.8 | 162.8 |  |  |  |  | -0.16082 | -26.1813 | [6 empty] | 278 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.021791 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.16082 | 161.4 | 161.4 |  |  |  |  | -0.16082 | -25.9561 | [6 empty] | 279 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.021791 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.16082 | 158.9 | 158.9 |  |  |  |  | -0.16082 | -25.5541 | [6 empty] | 280 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.021791 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.16082 | 269.2 | 269.2 |  |  |  |  | -0.16082 | -43.2924 | [6 empty] | 281 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 | [6 empty] | 282 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 | [6 empty] | 283 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 | [6 empty] | 284 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.02302 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.16205 | 0 | 0 |  |  |  |  | -0.16205 | 0 | [6 empty] | 285 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.023354 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | [6 empty] | 286 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.023354 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | [6 empty] | 287 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.023354 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | [6 empty] | 288 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.023354 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | [6 empty] | 289 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.023354 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | [6 empty] | 290 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.023354 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | [6 empty] | 291 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.023354 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | [6 empty] | 292 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.023373 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.1624 | 744 | 744 |  |  |  |  | -0.1624 | -120.8262 | [6 empty] | 293 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.023395 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.16242 | 0 | 0 |  |  |  |  | -0.16242 | 0 | [6 empty] | 294 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.023414 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.16244 | 0 | 0 |  |  |  |  | -0.16244 | 0 | [6 empty] | 295 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.023414 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.16244 | 0 | 0 |  |  |  |  | -0.16244 | 0 | [6 empty] | 296 | 0
49803 | EXN_15GT | 1 | Houston | YES | -0.024016 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 297 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.024016 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 298 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.024016 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 299 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.024016 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 300 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.024016 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 301 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.024016 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 302 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.024016 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 303 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.024016 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 304 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.024016 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 305 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.024016 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 306 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.024016 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | [6 empty] | 307 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.024179 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.16321 | 12 | 12 |  |  |  |  | -0.16321 | -1.9585 | [6 empty] | 308 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.024639 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.16367 | 746 | 746 |  |  |  |  | -0.16367 | -122.0954 | [6 empty] | 309 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.025572 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.1646 | 107 | 107 |  |  |  |  | -0.1646 | -17.6122 | [6 empty] | 310 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.025572 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.1646 | 108 | 108 |  |  |  |  | -0.1646 | -17.7768 | [6 empty] | 311 | 0
48875 | THW_3132 | A | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 | [6 empty] | 312 | 0
48875 | THW_3132 | B | Houston | YES | -0.025572 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.1646 | 53 | 53 |  |  |  |  | -0.1646 | -8.7238 | [6 empty] | 313 | 0
48877 | THW_3334 | C | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 | [6 empty] | 314 | 0
48877 | THW_3334 | D | Houston | YES | -0.025572 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.1646 | 57 | 57 |  |  |  |  | -0.1646 | -9.3822 | [6 empty] | 315 | 0
48879 | THW_4142 | E | Houston | YES | -0.025572 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.1646 | 56 | 56 |  |  |  |  | -0.1646 | -9.2176 | [6 empty] | 316 | 0
48879 | THW_4142 | F | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 | [6 empty] | 317 | 0
48881 | THW_4344 | G | Houston | YES | -0.025572 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.1646 | 58 | 58 |  |  |  |  | -0.1646 | -9.5468 | [6 empty] | 318 | 0
48881 | THW_4344 | H | Houston | YES | -0.025572 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.1646 | 58 | 58 |  |  |  |  | -0.1646 | -9.5468 | [6 empty] | 319 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.026716 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.16574 | 0 | 0 |  |  |  |  | -0.16574 | 0 | [6 empty] | 320 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.026716 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.16574 | 0 | 0 |  |  |  |  | -0.16574 | 0 | [6 empty] | 321 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.026832 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.16586 | 42 | 42 |  |  |  |  | -0.16586 | -6.9661 | [6 empty] | 322 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.026832 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.16586 | 42 | 42 |  |  |  |  | -0.16586 | -6.9661 | [6 empty] | 323 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.026832 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.16586 | 39 | 39 |  |  |  |  | -0.16586 | -6.4685 | [6 empty] | 324 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.026832 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.16586 | 39 | 39 |  |  |  |  | -0.16586 | -6.4685 | [6 empty] | 325 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.027012 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.16604 | 0 | 0 |  |  |  |  | -0.16604 | 0 | [6 empty] | 326 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.027787 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 | [6 empty] | 327 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.027787 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 | [6 empty] | 328 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.027787 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 | [6 empty] | 329 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.027787 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 | [6 empty] | 330 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.028348 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 | [6 empty] | 331 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.028348 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 | [6 empty] | 332 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.028348 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 | [6 empty] | 333 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.028349 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.16738 | 228 | 228 |  |  |  |  | -0.16738 | -38.1619 | [6 empty] | 334 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.02836 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 | [6 empty] | 335 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.02836 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 | [6 empty] | 336 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.02836 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 | [6 empty] | 337 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.02836 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 | [6 empty] | 338 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.028365 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.16739 | 16.2 | 16.2 |  |  |  |  | -0.16739 | -2.7118 | [6 empty] | 339 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.028372 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.1674 | 213 | 213 |  |  |  |  | -0.1674 | -35.6561 | [6 empty] | 340 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.028468 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.1675 | 0 | 0 |  |  |  |  | -0.1675 | 0 | [6 empty] | 341 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.028468 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.1675 | 0 | 0 |  |  |  |  | -0.1675 | 0 | [6 empty] | 342 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.028478 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.16751 | 165 | 165 |  |  |  |  | -0.16751 | -27.6384 | [6 empty] | 343 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.028508 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.16754 | 176 | 176 |  |  |  |  | -0.16754 | -29.4863 | [6 empty] | 344 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.02853 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.16756 | 18 | 18 |  |  |  |  | -0.16756 | -3.016 | [6 empty] | 345 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | -0.02853 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.16756 | 12 | 12 |  |  |  |  | -0.16756 | -2.0107 | [6 empty] | 346 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.028932 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.16796 | 0 | 0 |  |  |  |  | -0.16796 | 0 | [6 empty] | 347 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.029327 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.16835 | 163.2 | 163.2 |  |  |  |  | -0.16835 | -27.4755 | [6 empty] | 348 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.029327 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.16835 | 157.1 | 157.1 |  |  |  |  | -0.16835 | -26.4485 | [6 empty] | 349 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.029327 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.16835 | 157.5 | 157.5 |  |  |  |  | -0.16835 | -26.5159 | [6 empty] | 350 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.029327 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.16835 | 157 | 157 |  |  |  |  | -0.16835 | -26.4317 | [6 empty] | 351 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.029327 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.16835 | 282 | 282 |  |  |  |  | -0.16835 | -47.476 | [6 empty] | 352 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.029744 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.16877 | 0 | 0 |  |  |  |  | -0.16877 | 0 | [6 empty] | 353 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.029744 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.16877 | 0 | 0 |  |  |  |  | -0.16877 | 0 | [6 empty] | 354 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 | [6 empty] | 355 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 | [6 empty] | 356 | 0
48692 | GBY_81821075 | D | Houston | YES | -0.03027 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.1693 | 55 | 55 |  |  |  |  | -0.1693 | -9.3114 | [6 empty] | 357 | 0
48692 | GBY_81821075 | C | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 | [6 empty] | 358 | 0
48693 | GBY_83841065 | F | Houston | YES | -0.03027 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.1693 | 54 | 54 |  |  |  |  | -0.1693 | -9.1421 | [6 empty] | 359 | 0
48693 | GBY_83841065 | E | Houston | YES | -0.03027 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.1693 | 57 | 57 |  |  |  |  | -0.1693 | -9.65 | [6 empty] | 360 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.031354 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 | [6 empty] | 361 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.031354 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 | [6 empty] | 362 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.031354 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 | [6 empty] | 363 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.031354 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 | [6 empty] | 364 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.032212 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | [6 empty] | 365 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.032212 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | [6 empty] | 366 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.032212 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | [6 empty] | 367 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.032212 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | [6 empty] | 368 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.032212 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | [6 empty] | 369 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.034448 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.17348 | 0 | 0 |  |  |  |  | -0.17348 | 0 | [6 empty] | 370 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.037654 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 371 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.037654 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 372 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.037654 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 373 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.037654 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 374 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.037654 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 375 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.037654 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 376 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.037654 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 377 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.037654 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 378 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.037654 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 379 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.037654 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 380 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.037654 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 381 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.037654 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 382 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.037654 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 383 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.037654 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 384 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.037654 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | [6 empty] | 385 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.045218 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.18425 | 166 | 166 |  |  |  |  | -0.18425 | -30.5848 | [6 empty] | 386 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.045218 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.18425 | 166 | 166 |  |  |  |  | -0.18425 | -30.5848 | [6 empty] | 387 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.045218 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.18425 | 248 | 248 |  |  |  |  | -0.18425 | -45.6929 | [6 empty] | 388 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.045218 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.18425 | 546 | 546 |  |  |  |  | -0.18425 | -100.5982 | [6 empty] | 389 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.045218 | 584.4 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.18425 | 0 | 654 |  |  |  |  | -0.18425 | 0 | [6 empty] | 390 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.045218 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.18425 | 13 | 13 |  |  |  |  | -0.18425 | -2.3952
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.045432 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.18446 | 0 | 0 |  |  |  |  | -0.18446 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.04705 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.18608 | 167.7 | 167.7 |  |  |  |  | -0.18608 | -31.2052
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.04705 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.18608 | 166.4 | 166.4 |  |  |  |  | -0.18608 | -30.9633
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.04705 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.18608 | 252.4 | 252.4 |  |  |  |  | -0.18608 | -46.966
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.047147 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 651 |  |  |  |  | -0.18617 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.047147 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 564 |  |  |  |  | -0.18617 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.047147 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 603 |  |  |  |  | -0.18617 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.047181 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.18621 | 0 | 0 |  |  |  |  | -0.18621 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.0588 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.0588 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.0588 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.0588 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.062036 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.20106 | 0 | 0 |  |  |  |  | -0.20106 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.062036 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.20106 | 0 | 0 |  |  |  |  | -0.20106 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.066124 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.066124 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.066124 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.066124 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.066124 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.066124 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.066124 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.066124 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.066124 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.066124 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.066124 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.066124 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.066124 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.066124 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.066124 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.066124 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.066124 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.066124 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.066124 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.066124 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.075631 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.075631 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0
88253 | HAMILTON | F | South | YES | -0.075631 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.082186 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.22121 | 0 | 0 |  |  |  |  | -0.22121 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153
48732 | CBE_GT2 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153
48733 | CBE_ST12 | 1 | Houston | YES | -0.087489 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22652 | 105 | 105 |  |  |  |  | -0.22652 | -23.7843
48734 | CBE_GT3 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153
48735 | CBE_GT4 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153
48736 | CBE_ST34 | 1 | Houston | YES | -0.087489 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22652 | 105 | 105 |  |  |  |  | -0.22652 | -23.7843
5911 | STP_GN1___1 | 1 | Houston | YES | -0.088308 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.22734 | 0 | 0 |  |  |  |  | -0.22734 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.088308 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.22734 | 0 | 0 |  |  |  |  | -0.22734 | 0
8262 | ELPS | 1 | South | YES | -0.098206 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.23723 | 0 | 0 |  |  | 0 | 0 | -0.23723 | 0
8134 | FOR #1 | 1 | South | YES | -0.13032 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
8138 | FOR #2 | 2 | South | YES | -0.13032 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
8153 | FOR #3 | 3 | South | YES | -0.13032 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
8154 | FOR #4 | 4 | South | YES | -0.13032 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
8155 | FOR #5 | 5 | South | YES | -0.13032 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
8156 | FOR #6 | 6 | South | YES | -0.13032 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
8157 | FOR #7 | 7 | South | YES | -0.13032 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
80051 | FOR #8 | 8 | South | YES | -0.13032 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
80052 | FOR #9 | 9 | South | YES | -0.13032 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
80053 | FOR #10 | 10 | South | YES | -0.13032 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0
80226 | ALCOA G | 1 | South | YES | -0.13149 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.27052 | 0 | 0 |  |  | 0 | 0 | -0.27052 | 0
8147 | UCAR #2 | 10 | South | YES | -0.13528 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0
8148 | UCAR #1 | 2 | South | YES | -0.13528 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0
80137 | CSDR89 | 9 | South | YES | -0.13528 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0
80137 | CSDR89 | 8 | South | YES | -0.13528 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0
80138 | CSDR7 | 7 | South | YES | -0.13528 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0
80139 | CSDR56 | 6 | South | YES | -0.13528 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0
80139 | CSDR56 | 5 | South | YES | -0.13528 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0
80140 | CSDR11 | 11 | South | YES | -0.13528 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0
80227 | AIRCO G | 1 | South | YES | -0.13582 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.27484 | 0 | 0 |  |  | 0 | 0 | -0.27484 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.13688 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.13688 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.13824 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.27727 | 22 | 22 |  |  | -3.0412 | 22 | -0.27727 | -6.0998
5505 | RAYBURNGEN1 | 1 | South | YES | -0.13824 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27727 | 11 | 11 |  |  | -1.5206 | 11 | -0.27727 | -3.0499
5506 | RAYBURNGEN2 | 1 | South | YES | -0.13824 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27727 | 11 | 11 |  |  | -1.5206 | 11 | -0.27727 | -3.0499
5508 | RAYBURNCC9 | 1 | South | YES | -0.13957 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.2786 | 47.7 | 47.7 |  |  | -6.6575 | 47.7 | -0.2786 | -13.2891
5509 | RAYBURNCC10 | 1 | South | YES | -0.13957 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.2786 | 37.3 | 37.3 |  |  | -5.206 | 37.3 | -0.2786 | -10.3917
5511 | RAYBURNCC7 | 1 | South | YES | -0.13957 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.2786 | 47.5 | 47.5 |  |  | -6.6296 | 47.5 | -0.2786 | -13.2334
5512 | RAYBURNCC8 | 1 | South | YES | -0.13957 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.2786 | 49.3 | 49.3 |  |  | -6.8808 | 49.3 | -0.2786 | -13.7349
8066 | DUP1V#1 | 1 | South | YES | -0.13974 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.27877 | 0 | 0 |  |  | 0 | 0 | -0.27877 | 0
80265 | LARECU40A | 4 | South | YES | -0.13989 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27892 | 100 | 100 |  |  | -13.9893 | 100 | -0.27892 | -27.8921
80266 | LARECU50A | 5 | South | YES | -0.13989 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27892 | 100 | 100 |  |  | -13.9893 | 100 | -0.27892 | -27.8921
80012 | LAR | F | South | YES | -0.13989 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.27892 | 0 | 0 |  |  | 0 | 0 | -0.27892 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.13998 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.13998 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.13998 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0
8930 | ICPGN10A | 1 | South | YES | -0.13998 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0
8931 | ICPGN20A | 2 | South | YES | -0.13998 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0
8932 | ICPGN30A | 3 | South | YES | -0.13998 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0
80223 | REYSHR G | 1 | South | YES | -0.13998 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0
88299 | ZAPATA | F | South | YES | -0.14093 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.27995 | 0 | 0 |  |  | 0 | 0 | -0.27995 | 0
8442 | NBEC7 | 7 | South | YES | -0.14135 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.28037 | 367 | 367 |  |  | -51.8743 | 367 | -0.28037 | -102.8975
8442 | NBEC7 | MB | South | YES | -0.14135 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.28037 | 0 | 0 |  |  | 0 | 0 | -0.28037 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.14136 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.14136 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0
8562 | CNOPST1 | 3 | South | YES | -0.14136 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0
8173 | VICEC51A | 5 | South | YES | -0.14137 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.28039 | 144 | 144 |  |  | -20.3568 | 144 | -0.28039 | -40.3768
8174 | VICEC61A | 6 | South | YES | -0.14137 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.28039 | 188 | 188 |  |  | -26.577 | 188 | -0.28039 | -52.7142
8456 | COSW#1 | 1 | South | YES | -0.14144 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.28047 | 0 | 0 |  |  | 0 | 0 | -0.28047 | 0
8457 | COSW#2 | 2 | South | YES | -0.14144 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.28047 | 0 | 0 |  |  | 0 | 0 | -0.28047 | 0
88508 | FALFURRI | F | South | YES | -0.1416 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.28063 | 0 | 0 |  |  | 0 | 0 | -0.28063 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.14163 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.14163 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.14163 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.14163 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.28066 | 0 | 0 |  |  | 0 | 0 | -0.28066 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.14163 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.28066 | 0 | 0 |  |  | 0 | 0 | -0.28066 | 0
80263 | B_DAVIS31A | 3 | South | YES | -0.14163 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.28066 | 180 | 180 |  |  | -25.493 | 180 | -0.28066 | -50.518
80264 | B_DAVIS41A | 4 | South | YES | -0.14163 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.28066 | 180 | 180 |  |  | -25.493 | 180 | -0.28066 | -50.518
8506 | VAL #1 | 1 | South | YES | -0.1417 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.28073 | 0 | 0 |  |  | 0 | 0 | -0.28073 | 0
8507 | VAL #2 | 2 | South | YES | -0.1417 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.28073 | 0 | 0 |  |  | 0 | 0 | -0.28073 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.14185 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.28087 | 0 | 0 |  |  | 0 | 0 | -0.28087 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.14185 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.28087 | 0 | 0 |  |  | 0 | 0 | -0.28087 | 0
8933 | FGNTS001 | 1 | South | YES | -0.14236 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.28138 | 146.5 | 146.5 |  |  | -20.8552 | 146.5 | -0.28138 | -41.2227
8934 | FGNTS101 | 2 | South | YES | -0.14236 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.28138 | 147.9 | 147.9 |  |  | -21.0545 | 147.9 | -0.28138 | -41.6167
8935 | FGNTS201 | 3 | South | YES | -0.14236 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.28138 | 173 | 173 |  |  | -24.6276 | 173 | -0.28138 | -48.6794
8517 | CELANEBI0A | 1 | South | YES | -0.14239 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.28141 | 0 | 0 |  |  | 0 | 0 | -0.28141 | 0
8936 | MVGN#1 | 1 | South | YES | -0.14248 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.28151 | 216.6 | 216.6 |  |  | -30.8612 | 216.6 | -0.28151 | -60.9746
8937 | MVGN#2 | 2 | South | YES | -0.14248 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.28151 | 216.7 | 216.7 |  |  | -30.8754 | 216.7 | -0.28151 | -61.0027
8938 | MVGN#3 | 3 | South | YES | -0.14248 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.28151 | 250.9 | 250.9 |  |  | -35.7482 | 250.9 | -0.28151 | -70.6303
8981 | HECN1 | 1 | South | YES | -0.14248 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.28151 | 144.8 | 144.8 |  |  | -20.6311 | 144.8 | -0.28151 | -40.7623
8982 | HECN2 | 2 | South | YES | -0.14248 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.28151 | 144.1 | 144.1 |  |  | -20.5314 | 144.1 | -0.28151 | -40.5653
8983 | HECN3 | 3 | South | YES | -0.14248 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.28151 | 171.9 | 171.9 |  |  | -24.4923 | 171.9 | -0.28151 | -48.3912
5932 | SI_RAY9 | 9 | South | YES | -0.14252 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.28155 | 38 | 38 |  |  | -5.4157 | 38 | -0.28155 | -10.6988
5933 | SI_RAY6 | 6 | South | YES | -0.14252 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.28155 | 19.3 | 19.3 |  |  | -2.7506 | 19.3 | -0.28155 | -5.4339
5935 | SI_RAY10 | 10 | South | YES | -0.14252 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.28155 | 47 | 47 |  |  | -6.6984 | 47 | -0.28155 | -13.2327
80003 | MILHWYS | F | South | YES | -0.14252 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.28155 | 0 | 0 |  |  | 0 | 0 | -0.28155 | 0
80080 | GWINDT11A | 3 | South | YES | -0.14255 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 38 |  |  | 0 | 0 | -0.28157 | 0
80080 | GWINDT11A | 4 | South | YES | -0.14255 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 19 |  |  | 0 | 0 | -0.28157 | 0
80080 | GWINDT11A | 2 | South | YES | -0.14255 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 41 |  |  | 0 | 0 | -0.28157 | 0
80080 | GWINDT11A | 1 | South | YES | -0.14255 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 94 |  |  | 0 | 0 | -0.28157 | 0
80081 | GWINDT21A | 4 | South | YES | -0.14255 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 22 |  |  | 0 | 0 | -0.28157 | 0
80081 | GWINDT21A | 1 | South | YES | -0.14255 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 94 |  |  | 0 | 0 | -0.28157 | 0
80081 | GWINDT21A | 3 | South | YES | -0.14255 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 43 |  |  | 0 | 0 | -0.28157 | 0
80081 | GWINDT21A | 2 | South | YES | -0.14255 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 36 |  |  | 0 | 0 | -0.28157 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.14255 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 50 |  |  | 0 | 0 | -0.28157 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.14255 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 148 |  |  | 0 | 0 | -0.28157 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.14255 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 50 |  |  | 0 | 0 | -0.28157 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.14255 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 55 |  |  | 0 | 0 | -0.28157 | 0
8161 | COLETO0A | 1 | South | YES | -0.14836 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.28739 | 0 | 633 |  |  | 0 | 0 | -0.28739 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58909 | PEARSALLSCG1 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58909 | PEARSALLSCG1 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58909 | PEARSALLSCG1 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58909 | PEARSALLSCG1 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58909 | PEARSALLSCG1 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58919 | PEARSALLSCG2 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58919 | PEARSALLSCG2 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58919 | PEARSALLSCG2 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58919 | PEARSALLSCG2 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58919 | PEARSALLSCG2 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58919 | PEARSALLSCG2 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58929 | PEARSALLSCG3 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58929 | PEARSALLSCG3 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58929 | PEARSALLSCG3 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58929 | PEARSALLSCG3 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58929 | PEARSALLSCG3 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58929 | PEARSALLSCG3 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58949 | PEARSALLSCG4 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58949 | PEARSALLSCG4 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58949 | PEARSALLSCG4 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58949 | PEARSALLSCG4 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58949 | PEARSALLSCG4 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
58949 | PEARSALLSCG4 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275
88198 | BEEVILLE | F | South | YES | -0.15001 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.28904 | 0 | 0 |  |  | 0 | 0 | -0.28904 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.15295 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.29198 | 24 | 24 |  |  | -3.6708 | 24 | -0.29198 | -7.0075
5891 | PEARSALLGEN2 | 1 | South | YES | -0.15295 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.29198 | 24.3 | 24.3 |  |  | -3.7167 | 24.3 | -0.29198 | -7.0951
5892 | PEARSALLGEN3 | 1 | South | YES | -0.15295 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.29198 | 23.9 | 23.9 |  |  | -3.6555 | 23.9 | -0.29198 | -6.9783
5903 | SANMIGUELGEN | 1 | South | YES | -0.16363 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.30266 | 0 | 396.3 |  |  | 0 | 0 | -0.30266 | 0
8189 | CUECPL2A | 1 | South | YES | -0.17052 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.30955 | 0 | 0 |  |  | 0 | 0 | -0.30955 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.17172 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.31075 | 0 | 562 |  |  | 0 | 0 | -0.31075 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.17241 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.31143 | 58 | 58 |  |  | -9.9995 | 58 | -0.31143 | -18.0631
5265 | LEON_LCP4G4 | 4 | South | YES | -0.17241 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.31143 | 89 | 89 |  |  | -15.344 | 89 | -0.31143 | -27.7175
5266 | LEON_LCPCT1 | 1 | South | YES | -0.17241 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.31143 | 44 | 44 |  |  | -7.5858 | 44 | -0.31143 | -13.703
5267 | LEON_LCPCT2 | 2 | South | YES | -0.17241 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.31143 | 44 | 44 |  |  | -7.5858 | 44 | -0.31143 | -13.703
5268 | LEON_LCPCT3 | 3 | South | YES | -0.17241 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.31143 | 43 | 43 |  |  | -7.4134 | 43 | -0.31143 | -13.3916
5269 | LEON_LCPCT4 | 4 | South | YES | -0.17241 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.31143 | 45 | 45 |  |  | -7.7582 | 45 | -0.31143 | -14.0145
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.17279 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.31182 | 155 | 155 |  |  | -26.7826 | 155 | -0.31182 | -48.3319
5477 | BRA_AVR1_ST | 1 | South | YES | -0.17279 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.31182 | 174 | 174 |  |  | -30.0656 | 174 | -0.31182 | -54.2565
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.17279 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.31182 | 155 | 155 |  |  | -26.7826 | 155 | -0.31182 | -48.3319
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.17355 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.31258 | 407 | 407 |  |  | -70.6349 | 407 | -0.31258 | -127.2191
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.17363 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.31266 | 215 | 215 |  |  | -37.3313 | 215 | -0.31266 | -67.2223
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.17363 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.31266 | 216 | 216 |  |  | -37.5049 | 216 | -0.31266 | -67.5349
5396 | CALAVER_OWS1 | 1 | South | YES | -0.17386 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.31289 | 418 | 418 |  |  | -72.6756 | 418 | -0.31289 | -130.7892
5397 | CALAVER_OWS2 | 2 | South | YES | -0.17386 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.31289 | 400 | 400 |  |  | -69.546 | 400 | -0.31289 | -125.1571
5111 | CALAVER_JTD1 | 1 | South | YES | -0.17406 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.31308 | 0 | 430 |  |  | 0 | 0 | -0.31308 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.17406 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.31308 | 0 | 430 |  |  | 0 | 0 | -0.31308 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.17474 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.31377 | 61 | 61 |  |  | -10.6591 | 61 | -0.31377 | -19.1398
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.17474 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.31377 | 95 | 95 |  |  | -16.6002 | 95 | -0.31377 | -29.8078
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.17474 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.31377 | 151 | 151 |  |  | -26.3856 | 151 | -0.31377 | -47.3788
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.1791 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.31813 | 147 | 147 |  |  | -26.328 | 147 | -0.31813 | -46.7651
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.1791 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.31813 | 138 | 138 |  |  | -24.7161 | 138 | -0.31813 | -43.9019
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.1791 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.31813 | 146 | 146 |  |  | -26.1489 | 146 | -0.31813 | -46.4469
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.1791 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.31813 | 149 | 149 |  |  | -26.6862 | 149 | -0.31813 | -47.4013
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.1791 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.31813 | 182 | 182 |  |  | -32.5966 | 182 | -0.31813 | -57.8996
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.1791 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.31813 | 203 | 203 |  |  | -36.3577 | 203 | -0.31813 | -64.5803
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.18179 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.32082 | 0 | 0 |  |  | 0 | 0 | -0.32082 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.18179 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.32082 | 0 | 0 |  |  | 0 | 0 | -0.32082 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.18316 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.32219 | 0 | 0 |  |  | 0 | 0 | -0.32219 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.18349 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.32252 | 0 | 0 |  |  | 0 | 0 | -0.32252 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.18533 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.18533 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.18533 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.18586 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.32488 | 148 | 148 |  |  | -27.5068 | 148 | -0.32488 | -48.0829
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.18586 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.32488 | 148 | 148 |  |  | -27.5068 | 148 | -0.32488 | -48.0829
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.18586 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.32488 | 154 | 154 |  |  | -28.622 | 154 | -0.32488 | -50.0323
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.18586 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.32488 | 293 | 293 |  |  | -54.4561 | 293 | -0.32488 | -95.1912
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.19059 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.32961 | 423.3 | 423.3 |  |  | -80.6746 | 423.3 | -0.32961 | -139.5251
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.19059 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.19059 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.19059 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.19212 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.33115 | 0 | 0 |  |  | 0 | 0 | -0.33115 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.19212 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.33115 | 0 | 0 |  |  | 0 | 0 | -0.33115 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.19304 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.33207 | 223.9 | 223.9 |  |  | -43.2214 | 223.9 | -0.33207 | -74.3497
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.19304 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.33207 | 225 | 225 |  |  | -43.4338 | 225 | -0.33207 | -74.715
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.19304 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.33207 | 224.6 | 224.6 |  |  | -43.3566 | 224.6 | -0.33207 | -74.5822
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.19304 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.33207 | 226.7 | 226.7 |  |  | -43.7619 | 226.7 | -0.33207 | -75.2795
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.1952 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.33422 | 0 | 0 |  |  | 0 | 0 | -0.33422 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.1978 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.33683 | 0 | 0 |  |  | 0 | 0 | -0.33683 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.1978 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.33683 | 0 | 0 |  |  | 0 | 0 | -0.33683 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.19837 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.3374 | 0 | 436 |  |  | 0 | 0 | -0.3374 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.19858 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.3376 | 0 | 606 |  |  | 0 | 0 | -0.3376 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.19858 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.3376 | 0 | 598 |  |  | 0 | 0 | -0.3376 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.21272 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.21272 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.21272 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.21458 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.3536 | 132 | 132 |  |  | -28.324 | 132 | -0.3536 | -46.6757
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.21458 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.3536 | 139 | 139 |  |  | -29.8261 | 139 | -0.3536 | -49.1509
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.21458 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.3536 | 329 | 329 |  |  | -70.5955 | 329 | -0.3536 | -116.3356
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.2208 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.35983 | 0 | 0 |  |  | 0 | 0 | -0.35983 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.2208 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.35983 | 0 | 0 |  |  | 0 | 0 | -0.35983 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.22125 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.36028 | 49 | 49 |  |  | -10.8412 | 49 | -0.36028 | -17.6535
9017 | SANDH_G2 | 2 | South | YES | -0.22125 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.36028 | 46 | 46 |  |  | -10.1774 | 46 | -0.36028 | -16.5727
9018 | SANDH_G3 | 3 | South | YES | -0.22125 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.36028 | 46 | 46 |  |  | -10.1774 | 46 | -0.36028 | -16.5727
9019 | SANDH_G4 | 4 | South | YES | -0.22125 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.36028 | 47 | 47 |  |  | -10.3987 | 47 | -0.36028 | -16.933
9020 | SANDHG5A | 5A | South | YES | -0.22125 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.36028 | 155 | 155 |  |  | -34.2934 | 155 | -0.36028 | -55.8427
9021 | SANDHG5C | 5C | South | YES | -0.22125 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.36028 | 148 | 148 |  |  | -32.7447 | 148 | -0.36028 | -53.3208
9000 | DECKR_G1 | 1 | South | YES | -0.22261 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.36164 | 321 | 321 |  |  | -71.4585 | 321 | -0.36164 | -116.0864
9001 | DECKR_G2 | 2 | South | YES | -0.22261 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.36164 | 426 | 426 |  |  | -94.8327 | 426 | -0.36164 | -154.0585
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.22486 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.36388 | 158 | 158 |  |  | -35.5274 | 158 | -0.36388 | -57.4938
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.22486 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.36388 | 160 | 160 |  |  | -35.9771 | 160 | -0.36388 | -58.2216
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.22486 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.36388 | 175 | 175 |  |  | -39.35 | 175 | -0.36388 | -63.6798
9002 | DECKR_G3 | 3 | South | YES | -0.22493 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.36396 | 42 | 42 |  |  | -9.4472 | 42 | -0.36396 | -15.2864
9003 | DECKR_G4 | 4 | South | YES | -0.22493 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.36396 | 44 | 44 |  |  | -9.8971 | 44 | -0.36396 | -16.0143
9004 | DECKR_G5 | 5 | South | YES | -0.22493 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.36396 | 44 | 44 |  |  | -9.8971 | 44 | -0.36396 | -16.0143
9005 | DECKR_G6 | 6 | South | YES | -0.22493 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.36396 | 47 | 47 |  |  | -10.5719 | 47 | -0.36396 | -17.1062
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.22552 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.36454 | 152.5 | 152.5 |  |  | -34.3912 | 152.5 | -0.36454 | -55.5929
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.22552 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.36454 | 149.5 | 149.5 |  |  | -33.7146 | 149.5 | -0.36454 | -54.4993
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.22552 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.36454 | 232.6 | 232.6 |  |  | -52.455 | 232.6 | -0.36454 | -84.7929
13432 | SANDOW_5G | 5 | South | YES | -0.27156 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.41058 | 0 | 581 |  |  | 0 | 0 | -0.41058 | 0
3432 | SANDOW_4G | 4 | South | YES | -0.28152 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.42055 | 0 | 580 |  |  | 0 | 0 | -0.42055 | 0
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ Tradinghouse to TemplePEC OL_ TempleSS to LakeCreek |  | i_PTDF_INC_pt | 387 |  | RAYBURNGEN2 | Unit at max
3432 | SANDOW_4G | 4 | South | YES | -0.28152 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.42055 | 0 | 580 |  |  | 0 | 0 | -0.42055 | 0 | 0 | 0 |  |  | i_10pctunit | 18 |  | 182 | # units @ max
13432 | SANDOW_5G | 5 | South | YES | -0.27156 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.41058 | 0 | 581 |  |  | 0 | 0 | -0.41058 | 0 | 0 | 0 | [5 empty] | 0.13728 | delta max
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.22552 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.36454 | 152.5 | 152.5 |  |  | -34.3912 | 152.5 | -0.36454 | -55.5929 | 0.0072049 | 0.010139 | [5 empty] | Delta
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.22552 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.36454 | 149.5 | 149.5 |  |  | -33.7146 | 149.5 | -0.36454 | -54.4993 | 0.014268 | 0.020078 | Weighted Shift Factors |  |  |  | 1 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.22552 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.36454 | 232.6 | 232.6 |  |  | -52.455 | 232.6 | -0.36454 | -84.7929 | 0.025257 | 0.035542 | North | 0.13903 |  |  | 2 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.22493 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.36396 | 42 | 42 |  |  | -9.4472 | 42 | -0.36396 | -15.2864 | 0.027242 | 0.03833 | South | -0.17994 |  |  | 3 | 0.0029338
9003 | DECKR_G4 | 4 | South | YES | -0.22493 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.36396 | 44 | 44 |  |  | -9.8971 | 44 | -0.36396 | -16.0143 | 0.02932 | 0.04125 |  |  |  |  | 4 | 0.0058099
9004 | DECKR_G5 | 5 | South | YES | -0.22493 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.36396 | 44 | 44 |  |  | -9.8971 | 44 | -0.36396 | -16.0143 | 0.031399 | 0.044171 |  |  |  |  | 5 | 0.010285
9005 | DECKR_G6 | 6 | South | YES | -0.22493 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.36396 | 47 | 47 |  |  | -10.5719 | 47 | -0.36396 | -17.1062 | 0.03362 | 0.047291 |  |  |  |  | 6 | 0.011088
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.22486 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.36388 | 158 | 158 |  |  | -35.5274 | 158 | -0.36388 | -57.4938 | 0.041084 | 0.057776 |  |  |  |  | 7 | 0.01193
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.22486 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.36388 | 160 | 160 |  |  | -35.9771 | 160 | -0.36388 | -58.2216 | 0.048644 | 0.068394 |  |  |  |  | 8 | 0.012772
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.22486 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.36388 | 175 | 175 |  |  | -39.35 | 175 | -0.36388 | -63.6798 | 0.056911 | 0.080008 |  |  |  |  | 9 | 0.013671
9000 | DECKR_G1 | 1 | South | YES | -0.22261 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.36164 | 321 | 321 |  |  | -71.4585 | 321 | -0.36164 | -116.0864 | 0.072077 | 0.10118 |  |  |  |  | 10 | 0.016692
9001 | DECKR_G2 | 2 | South | YES | -0.22261 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.36164 | 426 | 426 |  |  | -94.8327 | 426 | -0.36164 | -154.0585 | 0.092204 | 0.12928 |  |  |  |  | 11 | 0.019751
9016 | SANDH_G1 | 1 | South | YES | -0.22125 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.36028 | 49 | 49 |  |  | -10.8412 | 49 | -0.36028 | -17.6535 | 0.094519 | 0.13249 |  |  |  |  | 12 | 0.023096
9017 | SANDH_G2 | 2 | South | YES | -0.22125 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.36028 | 46 | 46 |  |  | -10.1774 | 46 | -0.36028 | -16.5727 | 0.096692 | 0.13552 |  |  |  |  | 13 | 0.029102
9018 | SANDH_G3 | 3 | South | YES | -0.22125 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.36028 | 46 | 46 |  |  | -10.1774 | 46 | -0.36028 | -16.5727 | 0.098865 | 0.13854 |  |  |  |  | 14 | 0.037072
9019 | SANDH_G4 | 4 | South | YES | -0.22125 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.36028 | 47 | 47 |  |  | -10.3987 | 47 | -0.36028 | -16.933 | 0.10109 | 0.14163 |  |  |  |  | 15 | 0.037976
9020 | SANDHG5A | 5A | South | YES | -0.22125 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.36028 | 155 | 155 |  |  | -34.2934 | 155 | -0.36028 | -55.8427 | 0.10841 | 0.15181 |  |  |  |  | 16 | 0.038825
9021 | SANDHG5C | 5C | South | YES | -0.22125 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.36028 | 148 | 148 |  |  | -32.7447 | 148 | -0.36028 | -53.3208 | 0.1154 | 0.16154 |  |  |  |  | 17 | 0.039674
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.2208 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.35983 | 0 | 0 |  |  | 0 | 0 | -0.35983 | 0 | 0.1154 | 0.16154 |  |  |  |  | 18 | 0.040542
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.2208 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.35983 | 0 | 0 |  |  | 0 | 0 | -0.35983 | 0 | 0.1154 | 0.16154 |  |  |  |  | 19 | 0.043403
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.21458 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.3536 | 132 | 132 |  |  | -28.324 | 132 | -0.3536 | -46.6757 | 0.12164 | 0.17005 |  |  |  |  | 20 | 0.046135
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.21458 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.3536 | 139 | 139 |  |  | -29.8261 | 139 | -0.3536 | -49.1509 | 0.1282 | 0.17901 |  |  |  |  | 21 | 0.046135
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.21458 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.3536 | 329 | 329 |  |  | -70.5955 | 329 | -0.3536 | -116.3356 | 0.14375 | 0.20023 |  |  |  |  | 22 | 0.046135
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.21272 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0 | 0.14375 | 0.20023 |  |  |  |  | 23 | 0.048411
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.21272 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0 | 0.14375 | 0.20023 |  |  |  |  | 24 | 0.050808
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.21272 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0 | 0.14375 | 0.20023 |  |  |  |  | 25 | 0.056481
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.19858 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.3376 | 0 | 606 |  |  | 0 | 0 | -0.3376 | 0 | 0.14375 | 0.20023 |  |  |  |  | 26 | 0.056481
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.19858 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.3376 | 0 | 598 |  |  | 0 | 0 | -0.3376 | 0 | 0.14375 | 0.20023 |  |  |  |  | 27 | 0.056481
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.19837 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.3374 | 0 | 436 |  |  | 0 | 0 | -0.3374 | 0 | 0.14375 | 0.20023 |  |  |  |  | 28 | 0.056481
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.1978 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.33683 | 0 | 0 |  |  | 0 | 0 | -0.33683 | 0 | 0.14375 | 0.20023 |  |  |  |  | 29 | 0.056481
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.1978 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.33683 | 0 | 0 |  |  | 0 | 0 | -0.33683 | 0 | 0.14375 | 0.20023 |  |  |  |  | 30 | 0.056481
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808 | 0.14611 | 0.20329 |  |  |  |  | 31 | 0.056481
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808 | 0.14847 | 0.20636 |  |  |  |  | 32 | 0.056481
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808 | 0.15083 | 0.20943 |  |  |  |  | 33 | 0.056481
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808 | 0.1532 | 0.21249 |  |  |  |  | 34 | 0.057184
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.1952 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.33422 | 0 | 0 |  |  | 0 | 0 | -0.33422 | 0 | 0.1532 | 0.21249 |  |  |  |  | 35 | 0.057887
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.19304 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.33207 | 223.9 | 223.9 |  |  | -43.2214 | 223.9 | -0.33207 | -74.3497 | 0.16378 | 0.22605 |  |  |  |  | 36 | 0.05859
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.19304 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.33207 | 225 | 225 |  |  | -43.4338 | 225 | -0.33207 | -74.715 | 0.17441 | 0.23968 |  |  |  |  | 37 | 0.059294
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.19304 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.33207 | 224.6 | 224.6 |  |  | -43.3566 | 224.6 | -0.33207 | -74.5822 | 0.18502 | 0.25328 |  |  |  |  | 38 | 0.059294
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.19304 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.33207 | 226.7 | 226.7 |  |  | -43.7619 | 226.7 | -0.33207 | -75.2795 | 0.19573 | 0.26701 |  |  |  |  | 39 | 0.062275
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.19212 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.33115 | 0 | 0 |  |  | 0 | 0 | -0.33115 | 0 | 0.19573 | 0.26701 |  |  |  |  | 40 | 0.065271
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.19212 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.33115 | 0 | 0 |  |  | 0 | 0 | -0.33115 | 0 | 0.19573 | 0.26701 |  |  |  |  | 41 | 0.068261
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.19059 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0 | 0.19573 | 0.26701 |  |  |  |  | 42 | 0.07128
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.19059 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0 | 0.19573 | 0.26701 |  |  |  |  | 43 | 0.07128
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.19059 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0 | 0.19573 | 0.26701 |  |  |  |  | 44 | 0.07128
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.19059 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.32961 | 423.3 | 423.3 |  |  | -80.6746 | 423.3 | -0.32961 | -139.5251 | 0.21573 | 0.29245 |  |  |  |  | 45 | 0.07128
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.18586 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.32488 | 148 | 148 |  |  | -27.5068 | 148 | -0.32488 | -48.0829 | 0.22272 | 0.30122 |  |  |  |  | 46 | 0.07128
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.18586 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.32488 | 148 | 148 |  |  | -27.5068 | 148 | -0.32488 | -48.0829 | 0.22971 | 0.30999 |  |  |  |  | 47 | 0.07128
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.18586 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.32488 | 154 | 154 |  |  | -28.622 | 154 | -0.32488 | -50.0323 | 0.23699 | 0.31912 |  |  |  |  | 48 | 0.076727
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.18586 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.32488 | 293 | 293 |  |  | -54.4561 | 293 | -0.32488 | -95.1912 | 0.25083 | 0.33648 |  |  |  |  | 49 | 0.078504
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.18533 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0 | 0.25083 | 0.33648 |  |  |  |  | 50 | 0.08028
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.18533 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0 | 0.25083 | 0.33648 |  |  |  |  | 51 | 0.082129
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.18533 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0 | 0.25083 | 0.33648 |  |  |  |  | 52 | 0.085647
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.18349 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.32252 | 0 | 0 |  |  | 0 | 0 | -0.32252 | 0 | 0.25083 | 0.33648 |  |  |  |  | 53 | 0.085647
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.18316 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.32219 | 0 | 0 |  |  | 0 | 0 | -0.32219 | 0 | 0.25083 | 0.33648 |  |  |  |  | 54 | 0.085647
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.18179 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.32082 | 0 | 0 |  |  | 0 | 0 | -0.32082 | 0 | 0.25083 | 0.33648 |  |  |  |  | 55 | 0.085647
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.18179 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.32082 | 0 | 0 |  |  | 0 | 0 | -0.32082 | 0 | 0.25083 | 0.33648 |  |  |  |  | 56 | 0.085647
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.1791 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.31813 | 147 | 147 |  |  | -26.328 | 147 | -0.31813 | -46.7651 | 0.25777 | 0.345 |  |  |  |  | 57 | 0.085647
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.1791 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.31813 | 138 | 138 |  |  | -24.7161 | 138 | -0.31813 | -43.9019 | 0.26429 | 0.35301 |  |  |  |  | 58 | 0.085647
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.1791 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.31813 | 146 | 146 |  |  | -26.1489 | 146 | -0.31813 | -46.4469 | 0.27119 | 0.36148 |  |  |  |  | 59 | 0.085647
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.1791 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.31813 | 149 | 149 |  |  | -26.6862 | 149 | -0.31813 | -47.4013 | 0.27823 | 0.37013 |  |  |  |  | 60 | 0.087231
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.1791 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.31813 | 182 | 182 |  |  | -32.5966 | 182 | -0.31813 | -57.8996 | 0.28683 | 0.38069 |  |  |  |  | 61 | 0.088717
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.1791 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.31813 | 203 | 203 |  |  | -36.3577 | 203 | -0.31813 | -64.5803 | 0.29642 | 0.39246 |  |  |  |  | 62 | 0.09029
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.17474 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.31377 | 61 | 61 |  |  | -10.6591 | 61 | -0.31377 | -19.1398 | 0.2993 | 0.39595 |  |  |  |  | 63 | 0.091895
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.17474 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.31377 | 95 | 95 |  |  | -16.6002 | 95 | -0.31377 | -29.8078 | 0.30379 | 0.40139 |  |  |  |  | 64 | 0.093856
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.17474 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.31377 | 151 | 151 |  |  | -26.3856 | 151 | -0.31377 | -47.3788 | 0.31092 | 0.41003 |  |  |  |  | 65 | 0.096043
5111 | CALAVER_JTD1 | 1 | South | YES | -0.17406 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.31308 | 0 | 430 |  |  | 0 | 0 | -0.31308 | 0 | 0.31092 | 0.41003 |  |  |  |  | 66 | 0.096652
5112 | CALAVER_JTD2 | 2 | South | YES | -0.17406 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.31308 | 0 | 430 |  |  | 0 | 0 | -0.31308 | 0 | 0.31092 | 0.41003 |  |  |  |  | 67 | 0.0976
5396 | CALAVER_OWS1 | 1 | South | YES | -0.17386 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.31289 | 418 | 418 |  |  | -72.6756 | 418 | -0.31289 | -130.7892 | 0.33067 | 0.43388 |  |  |  |  | 68 | 0.099106
5397 | CALAVER_OWS2 | 2 | South | YES | -0.17386 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.31289 | 400 | 400 |  |  | -69.546 | 400 | -0.31289 | -125.1571 | 0.34957 | 0.45671 |  |  |  |  | 69 | 0.099106
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.17363 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.31266 | 215 | 215 |  |  | -37.3313 | 215 | -0.31266 | -67.2223 | 0.35973 | 0.46897 |  |  |  |  | 70 | 0.099106
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.17363 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.31266 | 216 | 216 |  |  | -37.5049 | 216 | -0.31266 | -67.5349 | 0.36993 | 0.48129 |  |  |  |  | 71 | 0.10321
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.17355 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.31258 | 407 | 407 |  |  | -70.6349 | 407 | -0.31258 | -127.2191 | 0.38916 | 0.50449 |  |  |  |  | 72 | 0.10714
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.17279 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.31182 | 155 | 155 |  |  | -26.7826 | 155 | -0.31182 | -48.3319 | 0.39649 | 0.5133 |  |  |  |  | 73 | 0.10924
5477 | BRA_AVR1_ST | 1 | South | YES | -0.17279 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.31182 | 174 | 174 |  |  | -30.0656 | 174 | -0.31182 | -54.2565 | 0.40471 | 0.5232 |  |  |  |  | 74 | 0.11135
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.17279 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.31182 | 155 | 155 |  |  | -26.7826 | 155 | -0.31182 | -48.3319 | 0.41203 | 0.53201 |  |  |  |  | 75 | 0.11532
5264 | LEON_LCP3G3 | 3 | South | YES | -0.17241 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.31143 | 58 | 58 |  |  | -9.9995 | 58 | -0.31143 | -18.0631 | 0.41477 | 0.53531 |  |  |  |  | 76 | 0.11682
5265 | LEON_LCP4G4 | 4 | South | YES | -0.17241 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.31143 | 89 | 89 |  |  | -15.344 | 89 | -0.31143 | -27.7175 | 0.41897 | 0.54036 |  |  |  |  | 77 | 0.11849
5266 | LEON_LCPCT1 | 1 | South | YES | -0.17241 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.31143 | 44 | 44 |  |  | -7.5858 | 44 | -0.31143 | -13.703 | 0.42105 | 0.54286 |  |  |  |  | 78 | 0.11998
5267 | LEON_LCPCT2 | 2 | South | YES | -0.17241 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.31143 | 44 | 44 |  |  | -7.5858 | 44 | -0.31143 | -13.703 | 0.42313 | 0.54536 |  |  |  |  | 79 | 0.12054
5268 | LEON_LCPCT3 | 3 | South | YES | -0.17241 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.31143 | 43 | 43 |  |  | -7.4134 | 43 | -0.31143 | -13.3916 | 0.42516 | 0.5478 |  |  |  |  | 80 | 0.12139
5269 | LEON_LCPCT4 | 4 | South | YES | -0.17241 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.31143 | 45 | 45 |  |  | -7.7582 | 45 | -0.31143 | -14.0145 | 0.42729 | 0.55036 |  |  |  |  | 81 | 0.12181
5401 | CALAVER_JKS1 | 1 | South | YES | -0.17172 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.31075 | 0 | 562 |  |  | 0 | 0 | -0.31075 | 0 | 0.42729 | 0.55036 |  |  |  |  | 82 | 0.12223
8189 | CUECPL2A | 1 | South | YES | -0.17052 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.30955 | 0 | 0 |  |  | 0 | 0 | -0.30955 | 0 | 0.42729 | 0.55036 |  |  |  |  | 83 | 0.12264
5903 | SANMIGUELGEN | 1 | South | YES | -0.16363 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.30266 | 0 | 396.3 |  |  | 0 | 0 | -0.30266 | 0 | 0.42729 | 0.55036 |  |  |  |  | 84 | 0.12307
5890 | PEARSALLGEN1 | 1 | South | YES | -0.15295 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.29198 | 24 | 24 |  |  | -3.6708 | 24 | -0.29198 | -7.0075 | 0.42842 | 0.55163 |  |  |  |  | 85 | 0.12307
5891 | PEARSALLGEN2 | 1 | South | YES | -0.15295 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.29198 | 24.3 | 24.3 |  |  | -3.7167 | 24.3 | -0.29198 | -7.0951 | 0.42957 | 0.55293 |  |  |  |  | 86 | 0.12307
5892 | PEARSALLGEN3 | 1 | South | YES | -0.15295 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.29198 | 23.9 | 23.9 |  |  | -3.6555 | 23.9 | -0.29198 | -6.9783 | 0.4307 | 0.5542 |  |  |  |  | 87 | 0.12307
88198 | BEEVILLE | F | South | YES | -0.15001 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.28904 | 0 | 0 |  |  | 0 | 0 | -0.28904 | 0 | 0.4307 | 0.5542 |  |  |  |  | 88 | 0.12321
58909 | PEARSALLSCG1 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.4311 | 0.55464 |  |  |  |  | 89 | 0.12336
58909 | PEARSALLSCG1 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43149 | 0.55509 |  |  |  |  | 90 | 0.1235
58909 | PEARSALLSCG1 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43189 | 0.55553 |  |  |  |  | 91 | 0.1235
58909 | PEARSALLSCG1 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43229 | 0.55597 |  |  |  |  | 92 | 0.12355
58909 | PEARSALLSCG1 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43269 | 0.55641 |  |  |  |  | 93 | 0.12359
58909 | PEARSALLSCG1 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43308 | 0.55686 |  |  |  |  | 94 | 0.12364
58919 | PEARSALLSCG2 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43348 | 0.5573 |  |  |  |  | 95 | 0.12368
58919 | PEARSALLSCG2 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43388 | 0.55774 |  |  |  |  | 96 | 0.12373
58919 | PEARSALLSCG2 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43427 | 0.55819 |  |  |  |  | 97 | 0.12378
58919 | PEARSALLSCG2 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43467 | 0.55863 |  |  |  |  | 98 | 0.12382
58919 | PEARSALLSCG2 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43507 | 0.55907 |  |  |  |  | 99 | 0.12387
58919 | PEARSALLSCG2 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43546 | 0.55951 |  |  |  |  | 100 | 0.12391
58929 | PEARSALLSCG3 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43586 | 0.55996 |  |  |  |  | 101 | 0.12396
58929 | PEARSALLSCG3 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43626 | 0.5604 |  |  |  |  | 102 | 0.124
58929 | PEARSALLSCG3 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43665 | 0.56084 |  |  |  |  | 103 | 0.12405
58929 | PEARSALLSCG3 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43705 | 0.56128 |  |  |  |  | 104 | 0.1241
58929 | PEARSALLSCG3 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43745 | 0.56173 |  |  |  |  | 105 | 0.12414
58929 | PEARSALLSCG3 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43784 | 0.56217 |  |  |  |  | 106 | 0.12419
58949 | PEARSALLSCG4 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43824 | 0.56261 |  |  |  |  | 107 | 0.12423
58949 | PEARSALLSCG4 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43864 | 0.56306 |  |  |  |  | 108 | 0.12428
58949 | PEARSALLSCG4 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43903 | 0.5635 |  |  |  |  | 109 | 0.12433
58949 | PEARSALLSCG4 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43943 | 0.56394 |  |  |  |  | 110 | 0.12437
58949 | PEARSALLSCG4 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.43983 | 0.56438 |  |  |  |  | 111 | 0.12442
58949 | PEARSALLSCG4 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 | 0.44023 | 0.56483 |  |  |  |  | 112 | 0.12446
8161 | COLETO0A | 1 | South | YES | -0.14836 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.28739 | 0 | 633 |  |  | 0 | 0 | -0.28739 | 0 | 0.44023 | 0.56483 |  |  |  |  | 113 | 0.12451
80080 | GWINDT11A | 3 | South | YES | -0.14255 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 38 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 114 | 0.12455
80080 | GWINDT11A | 4 | South | YES | -0.14255 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 19 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 115 | 0.1246
80080 | GWINDT11A | 2 | South | YES | -0.14255 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 41 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 116 | 0.1246
80080 | GWINDT11A | 1 | South | YES | -0.14255 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 94 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 117 | 0.1246
80081 | GWINDT21A | 4 | South | YES | -0.14255 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 22 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 118 | 0.1246
80081 | GWINDT21A | 1 | South | YES | -0.14255 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 94 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 119 | 0.1246
80081 | GWINDT21A | 3 | South | YES | -0.14255 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 43 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 120 | 0.1246
80081 | GWINDT21A | 2 | South | YES | -0.14255 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 36 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 121 | 0.1246
80180 | PNSCALT11A | 2 | South | YES | -0.14255 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 50 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 122 | 0.1246
80180 | PNSCALT11A | 1 | South | YES | -0.14255 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 148 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 123 | 0.1246
80181 | PNSCALT21A | 2 | South | YES | -0.14255 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 50 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 124 | 0.1246
80181 | PNSCALT21A | 1 | South | YES | -0.14255 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 55 |  |  | 0 | 0 | -0.28157 | 0 | 0.44023 | 0.56483 |  |  |  |  | 125 | 0.1246
5932 | SI_RAY9 | 9 | South | YES | -0.14252 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.28155 | 38 | 38 |  |  | -5.4157 | 38 | -0.28155 | -10.6988 | 0.44202 | 0.56678 |  |  |  |  | 126 | 0.1246
5933 | SI_RAY6 | 6 | South | YES | -0.14252 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.28155 | 19.3 | 19.3 |  |  | -2.7506 | 19.3 | -0.28155 | -5.4339 | 0.44293 | 0.56777 |  |  |  |  | 127 | 0.1246
5935 | SI_RAY10 | 10 | South | YES | -0.14252 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.28155 | 47 | 47 |  |  | -6.6984 | 47 | -0.28155 | -13.2327 | 0.44515 | 0.57018 |  |  |  |  | 128 | 0.1246
80003 | MILHWYS | F | South | YES | -0.14252 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.28155 | 0 | 0 |  |  | 0 | 0 | -0.28155 | 0 | 0.44515 | 0.57018 |  |  |  |  | 129 | 0.12476
8936 | MVGN#1 | 1 | South | YES | -0.14248 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.28151 | 216.6 | 216.6 |  |  | -30.8612 | 216.6 | -0.28151 | -60.9746 | 0.45539 | 0.5813 |  |  |  |  | 130 | 0.12484
8937 | MVGN#2 | 2 | South | YES | -0.14248 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.28151 | 216.7 | 216.7 |  |  | -30.8754 | 216.7 | -0.28151 | -61.0027 | 0.46562 | 0.59243 |  |  |  |  | 131 | 0.12503
8938 | MVGN#3 | 3 | South | YES | -0.14248 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.28151 | 250.9 | 250.9 |  |  | -35.7482 | 250.9 | -0.28151 | -70.6303 | 0.47748 | 0.60531 |  |  |  |  | 132 | 0.12503
8981 | HECN1 | 1 | South | YES | -0.14248 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.28151 | 144.8 | 144.8 |  |  | -20.6311 | 144.8 | -0.28151 | -40.7623 | 0.48432 | 0.61274 |  |  |  |  | 133 | 0.12592
8982 | HECN2 | 2 | South | YES | -0.14248 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.28151 | 144.1 | 144.1 |  |  | -20.5314 | 144.1 | -0.28151 | -40.5653 | 0.49113 | 0.62014 |  |  |  |  | 134 | 0.1268
8983 | HECN3 | 3 | South | YES | -0.14248 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.28151 | 171.9 | 171.9 |  |  | -24.4923 | 171.9 | -0.28151 | -48.3912 | 0.49925 | 0.62897 |  |  |  |  | 135 | 0.12783
8517 | CELANEBI0A | 1 | South | YES | -0.14239 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.28141 | 0 | 0 |  |  | 0 | 0 | -0.28141 | 0 | 0.49925 | 0.62897 |  |  |  |  | 136 | 0.12842
8933 | FGNTS001 | 1 | South | YES | -0.14236 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.28138 | 146.5 | 146.5 |  |  | -20.8552 | 146.5 | -0.28138 | -41.2227 | 0.50617 | 0.63648 |  |  |  |  | 137 | 0.12901
8934 | FGNTS101 | 2 | South | YES | -0.14236 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.28138 | 147.9 | 147.9 |  |  | -21.0545 | 147.9 | -0.28138 | -41.6167 | 0.51316 | 0.64407 |  |  |  |  | 138 | 0.12972
8935 | FGNTS201 | 3 | South | YES | -0.14236 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.28138 | 173 | 173 |  |  | -24.6276 | 173 | -0.28138 | -48.6794 | 0.52133 | 0.65295 |  |  |  |  | 139 | 0.12972
8461 | KOCH_UP0A | 1 | South | YES | -0.14185 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.28087 | 0 | 0 |  |  | 0 | 0 | -0.28087 | 0 | 0.52133 | 0.65295 |  |  |  |  | 140 | 0.13031
8511 | OXY_CC0A | 1 | South | YES | -0.14185 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.28087 | 0 | 0 |  |  | 0 | 0 | -0.28087 | 0 | 0.52133 | 0.65295 |  |  |  |  | 141 | 0.13092
8506 | VAL #1 | 1 | South | YES | -0.1417 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.28073 | 0 | 0 |  |  | 0 | 0 | -0.28073 | 0 | 0.52133 | 0.65295 |  |  |  |  | 142 | 0.13162
8507 | VAL #2 | 2 | South | YES | -0.1417 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.28073 | 0 | 0 |  |  | 0 | 0 | -0.28073 | 0 | 0.52133 | 0.65295 |  |  |  |  | 143 | 0.13162
8459 | B_DAVIS0B | MB | South | YES | -0.14163 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.28066 | 0 | 0 |  |  | 0 | 0 | -0.28066 | 0 | 0.52133 | 0.65295 |  |  |  |  | 144 | 0.13162
8460 | B_DAVIS0A | MB | South | YES | -0.14163 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.28066 | 0 | 0 |  |  | 0 | 0 | -0.28066 | 0 | 0.52133 | 0.65295 |  |  |  |  | 145 | 0.13162
80263 | B_DAVIS31A | 3 | South | YES | -0.14163 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.28066 | 180 | 180 |  |  | -25.493 | 180 | -0.28066 | -50.518 | 0.52984 | 0.66216 |  |  |  |  | 146 | 0.13162
80264 | B_DAVIS41A | 4 | South | YES | -0.14163 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.28066 | 180 | 180 |  |  | -25.493 | 180 | -0.28066 | -50.518 | 0.53834 | 0.67138 |  |  |  |  | 147 | 0.13162
5728 | FALCONHYDRO2 | 2 | South | YES | -0.14163 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0 | 0.53834 | 0.67138 |  |  |  |  | 148 | 0.13162
5729 | FALCONHYDRO3 | 3 | South | YES | -0.14163 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0 | 0.53834 | 0.67138 |  |  |  |  | 149 | 0.13233
8048 | FALCONHYDRO1 | 1 | South | YES | -0.14163 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0 | 0.53834 | 0.67138 |  |  |  |  | 150 | 0.13304
88508 | FALFURRI | F | South | YES | -0.1416 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.28063 | 0 | 0 |  |  | 0 | 0 | -0.28063 | 0 | 0.53834 | 0.67138 |  |  |  |  | 151 | 0.13304
8456 | COSW#1 | 1 | South | YES | -0.14144 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.28047 | 0 | 0 |  |  | 0 | 0 | -0.28047 | 0 | 0.53834 | 0.67138 |  |  |  |  | 152 | 0.13304
8457 | COSW#2 | 2 | South | YES | -0.14144 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.28047 | 0 | 0 |  |  | 0 | 0 | -0.28047 | 0 | 0.53834 | 0.67138 |  |  |  |  | 153 | 0.13304
8173 | VICEC51A | 5 | South | YES | -0.14137 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.28039 | 144 | 144 |  |  | -20.3568 | 144 | -0.28039 | -40.3768 | 0.54514 | 0.67874 |  |  |  |  | 154 | 0.13304
8174 | VICEC61A | 6 | South | YES | -0.14137 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.28039 | 188 | 188 |  |  | -26.577 | 188 | -0.28039 | -52.7142 | 0.55402 | 0.68835 |  |  |  |  | 155 | 0.13304
8560 | CNOPGT1 | 1 | South | YES | -0.14136 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0 | 0.55402 | 0.68835 |  |  |  |  | 156 | 0.13304
8561 | CNOPGT2 | 2 | South | YES | -0.14136 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0 | 0.55402 | 0.68835 |  |  |  |  | 157 | 0.1336
8562 | CNOPST1 | 3 | South | YES | -0.14136 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0 | 0.55402 | 0.68835 |  |  |  |  | 158 | 0.13433
8442 | NBEC7 | 7 | South | YES | -0.14135 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.28037 | 367 | 367 |  |  | -51.8743 | 367 | -0.28037 | -102.8975 | 0.57136 | 0.70712 |  |  |  |  | 159 | 0.13433
8442 | NBEC7 | MB | South | YES | -0.14135 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.28037 | 0 | 0 |  |  | 0 | 0 | -0.28037 | 0 | 0.57136 | 0.70712 |  |  |  |  | 160 | 0.13433
88299 | ZAPATA | F | South | YES | -0.14093 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.27995 | 0 | 0 |  |  | 0 | 0 | -0.27995 | 0 | 0.57136 | 0.70712 |  |  |  |  | 161 | 0.13433
8926 | LGE_GT10A | 1 | South | YES | -0.13998 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 | 0.57136 | 0.70712 |  |  |  |  | 162 | 0.13576
8927 | LGE_GT20A | 2 | South | YES | -0.13998 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 | 0.57136 | 0.70712 |  |  |  |  | 163 | 0.13576
8928 | LGE_STG0A | 3 | South | YES | -0.13998 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 | 0.57136 | 0.70712 |  |  |  |  | 164 | 0.13576
8930 | ICPGN10A | 1 | South | YES | -0.13998 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 | 0.57136 | 0.70712 |  |  |  |  | 165 | 0.13576
8931 | ICPGN20A | 2 | South | YES | -0.13998 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 | 0.57136 | 0.70712 |  |  |  |  | 166 | 0.13576
8932 | ICPGN30A | 3 | South | YES | -0.13998 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 | 0.57136 | 0.70712 |  |  |  |  | 167 | 0.13576
80223 | REYSHR G | 1 | South | YES | -0.13998 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 | 0.57136 | 0.70712 |  |  |  |  | 168 | 0.13576
80012 | LAR | F | South | YES | -0.13989 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.27892 | 0 | 0 |  |  | 0 | 0 | -0.27892 | 0 | 0.57136 | 0.70712 |  |  |  |  | 169 | 0.13576
80265 | LARECU40A | 4 | South | YES | -0.13989 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27892 | 100 | 100 |  |  | -13.9893 | 100 | -0.27892 | -27.8921 | 0.57609 | 0.71221 |  |  |  |  | 170 | 0.13576
80266 | LARECU50A | 5 | South | YES | -0.13989 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27892 | 100 | 100 |  |  | -13.9893 | 100 | -0.27892 | -27.8921 | 0.58081 | 0.71729 |  |  |  |  | 171 | 0.13576
8066 | DUP1V#1 | 1 | South | YES | -0.13974 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.27877 | 0 | 0 |  |  | 0 | 0 | -0.27877 | 0 | 0.58081 | 0.71729 |  |  |  |  | 172 | 0.13576
5508 | RAYBURNCC9 | 1 | South | YES | -0.13957 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.2786 | 47.7 | 47.7 |  |  | -6.6575 | 47.7 | -0.2786 | -13.2891 | 0.58307 | 0.71972 |  |  |  |  | 173 | 0.13612
5509 | RAYBURNCC10 | 1 | South | YES | -0.13957 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.2786 | 37.3 | 37.3 |  |  | -5.206 | 37.3 | -0.2786 | -10.3917 | 0.58483 | 0.72161 |  |  |  |  | 174 | 0.13648
5511 | RAYBURNCC7 | 1 | South | YES | -0.13957 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.2786 | 47.5 | 47.5 |  |  | -6.6296 | 47.5 | -0.2786 | -13.2334 | 0.58707 | 0.72403 |  |  |  |  | 175 | 0.13648
5512 | RAYBURNCC8 | 1 | South | YES | -0.13957 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.2786 | 49.3 | 49.3 |  |  | -6.8808 | 49.3 | -0.2786 | -13.7349 | 0.5894 | 0.72653 |  |  |  |  | 176 | 0.13665
5503 | RAYBURNGEN3 | 1 | South | YES | -0.13824 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.27727 | 22 | 22 |  |  | -3.0412 | 22 | -0.27727 | -6.0998 | 0.59044 | 0.72764 |  |  |  |  | 177 | 0.13678
5505 | RAYBURNGEN1 | 1 | South | YES | -0.13824 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27727 | 11 | 11 |  |  | -1.5206 | 11 | -0.27727 | -3.0499 | 0.59096 | 0.7282 |  |  |  |  | 178 | 0.13695
5506 | RAYBURNGEN2 | 1 | South | YES | -0.13824 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27727 | 11 | 11 |  |  | -1.5206 | 11 | -0.27727 | -3.0499 | 0.59148 | 0.72876 |  |  |  |  | 179 | 0.13713
80224 | VISTRONG1 | 1 | South | YES | -0.13688 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0 | 0.59148 | 0.72876 |  |  |  |  | 180 | 0.1372
80225 | VISTRONG2 | 2 | South | YES | -0.13688 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0 | 0.59148 | 0.72876 |  |  |  |  | 181 | 0.13724
80227 | AIRCO G | 1 | South | YES | -0.13582 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.27484 | 0 | 0 |  |  | 0 | 0 | -0.27484 | 0 | 0.59148 | 0.72876 |  |  |  |  | 182 | 0.13728
8147 | UCAR #2 | 10 | South | YES | -0.13528 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 | 0.59148 | 0.72876 |  |  |  |  | 183 | 0.13728
8148 | UCAR #1 | 2 | South | YES | -0.13528 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 | 0.59148 | 0.72876 |  |  |  |  | 184 | 0.13728
80137 | CSDR89 | 9 | South | YES | -0.13528 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 | 0.59148 | 0.72876 |  |  |  |  | 185 | 0.13728
80137 | CSDR89 | 8 | South | YES | -0.13528 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 | 0.59148 | 0.72876 |  |  |  |  | 186 | 0.13728
80138 | CSDR7 | 7 | South | YES | -0.13528 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 | 0.59148 | 0.72876 |  |  |  |  | 187 | 0.13728
80139 | CSDR56 | 6 | South | YES | -0.13528 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 | 0.59148 | 0.72876 |  |  |  |  | 188 | 0.13728
80139 | CSDR56 | 5 | South | YES | -0.13528 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 | 0.59148 | 0.72876 |  |  |  |  | 189 | 0.13728
80140 | CSDR11 | 11 | South | YES | -0.13528 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 | 0.59148 | 0.72876 |  |  |  |  | 190 | 0.13728
80226 | ALCOA G | 1 | South | YES | -0.13149 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.27052 | 0 | 0 |  |  | 0 | 0 | -0.27052 | 0 | 0.59148 | 0.72876 |  |  |  |  | 191 | 0.13728
8134 | FOR #1 | 1 | South | YES | -0.13032 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 192 | 0.13728
8138 | FOR #2 | 2 | South | YES | -0.13032 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 193 | 0.13728
8153 | FOR #3 | 3 | South | YES | -0.13032 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 194 | 0.13728
8154 | FOR #4 | 4 | South | YES | -0.13032 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 195 | 0.13728
8155 | FOR #5 | 5 | South | YES | -0.13032 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 196 | 0.13728
8156 | FOR #6 | 6 | South | YES | -0.13032 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 197 | 0.13728
8157 | FOR #7 | 7 | South | YES | -0.13032 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 198 | 0.13728
80051 | FOR #8 | 8 | South | YES | -0.13032 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 199 | 0.13728
80052 | FOR #9 | 9 | South | YES | -0.13032 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 200 | 0.13728
80053 | FOR #10 | 10 | South | YES | -0.13032 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 | 0.59148 | 0.72876 |  |  |  |  | 201 | 0.13728
8262 | ELPS | 1 | South | YES | -0.098206 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.23723 | 0 | 0 |  |  | 0 | 0 | -0.23723 | 0 | 0.59148 | 0.72876 |  |  |  |  | 202 | 0.13728
5911 | STP_GN1___1 | 1 | Houston | YES | -0.088308 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.22734 | 0 | 0 |  |  |  |  | -0.22734 | 0 | 0.59148 | 0.72876 |  |  |  |  | 203 | 0.13728
5912 | STP_GN2___2 | 2 | Houston | YES | -0.088308 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.22734 | 0 | 0 |  |  |  |  | -0.22734 | 0 | 0.59148 | 0.72876 |  |  |  |  | 204 | 0.13728
48731 | CBE_GT1 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153 | 0.59507 | 0.7319 |  |  |  |  | 205 | 0.13728
48732 | CBE_GT2 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153 | 0.59866 | 0.73504 |  |  |  |  | 206 | 0.13728
48733 | CBE_ST12 | 1 | Houston | YES | -0.087489 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22652 | 105 | 105 |  |  |  |  | -0.22652 | -23.7843 | 0.60362 | 0.73937 |  |  |  |  | 207 | 0.13728
48734 | CBE_GT3 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153 | 0.60721 | 0.74251 |  |  |  |  | 208 | 0.13682
48735 | CBE_GT4 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153 | 0.6108 | 0.74565 |  |  |  |  | 209 | 0.13637
48736 | CBE_ST34 | 1 | Houston | YES | -0.087489 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22652 | 105 | 105 |  |  |  |  | -0.22652 | -23.7843 | 0.61576 | 0.74999 |  |  |  |  | 210 | 0.13575
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.082186 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.22121 | 0 | 0 |  |  |  |  | -0.22121 | 0 | 0.61576 | 0.74999 |  |  |  |  | 211 | 0.1353
8032 | AMISTADHYD1 | 1 | South | YES | -0.075631 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0 | 0.61576 | 0.74999 |  |  |  |  | 212 | 0.13485
8033 | AMISTADHYD2 | 2 | South | YES | -0.075631 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0 | 0.61576 | 0.74999 |  |  |  |  | 213 | 0.13423
88253 | HAMILTON | F | South | YES | -0.075631 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0 | 0.61576 | 0.74999 |  |  |  |  | 214 | 0.13423
49851 | DOW17000 | 37 | Houston | YES | -0.066124 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 215 | 0.13423
49858 | DOW38100 | 31 | Houston | YES | -0.066124 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 216 | 0.13423
49859 | DOW38200 | 33 | Houston | YES | -0.066124 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 217 | 0.13423
49860 | DOW38300 | 32 | Houston | YES | -0.066124 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 218 | 0.13423
49862 | DOW39100 | 36 | Houston | YES | -0.066124 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 219 | 0.13423
49863 | DOW39200 | 35 | Houston | YES | -0.066124 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 220 | 0.13423
49865 | DOW41000 | 41 | Houston | YES | -0.066124 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 221 | 0.13423
49866 | DOW42000 | 42 | Houston | YES | -0.066124 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 222 | 0.13423
49869 | DOW49000 | 45 | Houston | YES | -0.066124 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 223 | 0.13423
49870 | DOW61000 | 61 | Houston | YES | -0.066124 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 224 | 0.13423
49871 | DOW62000 | 62 | Houston | YES | -0.066124 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 225 | 0.13423
49872 | DOW63000 | 63 | Houston | YES | -0.066124 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 226 | 0.13423
49873 | DOW64000 | 64 | Houston | YES | -0.066124 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 227 | 0.13423
49876 | DOW65000 | 65 | Houston | YES | -0.066124 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 228 | 0.13423
49877 | DOW66000 | 66 | Houston | YES | -0.066124 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 229 | 0.13423
49878 | DOW67000 | 67 | Houston | YES | -0.066124 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 230 | 0.13423
49882 | DOW81000 | 81 | Houston | YES | -0.066124 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 231 | 0.13423
49884 | DOW82000 | 82 | Houston | YES | -0.066124 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 232 | 0.13423
49885 | DOW83000 | 83 | Houston | YES | -0.066124 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 233 | 0.13423
49886 | DOW84000 | 84 | Houston | YES | -0.066124 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 | 0.61576 | 0.74999 |  |  |  |  | 234 | 0.13423
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.062036 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.20106 | 0 | 0 |  |  |  |  | -0.20106 | 0 | 0.61576 | 0.74999 |  |  |  |  | 235 | 0.13423
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.062036 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.20106 | 0 | 0 |  |  |  |  | -0.20106 | 0 | 0.61576 | 0.74999 |  |  |  |  | 236 | 0.13423
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.0588 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0 | 0.61576 | 0.74999 |  |  |  |  | 237 | 0.13423
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.0588 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0 | 0.61576 | 0.74999 |  |  |  |  | 238 | 0.13423
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.0588 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0 | 0.61576 | 0.74999 |  |  |  |  | 239 | 0.13423
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.0588 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0 | 0.61576 | 0.74999 |  |  |  |  | 240 | 0.13423
48730 | MNS_GT | 1 | Houston | YES | -0.047181 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.18621 | 0 | 0 |  |  |  |  | -0.18621 | 0 | 0.61576 | 0.74999 |  |  |  |  | 241 | 0.13423
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.047147 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 651 |  |  |  |  | -0.18617 | 0 | 0.61576 | 0.74999 |  |  |  |  | 242 | 0.13423
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.047147 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 564 |  |  |  |  | -0.18617 | 0 | 0.61576 | 0.74999 |  |  |  |  | 243 | 0.13423
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.047147 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 603 |  |  |  |  | -0.18617 | 0 | 0.61576 | 0.74999 |  |  |  |  | 244 | 0.13423
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.04705 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.18608 | 167.7 | 167.7 |  |  |  |  | -0.18608 | -31.2052 | 0.62369 | 0.75568 |  |  |  |  | 245 | 0.13423
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.04705 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.18608 | 166.4 | 166.4 |  |  |  |  | -0.18608 | -30.9633 | 0.63155 | 0.76133 |  |  |  |  | 246 | 0.13423
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.04705 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.18608 | 252.4 | 252.4 |  |  |  |  | -0.18608 | -46.966 | 0.64347 | 0.76989 |  |  |  |  | 247 | 0.13423
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.045432 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.18446 | 0 | 0 |  |  |  |  | -0.18446 | 0 | 0.64347 | 0.76989 |  |  |  |  | 248 | 0.13199
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.045218 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.18425 | 166 | 166 |  |  |  |  | -0.18425 | -30.5848 | 0.65132 | 0.77547 |  |  |  |  | 249 | 0.12978
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.045218 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.18425 | 166 | 166 |  |  |  |  | -0.18425 | -30.5848 | 0.65916 | 0.78105 |  |  |  |  | 250 | 0.12642
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.045218 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.18425 | 248 | 248 |  |  |  |  | -0.18425 | -45.6929 | 0.67088 | 0.78938 |  |  |  |  | 251 | 0.12642
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.045218 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.18425 | 546 | 546 |  |  |  |  | -0.18425 | -100.5982 | 0.69667 | 0.80773 |  |  |  |  | 252 | 0.12415
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.045218 | 584.4 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.18425 | 0 | 654 |  |  |  |  | -0.18425 | 0 | 0.69667 | 0.80773 |  |  |  |  | 253 | 0.12189
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.045218 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.18425 | 13 | 13 |  |  |  |  | -0.18425 | -2.3952 | 0.69729 | 0.80817 |  |  |  |  | 254 | 0.11851
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.037654 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 255 | 0.11106
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.037654 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 256 | 0.11106
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.037654 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 257 | 0.11088
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.037654 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 258 | 0.11088
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.037654 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 259 | 0.11088
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.037654 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 260 | 0.11088
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.037654 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 261 | 0.11088
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.037654 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 262 | 0.11088
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.037654 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 263 | 0.11088
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.037654 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 264 | 0.11088
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.037654 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 265 | 0.11088
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.037654 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 266 | 0.11088
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.037654 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 267 | 0.11088
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.037654 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 268 | 0.11088
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.037654 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 | 0.69729 | 0.80817 |  |  |  |  | 269 | 0.11088
48772 | PHR_GN2_2 | MB | Houston | YES | -0.034448 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.17348 | 0 | 0 |  |  |  |  | -0.17348 | 0 | 0.69729 | 0.80817 |  |  |  |  | 270 | 0.11088
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.032212 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | 0.69729 | 0.80817 |  |  |  |  | 271 | 0.11088
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.032212 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | 0.69729 | 0.80817 |  |  |  |  | 272 | 0.11088
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.032212 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | 0.69729 | 0.80817 |  |  |  |  | 273 | 0.11088
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.032212 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | 0.69729 | 0.80817 |  |  |  |  | 274 | 0.11088
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.032212 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 | 0.69729 | 0.80817 |  |  |  |  | 275 | 0.11088
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.031354 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 | 0.69729 | 0.80817 |  |  |  |  | 276 | 0.11088
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.031354 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 | 0.69729 | 0.80817 |  |  |  |  | 277 | 0.11088
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.031354 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 | 0.69729 | 0.80817 |  |  |  |  | 278 | 0.11088
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.031354 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 | 0.69729 | 0.80817 |  |  |  |  | 279 | 0.11088
48691 | GBY_73741085 | B | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 | 0.69951 | 0.80962 |  |  |  |  | 280 | 0.11088
48691 | GBY_73741085 | A | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 | 0.70173 | 0.81107 |  |  |  |  | 281 | 0.11088
48692 | GBY_81821075 | D | Houston | YES | -0.03027 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.1693 | 55 | 55 |  |  |  |  | -0.1693 | -9.3114 | 0.70433 | 0.81277 |  |  |  |  | 282 | 0.11088
48692 | GBY_81821075 | C | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 | 0.70655 | 0.81422 |  |  |  |  | 283 | 0.11011
48693 | GBY_83841065 | F | Houston | YES | -0.03027 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.1693 | 54 | 54 |  |  |  |  | -0.1693 | -9.1421 | 0.7091 | 0.81588 |  |  |  |  | 284 | 0.10934
48693 | GBY_83841065 | E | Houston | YES | -0.03027 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.1693 | 57 | 57 |  |  |  |  | -0.1693 | -9.65 | 0.71179 | 0.81764 |  |  |  |  | 285 | 0.10844
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.029744 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.16877 | 0 | 0 |  |  |  |  | -0.16877 | 0 | 0.71179 | 0.81764 |  |  |  |  | 286 | 0.10767
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.029744 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.16877 | 0 | 0 |  |  |  |  | -0.16877 | 0 | 0.71179 | 0.81764 |  |  |  |  | 287 | 0.10679
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.029327 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.16835 | 163.2 | 163.2 |  |  |  |  | -0.16835 | -27.4755 | 0.7195 | 0.82266 |  |  |  |  | 288 | 0.10585
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.029327 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.16835 | 157.1 | 157.1 |  |  |  |  | -0.16835 | -26.4485 | 0.72692 | 0.82748 |  |  |  |  | 289 | 0.10585
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.029327 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.16835 | 157.5 | 157.5 |  |  |  |  | -0.16835 | -26.5159 | 0.73436 | 0.83231 |  |  |  |  | 290 | 0.10585
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.029327 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.16835 | 157 | 157 |  |  |  |  | -0.16835 | -26.4317 | 0.74178 | 0.83714 |  |  |  |  | 291 | 0.10315
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.029327 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.16835 | 282 | 282 |  |  |  |  | -0.16835 | -47.476 | 0.7551 | 0.84579 |  |  |  |  | 292 | 0.10056
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.028932 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.16796 | 0 | 0 |  |  |  |  | -0.16796 | 0 | 0.7551 | 0.84579 |  |  |  |  | 293 | 0.09795
48855 | SRB_GT211035 | B1 | Houston | YES | -0.02853 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.16756 | 18 | 18 |  |  |  |  | -0.16756 | -3.016 | 0.75596 | 0.84634 |  |  |  |  | 294 | 0.095353
48855 | SRB_GT211035 | B2 | Houston | YES | -0.02853 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.16756 | 12 | 12 |  |  |  |  | -0.16756 | -2.0107 | 0.75652 | 0.84671 |  |  |  |  | 295 | 0.090689
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.028508 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.16754 | 176 | 176 |  |  |  |  | -0.16754 | -29.4863 | 0.76484 | 0.85209 |  |  |  |  | 296 | 0.090689
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.028478 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.16751 | 165 | 165 |  |  |  |  | -0.16751 | -27.6384 | 0.77263 | 0.85713 |  |  |  |  | 297 | 0.090388
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.028468 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.1675 | 0 | 0 |  |  |  |  | -0.1675 | 0 | 0.77263 | 0.85713 |  |  |  |  | 298 | 0.090188
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.028468 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.1675 | 0 | 0 |  |  |  |  | -0.1675 | 0 | 0.77263 | 0.85713 |  |  |  |  | 299 | 0.08725
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.028372 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.1674 | 213 | 213 |  |  |  |  | -0.1674 | -35.6561 | 0.7827 | 0.86363 |  |  |  |  | 300 | 0.084495
48845 | SOL_GT1 | 1 | Houston | YES | -0.028365 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.16739 | 16.2 | 16.2 |  |  |  |  | -0.16739 | -2.7118 | 0.78346 | 0.86413 |  |  |  |  | 301 | 0.084495
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.02836 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 | 0.78346 | 0.86413 |  |  |  |  | 302 | 0.084495
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.02836 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 | 0.78346 | 0.86413 |  |  |  |  | 303 | 0.080935
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.02836 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 | 0.78346 | 0.86413 |  |  |  |  | 304 | 0.080664
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.02836 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 | 0.78346 | 0.86413 |  |  |  |  | 305 | 0.080664
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.028349 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.16738 | 228 | 228 |  |  |  |  | -0.16738 | -38.1619 | 0.79423 | 0.87109 |  |  |  |  | 306 | 0.080664
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.028348 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 | 0.79423 | 0.87109 |  |  |  |  | 307 | 0.080664
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.028348 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 | 0.79423 | 0.87109 |  |  |  |  | 308 | 0.080664
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.028348 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 | 0.79423 | 0.87109 |  |  |  |  | 309 | 0.076852
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.027787 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 | 0.79423 | 0.87109 |  |  |  |  | 310 | 0.076852
48821 | SHELLG2 | 2 | Houston | YES | -0.027787 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 | 0.79423 | 0.87109 |  |  |  |  | 311 | 0.076852
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.027787 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 | 0.79423 | 0.87109 |  |  |  |  | 312 | 0.076852
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.027787 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 | 0.79423 | 0.87109 |  |  |  |  | 313 | 0.076852
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.027012 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.16604 | 0 | 0 |  |  |  |  | -0.16604 | 0 | 0.79423 | 0.87109 |  |  |  |  | 314 | 0.076852
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.026832 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.16586 | 42 | 42 |  |  |  |  | -0.16586 | -6.9661 | 0.79622 | 0.87236 |  |  |  |  | 315 | 0.076852
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.026832 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.16586 | 42 | 42 |  |  |  |  | -0.16586 | -6.9661 | 0.7982 | 0.87363 |  |  |  |  | 316 | 0.076852
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.026832 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.16586 | 39 | 39 |  |  |  |  | -0.16586 | -6.4685 | 0.80004 | 0.87481 |  |  |  |  | 317 | 0.076852
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.026832 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.16586 | 39 | 39 |  |  |  |  | -0.16586 | -6.4685 | 0.80189 | 0.87599 |  |  |  |  | 318 | 0.076138
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.026716 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.16574 | 0 | 0 |  |  |  |  | -0.16574 | 0 | 0.80189 | 0.87599 |  |  |  |  | 319 | 0.075424
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.026716 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.16574 | 0 | 0 |  |  |  |  | -0.16574 | 0 | 0.80189 | 0.87599 |  |  |  |  | 320 | 0.074761
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.025572 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.1646 | 107 | 107 |  |  |  |  | -0.1646 | -17.6122 | 0.80694 | 0.8792 |  |  |  |  | 321 | 0.074099
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.025572 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.1646 | 108 | 108 |  |  |  |  | -0.1646 | -17.7768 | 0.81204 | 0.88244 |  |  |  |  | 322 | 0.074099
48875 | THW_3132 | A | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 | 0.81464 | 0.88409 |  |  |  |  | 323 | 0.074099
48875 | THW_3132 | B | Houston | YES | -0.025572 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.1646 | 53 | 53 |  |  |  |  | -0.1646 | -8.7238 | 0.81715 | 0.88568 |  |  |  |  | 324 | 0.072255
48877 | THW_3334 | C | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 | 0.81975 | 0.88733 |  |  |  |  | 325 | 0.070395
48877 | THW_3334 | D | Houston | YES | -0.025572 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.1646 | 57 | 57 |  |  |  |  | -0.1646 | -9.3822 | 0.82244 | 0.88904 |  |  |  |  | 326 | 0.069447
48879 | THW_4142 | E | Houston | YES | -0.025572 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.1646 | 56 | 56 |  |  |  |  | -0.1646 | -9.2176 | 0.82508 | 0.89072 |  |  |  |  | 327 | 0.068534
48879 | THW_4142 | F | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 | 0.82768 | 0.89238 |  |  |  |  | 328 | 0.067587
48881 | THW_4344 | G | Houston | YES | -0.025572 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.1646 | 58 | 58 |  |  |  |  | -0.1646 | -9.5468 | 0.83042 | 0.89412 |  |  |  |  | 329 | 0.066605
48881 | THW_4344 | H | Houston | YES | -0.025572 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.1646 | 58 | 58 |  |  |  |  | -0.1646 | -9.5468 | 0.83316 | 0.89586 |  |  |  |  | 330 | 0.06564
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.024639 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.16367 | 746 | 746 |  |  |  |  | -0.16367 | -122.0954 | 0.86841 | 0.91812 |  |  |  |  | 331 | 0.064693
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.024179 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.16321 | 12 | 12 |  |  |  |  | -0.16321 | -1.9585 | 0.86898 | 0.91848 |  |  |  |  | 332 | 0.063694
49803 | EXN_15GT | 1 | Houston | YES | -0.024016 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 333 | 0.062695
49804 | EXN_16GT | 2 | Houston | YES | -0.024016 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 334 | 0.049717
49805 | EXN_17GT | 3 | Houston | YES | -0.024016 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 335 | 0.049507
49826 | EXN938GT | 5 | Houston | YES | -0.024016 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 336 | 0.049507
49828 | EXN941GT | 10 | Houston | YES | -0.024016 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 337 | 0.049507
49829 | EXN942GT | 11 | Houston | YES | -0.024016 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 338 | 0.049507
49830 | EXN943GT | 12 | Houston | YES | -0.024016 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 339 | 0.049507
49831 | EXN944GT | 13 | Houston | YES | -0.024016 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 340 | 0.049507
49832 | EXN945GT | 9 | Houston | YES | -0.024016 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 341 | 0.049507
49837 | EXN_GT | 4 | Houston | YES | -0.024016 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 342 | 0.049507
49838 | EXN_14GT | 14 | Houston | YES | -0.024016 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 | 0.86898 | 0.91848 |  |  |  |  | 343 | 0.049507
48651 | EP_1_2 | 1 | Houston | YES | -0.023414 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.16244 | 0 | 0 |  |  |  |  | -0.16244 | 0 | 0.86898 | 0.91848 |  |  |  |  | 344 | 0.049507
48651 | EP_1_2 | 2 | Houston | YES | -0.023414 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.16244 | 0 | 0 |  |  |  |  | -0.16244 | 0 | 0.86898 | 0.91848 |  |  |  |  | 345 | 0.049507
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.023395 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.16242 | 0 | 0 |  |  |  |  | -0.16242 | 0 | 0.86898 | 0.91848 |  |  |  |  | 346 | 0.049507
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.023373 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.1624 | 744 | 744 |  |  |  |  | -0.1624 | -120.8262 | 0.90413 | 0.94052 |  |  |  |  | 347 | 0.049507
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.023354 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | 0.90413 | 0.94052 |  |  |  |  | 348 | 0.049507
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.023354 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | 0.90413 | 0.94052 |  |  |  |  | 349 | 0.049507
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.023354 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | 0.90413 | 0.94052 |  |  |  |  | 350 | 0.036392
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.023354 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | 0.90413 | 0.94052 |  |  |  |  | 351 | 0.036392
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.023354 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | 0.90413 | 0.94052 |  |  |  |  | 352 | 0.036392
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.023354 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | 0.90413 | 0.94052 |  |  |  |  | 353 | 0.036392
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.023354 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 | 0.90413 | 0.94052 |  |  |  |  | 354 | 0.036392
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.02302 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.16205 | 0 | 0 |  |  |  |  | -0.16205 | 0 | 0.90413 | 0.94052 |  |  |  |  | 355 | 0.036392
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 | 0.91225 | 0.9456 |  |  |  |  | 356 | 0.036392
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 | 0.92038 | 0.95067 |  |  |  |  | 357 | 0.036392
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 | 0.9285 | 0.95575 |  |  |  |  | 358 | 0.036392
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.021791 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.16082 | 162.8 | 162.8 |  |  |  |  | -0.16082 | -26.1813 | 0.9362 | 0.96053 |  |  |  |  | 359 | 0.033344
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.021791 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.16082 | 161.4 | 161.4 |  |  |  |  | -0.16082 | -25.9561 | 0.94382 | 0.96526 |  |  |  |  | 360 | 0.030295
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.021791 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.16082 | 158.9 | 158.9 |  |  |  |  | -0.16082 | -25.5541 | 0.95133 | 0.96992 |  |  |  |  | 361 | 0.027246
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.021791 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.16082 | 269.2 | 269.2 |  |  |  |  | -0.16082 | -43.2924 | 0.96405 | 0.97781 |  |  |  |  | 362 | 0.02433
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.021457 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.16048 | 398 | 398 |  |  |  |  | -0.16048 | -63.8729 | 0.98285 | 0.98946 |  |  |  |  | 363 | 0.021438
48885 | THW_5152 | B | Houston | YES | -0.020999 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16003 | 59 | 59 |  |  |  |  | -0.16003 | -9.4416 | 0.98564 | 0.99119 |  |  |  |  | 364 | 0.018591
48885 | THW_5152 | A | Houston | YES | -0.020999 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16003 | 58 | 58 |  |  |  |  | -0.16003 | -9.2816 | 0.98838 | 0.99288 |  |  |  |  | 365 | 0.013768
48886 | THW_5354 | D | Houston | YES | -0.020999 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16003 | 58 | 58 |  |  |  |  | -0.16003 | -9.2816 | 0.99112 | 0.99457 |  |  |  |  | 366 | 0.0066134
48886 | THW_5354 | C | Houston | YES | -0.020999 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16003 | 57 | 57 |  |  |  |  | -0.16003 | -9.1215 | 0.99381 | 0.99623 |  |  |  |  | 367 | 0.0055478
48887 | THW_5556 | E | Houston | YES | -0.020999 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16003 | 59 | 59 |  |  |  |  | -0.16003 | -9.4416 | 0.9966 | 0.99796 |  |  |  |  | 368 | 0.0045003
48887 | THW_5556 | F | Houston | YES | -0.020999 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16003 | 57 | 57 |  |  |  |  | -0.16003 | -9.1215 | 0.99929 | 0.99962 |  |  |  |  | 369 | 0.0034528
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.014605 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | 0.99929 | 0.99962 |  |  |  |  | 370 | 0.0024234
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.014605 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | 0.99929 | 0.99962 |  |  |  |  | 371 | 0.0013578
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.014605 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | 0.99929 | 0.99962 |  |  |  |  | 372 | 0.00032835
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.014605 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | 0.99929 | 0.99962 |  |  |  |  | 373 | 0.00032835
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.014605 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | 0.99929 | 0.99962 |  |  |  |  | 374 | 0.00032835
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.13903 | 15 | 15 |  |  | 0 | 15 | -0.13903 | -2.0854 | 1 | 1 |  |  |  |  | 375 | 0.00032835
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | 1 | 1 |  |  |  |  | 376 | 0.00032835
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | 1 | 1 |  |  |  |  | 377 | 0.00032835
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | 1 | 1 |  |  |  |  | 378 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | 1 | 1 |  |  |  |  | 379 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | 1 | 1 |  |  |  |  | 380 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | 1 | 1 |  |  |  |  | 381 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | 1 | 1 |  |  |  |  | 382 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | 1 | 1 |  |  |  |  | 383 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.13903 | 0 | 0 |  |  |  |  | -0.13903 | 0 | 1 | 1 |  |  |  |  | 384 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.037558 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.21749 | 48 | 48 | 1.8028 | 48 |  |  | 0.21749 | 10.4397 | [6 empty] | 385 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.037558 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.21749 | 46 | 46 | 1.7277 | 46 |  |  | 0.21749 | 10.0048 | [6 empty] | 386 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.037558 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.21749 | 105 | 105 | 3.9436 | 105 |  |  | 0.21749 | 22.8369 | [6 empty] | 387 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | 0.042125 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 | [6 empty] | 388 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.042125 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 | [6 empty] | 389 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.042125 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.22206 | 17 | 17 | 0.71613 | 17 |  |  | 0.22206 | 3.775 | [6 empty] | 390 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | 0.042125 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.042125 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.043221 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.22316 | 154.2 | 154.2 | 6.6647 | 154.2 |  |  | 0.22316 | 34.4109
48672 | FTR_GT2_5110 | 2 | North | YES | 0.043221 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.22316 | 159 | 159 | 6.8721 | 159 |  |  | 0.22316 | 35.4821
48673 | FTR_GT3_5085 | 3 | North | YES | 0.043221 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.22316 | 158 | 158 | 6.8289 | 158 |  |  | 0.22316 | 35.2589
48674 | FTR_CN4_5095 | 4 | North | YES | 0.043221 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.22316 | 380 | 380 | 16.424 | 380 |  |  | 0.22316 | 84.7999
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.043803 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.22374 | 32 | 32 | 1.4017 | 32 |  |  | 0.22374 | 7.1597
990 | GIBN_CREK_G1 | 1 | North | YES | 0.054087 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.23402 | 0 | 463 | 25.0423 | 463 |  |  | 0.23402 | 108.3529
60202 | FRNDDRCS | F | West | YES | 0.080216 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.26015 | 0 | 0 |  |  |  |  | 0.26015 | 0
39960 | TNTNPONE_18 | 1 | North | YES | 0.091914 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.27185 | 0 | 152.3 | 13.9985 | 152.3 |  |  | 0.27185 | 41.4029
39970 | TNTNPONE_28 | 1 | North | YES | 0.091914 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.27185 | 0 | 153 | 14.0628 | 153 |  |  | 0.27185 | 41.5931
60018 | DSKY1 | 1 | West | YES | 0.10039 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.28032 | 0 | 84 |  |  |  |  | 0.28032 | 23.5472
60000 | DSKY2 | 1 | West | YES | 0.10065 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.28059 | 0 | 76.5 |  |  |  |  | 0.28059 | 21.4653
60017 | ORNNWP1 | 1 | West | YES | 0.10169 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.28163 | 0 | 80 |  |  |  |  | 0.28163 | 22.5305
38437 | TNSRBNMESA9 | 1 | West | YES | 0.10557 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.2855 | 0 | 150 |  |  |  |  | 0.2855 | 42.8254
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.10568 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.28562 | 0 | 80 |  |  |  |  | 0.28562 | 22.8493
60016 | WOODWRD11A | 1 | West | YES | 0.1057 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.28564 | 0 | 80 |  |  |  |  | 0.28564 | 22.8513
6016 | SWMESA | 1 | West | YES | 0.10584 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.28577 | 0 | 75 |  |  |  |  | 0.28577 | 21.433
60003 | KING_NE1A | 1 | West | YES | 0.10584 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28577 | 0 | 80 |  |  |  |  | 0.28577 | 22.8619
60005 | KING_SE1A | 1 | West | YES | 0.10584 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.28577 | 0 | 40 |  |  |  |  | 0.28577 | 11.4309
60201 | RIO DRCS | F | West | YES | 0.10605 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.28599 | 0 | 0 |  |  |  |  | 0.28599 | 0
60007 | KING_SW1A | 1 | West | YES | 0.10656 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.2865 | 0 | 80 |  |  |  |  | 0.2865 | 22.9199
60019 | KING_NW1A | 1 | West | YES | 0.10656 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.2865 | 0 | 80 |  |  |  |  | 0.2865 | 22.9199
48721 | LEG_1___1 | 1 | North | YES | 0.10828 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.28822 | 0 | 827 | 89.55 | 827 |  |  | 0.28822 | 238.3576
48722 | LEG_2___2 | 2 | North | YES | 0.10828 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.28822 | 0 | 819 | 88.6838 | 819 |  |  | 0.28822 | 236.0519
60057 | CALLAHAN1A | 1 | West | YES | 0.11624 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.29618 | 0 | 114 |  |  |  |  | 0.29618 | 33.7646
1349 | WESTXWIN_1G | 1 | West | YES | 0.11655 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.29649 | 0 | 6.6 |  |  |  |  | 0.29649 | 1.9568
1350 | NWPWRG1_1G | 1 | West | YES | 0.11655 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.29649 | 0 | 34.3 |  |  |  |  | 0.29649 | 10.1695
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.1176 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.29754 | 0 | 112.5 |  |  |  |  | 0.29754 | 33.4732
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.1176 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 149.5 |  |  |  |  | 0.29754 | 44.4822
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.1176 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 186 |  |  |  |  | 0.29754 | 55.3424
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.1176 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 214.5 |  |  |  |  | 0.29754 | 63.8223
1002 | PBCTAGE_1G | A | West | YES | 0.11795 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.29788 | 66 | 66 |  |  |  |  | 0.29788 | 19.6603
1003 | PBCTBGE_2G | B | West | YES | 0.11795 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.29788 | 66 | 66 |  |  |  |  | 0.29788 | 19.6603
1004 | PBCTCGE_3G | C | West | YES | 0.11795 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.29788 | 67 | 67 |  |  |  |  | 0.29788 | 19.9581
1005 | PBCTDGE_4G | D | West | YES | 0.11795 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.29788 | 68 | 68 |  |  |  |  | 0.29788 | 20.256
1006 | PBCTEGE_5G | E | West | YES | 0.11795 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.29788 | 67 | 67 |  |  |  |  | 0.29788 | 19.9581
1007 | PB5GEN_6G | 5 | West | YES | 0.11795 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.29788 | 114 | 114 |  |  |  |  | 0.29788 | 33.9586
1008 | PB6GEN_7G | 6 | West | YES | 0.11795 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.29788 | 515 | 515 |  |  |  |  | 0.29788 | 153.4096
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.11806 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.298 | 0 | 35 |  |  |  |  | 0.298 | 10.43
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.11806 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.298 | 0 | 30 |  |  |  |  | 0.298 | 8.94
11147 | NOTREES_1G | 1 | West | YES | 0.11829 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.29823 | 0 | 149 |  |  |  |  | 0.29823 | 44.4359
76031 | L_GASCCR1_1N | W1 | West | YES | 0.11831 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.29825 | 0 | 150 |  |  |  |  | 0.29825 | 44.7374
1320 | BSP 1 | 1 | West | YES | 0.11914 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.29908 | 0 | 0 |  |  |  |  | 0.29908 | 0
1326 | STANTONW_8 | 1 | West | YES | 0.11955 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.29948 | 0 | 100.5 |  |  |  |  | 0.29948 | 30.0982
11020 | TIEHVSG_1G | 1 | West | YES | 0.11967 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.29961 | 208.2 | 208.2 |  |  |  |  | 0.29961 | 62.3783
11021 | TIEHVCG_1G | 1 | West | YES | 0.11967 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.29961 | 142.1 | 142.1 |  |  |  |  | 0.29961 | 42.5742
11022 | TIEHVCG_2G | 1 | West | YES | 0.11967 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.29961 | 132.4 | 132.4 |  |  |  |  | 0.29961 | 39.6681
11023 | TIEHVCG_3G | 1 | West | YES | 0.11967 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.29961 | 137.4 | 137.4 |  |  |  |  | 0.29961 | 41.1661
11024 | TIEHVCG_4G | 1 | West | YES | 0.11967 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.29961 | 147 | 147 |  |  |  |  | 0.29961 | 44.0423
11025 | TIEHVSG_2G | 1 | West | YES | 0.11967 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.29961 | 213.2 | 213.2 |  |  |  |  | 0.29961 | 63.8763
11001 | NAV1CT | 1 | West | YES | 0.11969 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.29963 | 70.4 | 70.4 |  |  |  |  | 0.29963 | 21.0938
11009 | NAV2CT | 1 | West | YES | 0.11969 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.29963 | 71.4 | 71.4 |  |  |  |  | 0.29963 | 21.3934
11011 | NAV3ST | 1 | West | YES | 0.11969 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.29963 | 92.8 | 92.8 |  |  |  |  | 0.29963 | 27.8054
11012 | NAV4CT | 1 | West | YES | 0.11969 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.29963 | 80 | 80 |  |  |  |  | 0.29963 | 23.9702
11013 | NAV5CT | 1 | West | YES | 0.11969 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.29963 | 80 | 80 |  |  |  |  | 0.29963 | 23.9702
11014 | NAV6ST | 1 | West | YES | 0.11969 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.29963 | 115 | 115 |  |  |  |  | 0.29963 | 34.4572
1328 | OCOTILLO_1G | 1 | West | YES | 0.11975 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.29968 | 0 | 58 |  |  |  |  | 0.29968 | 17.3815
1333 | MCDDONAL_8 | 1 | West | YES | 0.12004 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.29998 | 0 | 214.2 |  |  |  |  | 0.29998 | 64.2561
1327 | WILDHRSE_1G | 1 | West | YES | 0.1204 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.30033 | 0 | 120 |  |  |  |  | 0.30033 | 36.0398
1360 | GUNSIGHT_8 | 1 | West | YES | 0.12046 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.30039 | 0 | 120 |  |  |  |  | 0.30039 | 36.047
11320 | COYOTE_1G | 1 | West | YES | 0.12099 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.30092 | 0 | 225 |  |  |  |  | 0.30092 | 67.708
11309 | BULLCREK_2G | 1 | West | YES | 0.1211 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.30104 | 0 | 180 |  |  |  |  | 0.30104 | 54.1866
11310 | BULLCREK_1G | 1 | West | YES | 0.1211 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.30104 | 0 | 180 |  |  |  |  | 0.30104 | 54.1866
1045 | CALENG1G_1G | 1 | West | YES | 0.12114 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.12114 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.12114 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0
60058 | BUFF_GAP1A | 1 | West | YES | 0.12125 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30118 | 0 | 120 |  |  |  |  | 0.30118 | 36.1418
60060 | CIRELLO | 1 | West | YES | 0.12125 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.30118 | 0 | 233 |  |  |  |  | 0.30118 | 70.1753
60063 | BUFF_GAP1B | 1 | West | YES | 0.12125 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.30118 | 0 | 170.2 |  |  |  |  | 0.30118 | 51.2611
60066 | H_HOLLOW1A | 1 | West | YES | 0.12125 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.30118 | 0 | 222 |  |  |  |  | 0.30118 | 66.8623
60068 | HHOLLOW21A | 1 | West | YES | 0.12125 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 184 |  |  |  |  | 0.30118 | 55.4174
60070 | HHOLLOW31A | 1 | West | YES | 0.12125 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 224 |  |  |  |  | 0.30118 | 67.4647
60072 | HHOLLOW41A | 1 | West | YES | 0.12125 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 115 |  |  |  |  | 0.30118 | 34.6359
1058 | LONGSHORE_5 | 1 | West | YES | 0.12148 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.30141 | 0 | 150 |  |  |  |  | 0.30141 | 45.212
1058 | LONGSHORE_5 | 2 | West | YES | 0.12148 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.30141 | 0 | 220 |  |  |  |  | 0.30141 | 66.311
11065 | ELBOWCK_1G | 1 | West | YES | 0.12148 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.30141 | 0 | 121.9 |  |  |  |  | 0.30141 | 36.7423
1037 | MORGAN5G_5G | 5 | West | YES | 0.12167 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.3016 | 137 | 137 |  |  |  |  | 0.3016 | 41.3198
1039 | MRGNAG_1G | A | West | YES | 0.12167 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.3016 | 69 | 69 |  |  |  |  | 0.3016 | 20.8107
1040 | MRGNBG_2G | B | West | YES | 0.12167 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.3016 | 71 | 71 |  |  |  |  | 0.3016 | 21.4139
1041 | MRGNCG_3G | C | West | YES | 0.12167 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.3016 | 70 | 70 |  |  |  |  | 0.3016 | 21.1123
1042 | MRGNDG_4G | D | West | YES | 0.12167 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.3016 | 68 | 68 |  |  |  |  | 0.3016 | 20.5091
1043 | MRGNEG_5G | E | West | YES | 0.12167 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.3016 | 70 | 70 |  |  |  |  | 0.3016 | 21.1123
1044 | MRGNFG_6G | F | West | YES | 0.12167 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.3016 | 66 | 66 |  |  |  |  | 0.3016 | 19.9059
6637 | SNYDERW1A | 1 | West | YES | 0.12174 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.30168 | 0 | 63 |  |  |  |  | 0.30168 | 19.0059
1068 | SCURRYCW_1G | 1 | West | YES | 0.12187 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.30181 | 0 | 141 |  |  |  |  | 0.30181 | 42.5553
1073 | SCURRYCW_2G | 2 | West | YES | 0.12187 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.30181 | 0 | 120 |  |  |  |  | 0.30181 | 36.2173
1061 | CIELOGEN_1G | 1 | West | YES | 0.12189 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.30183 | 0 | 99 |  |  |  |  | 0.30183 | 29.8811
1062 | CIELOGEN_2G | 1 | West | YES | 0.12189 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.30183 | 0 | 61 |  |  |  |  | 0.30183 | 18.4116
1069 | KINDERMG_1G | 1 | West | YES | 0.12189 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.12189 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.12189 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0
36998 | RDCNYNG1 | 1 | West | YES | 0.12222 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.30215 | 0 | 84 |  |  |  |  | 0.30215 | 25.381
1343 | TRENTIPP_8 | 1 | West | YES | 0.12229 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.30223 | 0 | 150 |  |  |  |  | 0.30223 | 45.3338
1354 | AEPWIND_8 | 1 | West | YES | 0.12229 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.30223 | 0 | 101 |  |  |  |  | 0.30223 | 30.5248
6407 | TURKTRAK1A | 1 | West | YES | 0.12258 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.30252 | 0 | 169.5 |  |  |  |  | 0.30252 | 51.2771
71051 | L_BITTCR1_1N | W1 | West | YES | 0.12356 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 37.5 |  |  |  |  | 0.3035 | 11.3812
71054 | L_SWEETW1_1N | W1 | West | YES | 0.12356 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 107.5 |  |  |  |  | 0.3035 | 32.6262
71057 | L_SWEETW1_2N | W1 | West | YES | 0.12356 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 135 |  |  |  |  | 0.3035 | 40.9725
71059 | L_SWEETW1_3N | W1 | West | YES | 0.12356 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 119 |  |  |  |  | 0.3035 | 36.1165
71060 | L_SWEETW1_4N | W1 | West | YES | 0.12356 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 105 |  |  |  |  | 0.3035 | 31.8675
71061 | L_SWEETW1_5N | W1 | West | YES | 0.12356 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 80.5 |  |  |  |  | 0.3035 | 24.4317
6144 | MCADOO1A | 1 | West | YES | 0.12365 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.30358 | 0 | 150 |  |  |  |  | 0.30358 | 45.5372
11056 | ROSCOE_1G | 1 | West | YES | 0.12374 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.30368 | 0 | 209 |  |  |  |  | 0.30368 | 63.4693
11057 | CHAMPION_1G | 1 | West | YES | 0.12374 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.30368 | 0 | 126.5 |  |  |  |  | 0.30368 | 38.4156
11058 | PYRON_1G | 1 | West | YES | 0.12374 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.30368 | 0 | 249 |  |  |  |  | 0.30368 | 75.6165
11059 | INADALE_1G | 1 | West | YES | 0.12374 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.30368 | 0 | 197 |  |  |  |  | 0.30368 | 59.8251
1416 | SWETWATR_1G | 1 | West | YES | 0.12461 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.30455 | 30 | 30 |  |  |  |  | 0.30455 | 9.1364
1417 | SWETWATR_2G | 2 | West | YES | 0.12461 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.30455 | 72 | 72 |  |  |  |  | 0.30455 | 21.9274
1418 | SWETWATR_3G | 3 | West | YES | 0.12461 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.30455 | 68 | 68 |  |  |  |  | 0.30455 | 20.7092
1419 | SWETWATR_4G | 4 | West | YES | 0.12461 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.30455 | 61 | 61 |  |  |  |  | 0.30455 | 18.5773
60081 | WHRLWIND1A | 1 | West | YES | 0.12555 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.30549 | 0 | 60 |  |  |  |  | 0.30549 | 18.3291
1437 | MESQUITW_1G | 1 | North | YES | 0.12873 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.30867 | 0 | 400 | 51.4928 | 400 |  |  | 0.30867 | 123.4675
1438 | MESQUITW_2G | 1 | North | YES | 0.12874 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.30868 | 0 | 236 | 30.3829 | 236 |  |  | 0.30868 | 72.8479
3381 | BBRN_1G | 1 | North | YES | 0.12876 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.30869 | 0 | 618 | 79.5718 | 618 |  |  | 0.30869 | 190.7727
3382 | BBRN_2G | 2 | North | YES | 0.12876 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.30869 | 0 | 589 | 75.8379 | 589 |  |  | 0.30869 | 181.8206
1643 | SLSTR1PP_1G | 1 | North | YES | 0.12968 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.30961 | 0 | 60 | 7.7806 | 60 |  |  | 0.30961 | 18.5768
13131 | CALFREST_1G | 1 | North | YES | 0.13002 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.30996 | 150.7 | 150.7 | 19.5945 | 150.7 |  |  | 0.30996 | 46.7109
13132 | CALFREST_2G | 2 | North | YES | 0.13002 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.30996 | 151 | 151 | 19.6335 | 151 |  |  | 0.30996 | 46.8039
13133 | CALFREST_3G | 3 | North | YES | 0.13002 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.30996 | 177.4 | 177.4 | 23.0661 | 177.4 |  |  | 0.30996 | 54.9868
13134 | CALFREST_4G | 4 | North | YES | 0.1302 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.31014 | 151.5 | 151.5 | 19.7255 | 151.5 |  |  | 0.31014 | 46.9859
13135 | CALFREST_5G | 5 | North | YES | 0.1302 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.31014 | 152.3 | 152.3 | 19.8296 | 152.3 |  |  | 0.31014 | 47.234
13136 | CALFREST_6G | 6 | North | YES | 0.1302 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.31014 | 177.5 | 177.5 | 23.1107 | 177.5 |  |  | 0.31014 | 55.0494
1442 | COKFIELD_5 | 1 | North | YES | 0.13041 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.31035 | 0 | 165 | 21.5178 | 165 |  |  | 0.31035 | 51.2074
6100 | OKLA7A | EQ | West | YES | 0.13155 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.31148 | 0 | 0 |  |  |  |  | 0.31148 | 0
6752 | OKLA0A | 1 | West | YES | 0.13155 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.31148 | 0 | 649.7 |  |  |  |  | 0.31148 | 202.3709
3107 | STRYKER_1G | 1 | North | YES | 0.13427 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.31421 | 182 | 182 | 24.4371 | 182 |  |  | 0.31421 | 57.1856
3108 | STRYKER_2G | 2 | North | YES | 0.13427 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.31421 | 484 | 484 | 64.9867 | 484 |  |  | 0.31421 | 152.076
1433 | GRHAMSES_1G | 1 | North | YES | 0.13454 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.31448 | 242 | 242 | 32.5592 | 242 |  |  | 0.31448 | 76.1038
3309 | ASPN_G | 1 | North | YES | 0.13498 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.31491 | 50 | 50 | 6.7489 | 50 |  |  | 0.31491 | 15.7457
3348 | CHAMPION_1G | MB | North | YES | 0.13501 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.31495 | 0 | 0 | 0 | 0 |  |  | 0.31495 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.13562 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.1357 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.31563 | 366 | 366 | 49.6655 | 366 |  |  | 0.31563 | 115.5223
13116 | TGATEWAY_1G | 1 | North | YES | 0.13575 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.31569 | 151 | 151 | 20.4986 | 151 |  |  | 0.31569 | 47.669
13117 | TGATEWAY_2G | 2 | North | YES | 0.13575 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.31569 | 130 | 130 | 17.6478 | 130 |  |  | 0.31569 | 41.0395
13118 | TGATEWAY_3G | 3 | North | YES | 0.13575 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.31569 | 148 | 148 | 20.0913 | 148 |  |  | 0.31569 | 46.7219
13119 | TGATEWAY_4G | 4 | North | YES | 0.13575 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.31569 | 399 | 399 | 54.165 | 399 |  |  | 0.31569 | 125.9598
3097 | MARTLAKE_1G | 1 | North | YES | 0.13627 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 790 | 107.6549 | 790 |  |  | 0.31621 | 249.8048
3098 | MARTLAKE_2G | 2 | North | YES | 0.13627 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 795 | 108.3362 | 795 |  |  | 0.31621 | 251.3859
3099 | MARTLAKE_3G | 3 | North | YES | 0.13627 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 804 | 109.5627 | 804 |  |  | 0.31621 | 254.2317
3126 | TRINIDAD_6G | 1 | North | YES | 0.13717 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.31711 | 224 | 224 | 30.727 | 224 |  |  | 0.31711 | 71.0328
1600 | BARTNWND_1G | 1 | North | YES | 0.13725 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.31718 | 0 | 120 | 16.4696 | 120 |  |  | 0.31718 | 38.062
344 | MRSSHPRD | 1 | North | YES | 0.13746 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.3174 | 0 | 0 | 0 | 0 |  |  | 0.3174 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.13746 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.3174 | 0 | 0 | 0 | 0 |  |  | 0.3174 | 0
332 | RWMILLER01 | 1 | North | YES | 0.13821 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.31814 | 73 | 73 | 10.0892 | 73 |  |  | 0.31814 | 23.2246
333 | RWMILLER02 | 2 | North | YES | 0.13821 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.31814 | 119 | 119 | 16.4468 | 119 |  |  | 0.31814 | 37.8592
334 | RWMILLER03 | 3 | North | YES | 0.13821 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.31814 | 208 | 208 | 28.7473 | 208 |  |  | 0.31814 | 66.1741
335 | RWMILLER04 | 4 | North | YES | 0.13821 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.31814 | 102 | 102 | 14.0972 | 102 |  |  | 0.31814 | 32.4508
336 | RWMILLER05 | 5 | North | YES | 0.13821 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.31814 | 101 | 101 | 13.959 | 101 |  |  | 0.31814 | 32.1326
1453 | WCPWRCO_1G | 1 | North | YES | 0.14048 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.32041 | 204 | 204 | 28.6571 | 204 |  |  | 0.32041 | 65.3642
1454 | WCPWRCO_2G | 2 | North | YES | 0.14048 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.32041 | 204 | 204 | 28.6571 | 204 |  |  | 0.32041 | 65.3642
1455 | WCPWRCO_3G | 3 | North | YES | 0.14048 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.32041 | 242 | 242 | 33.9952 | 242 |  |  | 0.32041 | 77.5399
503 | NTHTEXAS01 | 1 | North | YES | 0.14048 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.32042 | 18 | 18 | 2.5286 | 18 |  |  | 0.32042 | 5.7675
504 | NTHTEXAS02 | 2 | North | YES | 0.14048 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.32042 | 18 | 18 | 2.5286 | 18 |  |  | 0.32042 | 5.7675
505 | NTHTEXAS03 | 3 | North | YES | 0.14048 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.32042 | 38 | 38 | 5.3382 | 38 |  |  | 0.32042 | 12.1758
12411 | FPLEFR1A_G | 1 | North | YES | 0.14061 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32054 | 161 | 161 | 22.6379 | 161 |  |  | 0.32054 | 51.6077
12412 | FPLEFR1B_G | 2 | North | YES | 0.14061 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32054 | 164 | 164 | 23.0597 | 164 |  |  | 0.32054 | 52.5693
12413 | FPLEFR1C_G | 3 | North | YES | 0.14061 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32054 | 164 | 164 | 23.0597 | 164 |  |  | 0.32054 | 52.5693
12414 | FPLEFR1S_G | 4 | North | YES | 0.14061 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.32054 | 414 | 414 | 58.2117 | 414 |  |  | 0.32054 | 132.7055
12421 | FPLEFR2A_G | 1 | North | YES | 0.14061 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.32054 | 162 | 162 | 22.7785 | 162 |  |  | 0.32054 | 51.9282
12422 | FPLEFR2B_G | 2 | North | YES | 0.14061 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32054 | 161 | 161 | 22.6379 | 161 |  |  | 0.32054 | 51.6077
12423 | FPLEFR2C_G | 3 | North | YES | 0.14061 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.32054 | 163 | 163 | 22.9191 | 163 |  |  | 0.32054 | 52.2488
12424 | FPLEFR2S_G | 4 | North | YES | 0.14061 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.32054 | 415 | 415 | 58.3523 | 415 |  |  | 0.32054 | 133.026
580 | JCKCNTY801 | 1 | North | YES | 0.14141 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.32135 | 288 | 288 | 40.7267 | 288 |  |  | 0.32135 | 92.5484
581 | JCKCNTY802 | 2 | North | YES | 0.14141 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32135 | 147 | 147 | 20.7876 | 147 |  |  | 0.32135 | 47.2382
582 | JCKCNTY803 | 3 | North | YES | 0.14141 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32135 | 147 | 147 | 20.7876 | 147 |  |  | 0.32135 | 47.2382
2451 | LKHB1_G | 1 | North | YES | 0.14151 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.32145 | 391 | 391 | 55.332 | 391 |  |  | 0.32145 | 125.6872
2452 | LKHB2_G | 2 | North | YES | 0.14151 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.32145 | 516 | 516 | 73.0212 | 516 |  |  | 0.32145 | 165.8685
948 | STEAM1 | 1 | North | YES | 0.14158 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.32151 | 20 | 20 | 2.8316 | 20 |  |  | 0.32151 | 6.4303
949 | STEAM2 | 1 | North | YES | 0.14158 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.32152 | 26 | 26 | 3.6811 | 26 |  |  | 0.32152 | 8.3594
950 | STEAM3 | 1 | North | YES | 0.14158 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.32152 | 42 | 42 | 5.9463 | 42 |  |  | 0.32152 | 13.5037
837 | NEWMAN_G5 | 1 | North | YES | 0.14174 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.32167 | 40 | 40 | 5.6695 | 40 |  |  | 0.32167 | 12.8669
728 | WOLFRIDGE801 | 1 | North | YES | 0.14175 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.32169 | 0 | 112.5 | 15.947 | 112.5 |  |  | 0.32169 | 36.1899
842 | OLINGER_G1 | 1 | North | YES | 0.14177 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.3217 | 79 | 79 | 11.1996 | 79 |  |  | 0.3217 | 25.4146
843 | OLINGER_G2 | 1 | North | YES | 0.14177 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.3217 | 110 | 110 | 15.5944 | 110 |  |  | 0.3217 | 35.3874
844 | OLINGER_G3 | 1 | North | YES | 0.14177 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.3217 | 150 | 150 | 21.265 | 150 |  |  | 0.3217 | 48.2555
845 | OLINGER_G4 | 1 | North | YES | 0.14177 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.3217 | 76 | 76 | 10.7743 | 76 |  |  | 0.3217 | 24.4495
12440 | PARKD_1SVC8 | 1 | North | YES | 0.1418 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.32173 | 0 | 0 | 0 | 0 |  |  | 0.32173 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.1418 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.32173 | 0 | 0 | 0 | 0 |  |  | 0.32173 | 0
1701 | MOSES_1G | 1 | North | YES | 0.14191 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 558 | 79.1875 | 558 |  |  | 0.32185 | 179.5921
1702 | MOSES_2G | 2 | North | YES | 0.14191 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 579 | 82.1676 | 579 |  |  | 0.32185 | 186.3509
1703 | MOSES_3G | 3 | North | YES | 0.14191 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 808 | 114.6657 | 808 |  |  | 0.32185 | 260.0545
5925 | DCEAST | EQ | North | YES | 0.14191 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.32185 | 0 | 0 | 0 | 0 |  |  | 0.32185 | 0
1675 | PEC_1G | 1 | North | YES | 0.14196 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0
1676 | PEC_2G | 2 | North | YES | 0.14196 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0
1677 | PEC_3G | 3 | North | YES | 0.14196 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.14207 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.32201 | 160 | 160 | 22.7318 | 160 |  |  | 0.32201 | 51.5217
1679 | LAMARPWR_2G | 2 | North | YES | 0.14207 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32201 | 156 | 156 | 22.1635 | 156 |  |  | 0.32201 | 50.2337
1680 | LAMARPWR_3G | 3 | North | YES | 0.14207 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.32201 | 196 | 196 | 27.8465 | 196 |  |  | 0.32201 | 63.1141
1681 | LAMARPWR_4G | 4 | North | YES | 0.14207 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32201 | 156 | 156 | 22.1635 | 156 |  |  | 0.32201 | 50.2337
1682 | LAMARPWR_5G | 5 | North | YES | 0.14207 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.32201 | 157 | 157 | 22.3056 | 157 |  |  | 0.32201 | 50.5557
1683 | LAMARPWR_6G | 6 | North | YES | 0.14207 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.32201 | 198 | 198 | 28.1307 | 198 |  |  | 0.32201 | 63.7581
1689 | VALLEY_3G | 3 | North | YES | 0.14218 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.32212 | 375 | 375 | 53.3182 | 375 |  |  | 0.32212 | 120.7945
11691 | KMICHICT1_G | 1 | North | YES | 0.14218 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32212 | 144 | 144 | 20.4742 | 144 |  |  | 0.32212 | 46.3851
11692 | KMICHICT2_G | 2 | North | YES | 0.14218 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.32212 | 146 | 146 | 20.7586 | 146 |  |  | 0.32212 | 47.0293
11693 | KMICHIST3_G | 3 | North | YES | 0.14218 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.32212 | 312 | 312 | 44.3608 | 312 |  |  | 0.32212 | 100.501
11694 | KMICHICT4_G | 4 | North | YES | 0.14218 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32212 | 144 | 144 | 20.4742 | 144 |  |  | 0.32212 | 46.3851
11695 | KMICHICT5_G | 5 | North | YES | 0.14218 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.32212 | 148 | 148 | 21.0429 | 148 |  |  | 0.32212 | 47.6736
11696 | KMICHIST6_G | 6 | North | YES | 0.14218 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.32212 | 310 | 310 | 44.0764 | 310 |  |  | 0.32212 | 99.8568
1687 | VALLEY_1G | 1 | North | YES | 0.14226 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.3222 | 170 | 170 | 24.1849 | 170 |  |  | 0.3222 | 54.7741
1688 | VALLEY_2G | 2 | North | YES | 0.14226 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.3222 | 527 | 527 | 74.9731 | 527 |  |  | 0.3222 | 169.7997
6948 | DENISNDM | 1 | North | YES | 0.14236 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.3223 | 0 | 0 | 0 | 0 |  |  | 0.3223 | 0
6948 | DENISNDM | 2 | North | YES | 0.14236 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.3223 | 0 | 0 | 0 | 0 |  |  | 0.3223 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.14294 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.32287 | 61 | 61 | 8.7191 | 61 |  |  | 0.32287 | 19.6952
924 | SPENCER_G5 | 1 | North | YES | 0.14294 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.32287 | 66 | 66 | 9.4338 | 66 |  |  | 0.32287 | 21.3096
12322 | ENNSTRAC_1G | 1 | North | YES | 0.14304 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.32298 | 196 | 196 | 28.0358 | 196 |  |  | 0.32298 | 63.3034
12323 | ENNSTRAC_2G | 2 | North | YES | 0.14304 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.32298 | 116 | 116 | 16.5926 | 116 |  |  | 0.32298 | 37.4653
2371 | COLLIN_1G | MB | North | YES | 0.14311 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.32304 | 0 | 0 | 0 | 0 |  |  | 0.32304 | 0
2413 | MTCK6_G | 6 | North | YES | 0.14399 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.32392 | 118 | 118 | 16.9905 | 118 |  |  | 0.32392 | 38.223
2414 | MTCK7_G | 7 | North | YES | 0.14399 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.32392 | 115 | 115 | 16.5585 | 115 |  |  | 0.32392 | 37.2512
2417 | MTCK8_G | 8 | North | YES | 0.14399 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.32392 | 556 | 556 | 80.0568 | 556 |  |  | 0.32392 | 180.1015
2381 | NTHLK1_G | 1 | North | YES | 0.14425 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.32419 | 156 | 156 | 22.5032 | 156 |  |  | 0.32419 | 50.5733
2382 | NTHLK2_G | 2 | North | YES | 0.14425 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.32419 | 181 | 181 | 26.1094 | 181 |  |  | 0.32419 | 58.678
2383 | NTHLK3_G | 3 | North | YES | 0.14425 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.32419 | 329 | 329 | 47.4586 | 329 |  |  | 0.32419 | 106.6577
1898 | COMCHEPK_1G | 1 | North | YES | 0.14433 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.32427 | 0 | 0 | 0 | 0 |  |  | 0.32427 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.14433 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.32427 | 0 | 0 | 0 | 0 |  |  | 0.32427 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.14465 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.32458 | 70 | 70 | 10.1254 | 70 |  |  | 0.32458 | 22.7209
1893 | DECRDOVA_3G | B | North | YES | 0.14465 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.32458 | 69 | 69 | 9.9807 | 69 |  |  | 0.32458 | 22.3963
1894 | DECRDOVA_4G | C | North | YES | 0.14465 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.32458 | 69 | 69 | 9.9807 | 69 |  |  | 0.32458 | 22.3963
1895 | DECRDOVA_5G | D | North | YES | 0.14465 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.32458 | 68 | 68 | 9.8361 | 68 |  |  | 0.32458 | 22.0718
1861 | EAGLEMNT_1G | MB | North | YES | 0.1447 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.1447 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.1447 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.14509 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.32503 | 217.3 | 217.3 | 31.5281 | 217.3 |  |  | 0.32503 | 70.6283
1878 | WLFHOLW_2G | 2 | North | YES | 0.14509 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.32503 | 215.7 | 215.7 | 31.2959 | 215.7 |  |  | 0.32503 | 70.1082
1879 | WLFHOLW_3G | 3 | North | YES | 0.14509 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.32503 | 272.4 | 272.4 | 39.5225 | 272.4 |  |  | 0.32503 | 88.5373
1889 | DECRDOVA_1G | 1 | North | YES | 0.14553 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.32546 | 779 | 779 | 113.3648 | 779 |  |  | 0.32546 | 253.5354
244 | WHITNYDM01 | 1 | North | YES | 0.14569 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32562 | 0 | 0 | 0 | 0 |  |  | 0.32562 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.14569 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32562 | 0 | 0 | 0 | 0 |  |  | 0.32562 | 0
251 | BOSQUESW803 | 2 | North | YES | 0.14734 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.32728 | 150 | 150 | 22.1012 | 150 |  |  | 0.32728 | 49.0916
253 | BOSQUESW804 | 2 | North | YES | 0.14734 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.32728 | 80 | 80 | 11.7873 | 80 |  |  | 0.32728 | 26.1822
366 | JNSNCNTY802 | 1 | North | YES | 0.14753 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.32747 | 0 | 0 | 0 | 0 |  |  | 0.32747 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.14753 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.32747 | 0 | 0 | 0 | 0 |  |  | 0.32747 | 0
1948 | HANDLEY_4G | 4 | North | YES | 0.14783 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.32777 | 435 | 435 | 64.3069 | 435 |  |  | 0.32777 | 142.5794
1947 | HANDLEY_3G | 3 | North | YES | 0.14804 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.32798 | 395 | 395 | 58.4766 | 395 |  |  | 0.32798 | 129.5516
1949 | HANDLEY_5G | 5 | North | YES | 0.14804 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.32798 | 435 | 435 | 64.3983 | 435 |  |  | 0.32798 | 142.6707
1937 | MDLTHELP_5G | 5 | North | YES | 0.15515 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.33509 | 224 | 224 | 34.754 | 224 |  |  | 0.33509 | 75.0599
1938 | MDLTHELP_6G | 6 | North | YES | 0.15515 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.33509 | 226 | 226 | 35.0644 | 226 |  |  | 0.33509 | 75.73
1943 | MDLTHELP_3G | 3 | North | YES | 0.15515 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.33509 | 212 | 212 | 32.8922 | 212 |  |  | 0.33509 | 71.0388
1944 | MDLTHELP_4G | 4 | North | YES | 0.15515 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.33509 | 211 | 211 | 32.7371 | 211 |  |  | 0.33509 | 70.7037
1941 | MDLTHELP_1G | 1 | North | YES | 0.15582 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.33575 | 216.4 | 216.4 | 33.7186 | 216.4 |  |  | 0.33575 | 72.6569
1942 | MDLTHELP_2G | 2 | North | YES | 0.15582 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.33575 | 216.1 | 216.1 | 33.6718 | 216.1 |  |  | 0.33575 | 72.5561
3416 | LAKE_CRK1_G | 1 | North | YES | 0.16701 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.34695 | 75 | 75 | 12.5258 | 75 |  |  | 0.34695 | 26.0211
3417 | LAKE_CRK2_G | 2 | North | YES | 0.16701 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.34695 | 222 | 222 | 37.0764 | 222 |  |  | 0.34695 | 77.0224
238 | BOSQUESW505 | 1 | North | YES | 0.197 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.37693 | 255 | 255 | 50.2342 | 255 |  |  | 0.37693 | 96.1181
239 | BOSQUESW502 | 1 | North | YES | 0.197 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.37693 | 149 | 149 | 29.3526 | 149 |  |  | 0.37693 | 56.1631
247 | BOSQUESW501 | 2 | North | YES | 0.197 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.37693 | 156 | 156 | 30.7315 | 156 |  |  | 0.37693 | 58.8016
3403 | THOUSE_1G | 1 | North | YES | 0.23807 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.41801 | 563 | 563 | 134.0345 | 563 |  |  | 0.41801 | 235.3389
3404 | THOUSE_2G | 2 | North | YES | 0.23807 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.41801 | 807 | 807 | 192.1241 | 807 |  |  | 0.41801 | 337.333
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Bound Gen
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | max of zone correlation | 0.13903 |  |  | Neg PTDF weight | Pos PTDF weight
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.13903 | 15 | 15 |  |  | 0 | 15 | -0.13903 | -2.0854 |  |  |  |  | 0 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 |  |  |  |  | 0 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 |  |  |  |  | 0 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 |  |  | Weighted Shift Factors |  | 0 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 |  |  | North | 0.13903 | 0 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 |  |  | South | -0.17994 | 0 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 |  |  |  |  | 0 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | South |  |  |  | 0 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.13903 | 0 | 0 |  |  | 0 | 0 | -0.13903 | 0 | Line Rating |  | 1072 |  | 0 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.13903 | 0 | 0 |  |  |  |  | -0.13903 | 0 | Impact Counter to Zone: |  | 0 |  | 0 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.014605 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 |  |  | 0% |  | 0 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.014605 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 |  |  |  |  | 0 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.014605 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | North |  |  |  | 0 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.014605 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | Line Rating |  | 1072 |  | 0 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.014605 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.15363 | 0 | 0 |  |  |  |  | -0.15363 | 0 | Impact Counter to Zone: |  | 0 |  | 0 | 0
48885 | THW_5152 | B | Houston | YES | -0.020999 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16003 | 59 | 59 |  |  |  |  | -0.16003 | -9.4416 |  |  | 0% |  | 0 | 0
48887 | THW_5556 | E | Houston | YES | -0.020999 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16003 | 59 | 59 |  |  |  |  | -0.16003 | -9.4416 |  |  |  |  | 0 | 0
48885 | THW_5152 | A | Houston | YES | -0.020999 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16003 | 58 | 58 |  |  |  |  | -0.16003 | -9.2816 |  |  |  |  | 0 | 0
48886 | THW_5354 | D | Houston | YES | -0.020999 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16003 | 58 | 58 |  |  |  |  | -0.16003 | -9.2816 |  |  |  |  | 0 | 0
48886 | THW_5354 | C | Houston | YES | -0.020999 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16003 | 57 | 57 |  |  |  |  | -0.16003 | -9.1215 |  |  |  |  | 0 | 0
48887 | THW_5556 | F | Houston | YES | -0.020999 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16003 | 57 | 57 |  |  |  |  | -0.16003 | -9.1215 |  |  |  |  | 0 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.021457 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.16048 | 398 | 398 |  |  |  |  | -0.16048 | -63.8729 |  |  |  |  | 0 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.021791 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.16082 | 269.2 | 269.2 |  |  |  |  | -0.16082 | -43.2924 |  |  |  |  | 0 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.021791 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.16082 | 162.8 | 162.8 |  |  |  |  | -0.16082 | -26.1813 |  |  |  |  | 0 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.021791 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.16082 | 161.4 | 161.4 |  |  |  |  | -0.16082 | -25.9561 |  |  |  |  | 0 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.021791 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.16082 | 158.9 | 158.9 |  |  |  |  | -0.16082 | -25.5541 |  |  |  |  | 0 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 |  |  |  |  | 0 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 |  |  |  |  | 0 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.02284 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.16187 | 172 | 172 |  |  |  |  | -0.16187 | -27.8413 |  |  |  |  | 0 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.02302 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.16205 | 0 | 0 |  |  |  |  | -0.16205 | 0 |  |  |  |  | 0 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.023354 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 |  |  |  |  | 0 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.023354 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 |  |  |  |  | 0 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.023354 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 |  |  |  |  | 0 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.023354 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 |  |  |  |  | 0 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.023354 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 |  |  |  |  | 0 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.023354 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 |  |  |  |  | 0 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.023354 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.16238 | 0 | 0 |  |  |  |  | -0.16238 | 0 |  |  |  |  | 0 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.023373 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.1624 | 744 | 744 |  |  |  |  | -0.1624 | -120.8262 |  |  |  |  | 0 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.023395 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.16242 | 0 | 0 |  |  |  |  | -0.16242 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.023414 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.16244 | 0 | 0 |  |  |  |  | -0.16244 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.023414 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.16244 | 0 | 0 |  |  |  |  | -0.16244 | 0 |  |  |  |  | 0 | 0
49803 | EXN_15GT | 1 | Houston | YES | -0.024016 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.024016 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.024016 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.024016 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.024016 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.024016 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.024016 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.024016 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.024016 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.024016 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.024016 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.16304 | 0 | 0 |  |  |  |  | -0.16304 | 0 |  |  |  |  | 0 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.024179 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.16321 | 12 | 12 |  |  |  |  | -0.16321 | -1.9585 |  |  |  |  | 0 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.024639 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.16367 | 746 | 746 |  |  |  |  | -0.16367 | -122.0954 |  |  |  |  | 0 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.025572 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.1646 | 108 | 108 |  |  |  |  | -0.1646 | -17.7768 |  |  |  |  | 0 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.025572 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.1646 | 107 | 107 |  |  |  |  | -0.1646 | -17.6122 |  |  |  |  | 0 | 0
48881 | THW_4344 | G | Houston | YES | -0.025572 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.1646 | 58 | 58 |  |  |  |  | -0.1646 | -9.5468 |  |  |  |  | 0 | 0
48881 | THW_4344 | H | Houston | YES | -0.025572 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.1646 | 58 | 58 |  |  |  |  | -0.1646 | -9.5468 |  |  |  |  | 0 | 0
48877 | THW_3334 | D | Houston | YES | -0.025572 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.1646 | 57 | 57 |  |  |  |  | -0.1646 | -9.3822 |  |  |  |  | 0 | 0
48879 | THW_4142 | E | Houston | YES | -0.025572 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.1646 | 56 | 56 |  |  |  |  | -0.1646 | -9.2176 |  |  |  |  | 0 | 0
48875 | THW_3132 | A | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 |  |  |  |  | 0 | 0
48877 | THW_3334 | C | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 |  |  |  |  | 0 | 0
48879 | THW_4142 | F | Houston | YES | -0.025572 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.1646 | 55 | 55 |  |  |  |  | -0.1646 | -9.053 |  |  |  |  | 0 | 0
48875 | THW_3132 | B | Houston | YES | -0.025572 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.1646 | 53 | 53 |  |  |  |  | -0.1646 | -8.7238 |  |  |  |  | 0 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.026716 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.16574 | 0 | 0 |  |  |  |  | -0.16574 | 0 |  |  |  |  | 0 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.026716 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.16574 | 0 | 0 |  |  |  |  | -0.16574 | 0 |  |  |  |  | 0 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.026832 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.16586 | 42 | 42 |  |  |  |  | -0.16586 | -6.9661 |  |  |  |  | 0 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.026832 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.16586 | 42 | 42 |  |  |  |  | -0.16586 | -6.9661 |  |  |  |  | 0 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.026832 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.16586 | 39 | 39 |  |  |  |  | -0.16586 | -6.4685 |  |  |  |  | 0 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.026832 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.16586 | 39 | 39 |  |  |  |  | -0.16586 | -6.4685 |  |  |  |  | 0 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.027012 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.16604 | 0 | 0 |  |  |  |  | -0.16604 | 0 |  |  |  |  | 0 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.027787 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 |  |  |  |  | 0 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.027787 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.027787 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.027787 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.16681 | 0 | 0 |  |  |  |  | -0.16681 | 0 |  |  |  |  | 0 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.028348 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 |  |  |  |  | 0 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.028348 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 |  |  |  |  | 0 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.028348 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.16738 | 0 | 0 |  |  |  |  | -0.16738 | 0 |  |  |  |  | 0 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.028349 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.16738 | 228 | 228 |  |  |  |  | -0.16738 | -38.1619 |  |  |  |  | 0 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.02836 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 |  |  |  |  | 0 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.02836 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 |  |  |  |  | 0 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.02836 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 |  |  |  |  | 0 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.02836 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.16739 | 0 | 0 |  |  |  |  | -0.16739 | 0 |  |  |  |  | 0 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.028365 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.16739 | 16.2 | 16.2 |  |  |  |  | -0.16739 | -2.7118 |  |  |  |  | 0 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.028372 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.1674 | 213 | 213 |  |  |  |  | -0.1674 | -35.6561 |  |  |  |  | 0 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.028468 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.1675 | 0 | 0 |  |  |  |  | -0.1675 | 0 |  |  |  |  | 0 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.028468 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.1675 | 0 | 0 |  |  |  |  | -0.1675 | 0 |  |  |  |  | 0 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.028478 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.16751 | 165 | 165 |  |  |  |  | -0.16751 | -27.6384 |  |  |  |  | 0 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.028508 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.16754 | 176 | 176 |  |  |  |  | -0.16754 | -29.4863 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.02853 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.16756 | 18 | 18 |  |  |  |  | -0.16756 | -3.016 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | -0.02853 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.16756 | 12 | 12 |  |  |  |  | -0.16756 | -2.0107 |  |  |  |  | 0 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.028932 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.16796 | 0 | 0 |  |  |  |  | -0.16796 | 0 |  |  |  |  | 0 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.029327 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.16835 | 282 | 282 |  |  |  |  | -0.16835 | -47.476 |  |  |  |  | 0 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.029327 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.16835 | 163.2 | 163.2 |  |  |  |  | -0.16835 | -27.4755 |  |  |  |  | 0 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.029327 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.16835 | 157.5 | 157.5 |  |  |  |  | -0.16835 | -26.5159 |  |  |  |  | 0 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.029327 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.16835 | 157.1 | 157.1 |  |  |  |  | -0.16835 | -26.4485 |  |  |  |  | 0 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.029327 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.16835 | 157 | 157 |  |  |  |  | -0.16835 | -26.4317 |  |  |  |  | 0 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.029744 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.16877 | 0 | 0 |  |  |  |  | -0.16877 | 0 |  |  |  |  | 0 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.029744 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.16877 | 0 | 0 |  |  |  |  | -0.16877 | 0 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | E | Houston | YES | -0.03027 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.1693 | 57 | 57 |  |  |  |  | -0.1693 | -9.65 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | D | Houston | YES | -0.03027 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.1693 | 55 | 55 |  |  |  |  | -0.1693 | -9.3114 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | F | Houston | YES | -0.03027 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.1693 | 54 | 54 |  |  |  |  | -0.1693 | -9.1421 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | C | Houston | YES | -0.03027 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.1693 | 47 | 47 |  |  |  |  | -0.1693 | -7.957 |  |  |  |  | 0 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.031354 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 |  |  |  |  | 0 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.031354 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 |  |  |  |  | 0 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.031354 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 |  |  |  |  | 0 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.031354 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17038 | 0 | 0 |  |  |  |  | -0.17038 | 0 |  |  |  |  | 0 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.032212 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 |  |  |  |  | 0 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.032212 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 |  |  |  |  | 0 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.032212 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 |  |  |  |  | 0 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.032212 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 |  |  |  |  | 0 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.032212 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.17124 | 0 | 0 |  |  |  |  | -0.17124 | 0 |  |  |  |  | 0 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.034448 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.17348 | 0 | 0 |  |  |  |  | -0.17348 | 0 |  |  |  |  | 0 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.037654 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.037654 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.037654 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.037654 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.037654 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.037654 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.037654 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.037654 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.037654 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.037654 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.037654 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.037654 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.037654 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.037654 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.037654 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.17668 | 0 | 0 |  |  |  |  | -0.17668 | 0 |  |  |  |  | 0 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.045218 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.18425 | 546 | 546 |  |  |  |  | -0.18425 | -100.5982 |  |  |  |  | 0 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.045218 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.18425 | 248 | 248 |  |  |  |  | -0.18425 | -45.6929 |  |  |  |  | 0 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.045218 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.18425 | 166 | 166 |  |  |  |  | -0.18425 | -30.5848 |  |  |  |  | 0 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.045218 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.18425 | 166 | 166 |  |  |  |  | -0.18425 | -30.5848 |  |  |  |  | 0 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.045218 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.18425 | 13 | 13 |  |  |  |  | -0.18425 | -2.3952 |  |  |  |  | 0 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.045218 | 584.4 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.18425 | 0 | 654 |  |  |  |  | -0.18425 | 0 |  |  |  |  | 0 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.045432 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.18446 | 0 | 0 |  |  |  |  | -0.18446 | 0 |  |  |  |  | 0 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.04705 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.18608 | 252.4 | 252.4 |  |  |  |  | -0.18608 | -46.966 |  |  |  |  | 0 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.04705 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.18608 | 167.7 | 167.7 |  |  |  |  | -0.18608 | -31.2052 |  |  |  |  | 0 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.04705 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.18608 | 166.4 | 166.4 |  |  |  |  | -0.18608 | -30.9633 |  |  |  |  | 0 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.047147 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 651 |  |  |  |  | -0.18617 | 0 |  |  |  |  | 0 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.047147 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 564 |  |  |  |  | -0.18617 | 0 |  |  |  |  | 0 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.047147 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.18617 | 0 | 603 |  |  |  |  | -0.18617 | 0 |  |  |  |  | 0 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.047181 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.18621 | 0 | 0 |  |  |  |  | -0.18621 | 0 |  |  |  |  | 0 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.0588 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0 |  |  |  |  | 0 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.0588 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0 |  |  |  |  | 0 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.0588 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0 |  |  |  |  | 0 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.0588 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.19783 | 0 | 0 |  |  |  |  | -0.19783 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.062036 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.20106 | 0 | 0 |  |  |  |  | -0.20106 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.062036 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.20106 | 0 | 0 |  |  |  |  | -0.20106 | 0 |  |  |  |  | 0 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.066124 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.066124 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.066124 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.066124 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.066124 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.066124 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.066124 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.066124 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.066124 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.066124 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.066124 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.066124 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.066124 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.066124 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.066124 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.066124 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.066124 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.066124 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.066124 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.066124 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.20515 | 0 | 0 |  |  |  |  | -0.20515 | 0 |  |  |  |  | 0 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.075631 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0 |  |  |  |  | 0 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.075631 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0 |  |  |  |  | 0 | 0
88253 | HAMILTON | F | South | YES | -0.075631 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.21466 | 0 | 0 |  |  | 0 | 0 | -0.21466 | 0 |  |  |  |  | 0 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.037558 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.21749 | 46 | 46 | 1.7277 | 46 |  |  | 0.21749 | 10.0048 |  |  |  |  | 0 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.037558 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.21749 | 48 | 48 | 1.8028 | 48 |  |  | 0.21749 | 10.4397 |  |  |  |  | 0 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.037558 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.21749 | 105 | 105 | 3.9436 | 105 |  |  | 0.21749 | 22.8369 |  |  |  |  | 0 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.082186 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.22121 | 0 | 0 |  |  |  |  | -0.22121 | 0 |  |  |  |  | 0 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | 0.042125 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 |  |  |  |  | 0 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.042125 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 |  |  |  |  | 0 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | 0.042125 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 |  |  |  |  | 0 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.042125 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.22206 | 0 | 0 | 0 | 0 |  |  | 0.22206 | 0 |  |  |  |  | 0 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.042125 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.22206 | 17 | 17 | 0.71613 | 17 |  |  | 0.22206 | 3.775 |  |  |  |  | 0 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.043221 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.22316 | 154.2 | 154.2 | 6.6647 | 154.2 |  |  | 0.22316 | 34.4109 |  |  |  |  | 0 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | 0.043221 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.22316 | 158 | 158 | 6.8289 | 158 |  |  | 0.22316 | 35.2589 |  |  |  |  | 0 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | 0.043221 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.22316 | 159 | 159 | 6.8721 | 159 |  |  | 0.22316 | 35.4821 |  |  |  |  | 0 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | 0.043221 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.22316 | 380 | 380 | 16.424 | 380 |  |  | 0.22316 | 84.7999 |  |  |  |  | 0 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.043803 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.22374 | 32 | 32 | 1.4017 | 32 |  |  | 0.22374 | 7.1597 |  |  |  |  | 0 | 0
48733 | CBE_ST12 | 1 | Houston | YES | -0.087489 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22652 | 105 | 105 |  |  |  |  | -0.22652 | -23.7843 |  |  |  |  | 0 | 0
48736 | CBE_ST34 | 1 | Houston | YES | -0.087489 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22652 | 105 | 105 |  |  |  |  | -0.22652 | -23.7843 |  |  |  |  | 0 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153 |  |  |  |  | 0 | 0
48732 | CBE_GT2 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153 |  |  |  |  | 0 | 0
48734 | CBE_GT3 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153 |  |  |  |  | 0 | 0
48735 | CBE_GT4 | 1 | Houston | YES | -0.087489 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22652 | 76 | 76 |  |  |  |  | -0.22652 | -17.2153 |  |  |  |  | 0 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.088308 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.22734 | 0 | 0 |  |  |  |  | -0.22734 | 0 |  |  |  |  | 0 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.088308 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.22734 | 0 | 0 |  |  |  |  | -0.22734 | 0 |  |  |  |  | 0 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | 0.054087 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.23402 | 0 | 463 | 25.0423 | 463 |  |  | 0.23402 | 108.3529 |  |  |  |  | 0 | 0
8262 | ELPS | 1 | South | YES | -0.098206 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.23723 | 0 | 0 |  |  | 0 | 0 | -0.23723 | 0 |  |  |  |  | 0 | 0
60202 | FRNDDRCS | F | West | YES | 0.080216 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.26015 | 0 | 0 |  |  |  |  | 0.26015 | 0 |  |  |  |  | 0 | 0
8134 | FOR #1 | 1 | South | YES | -0.13032 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
8138 | FOR #2 | 2 | South | YES | -0.13032 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
8153 | FOR #3 | 3 | South | YES | -0.13032 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
8154 | FOR #4 | 4 | South | YES | -0.13032 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
8155 | FOR #5 | 5 | South | YES | -0.13032 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
8156 | FOR #6 | 6 | South | YES | -0.13032 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
8157 | FOR #7 | 7 | South | YES | -0.13032 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
80051 | FOR #8 | 8 | South | YES | -0.13032 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
80052 | FOR #9 | 9 | South | YES | -0.13032 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
80053 | FOR #10 | 10 | South | YES | -0.13032 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.26935 | 0 | 0 |  |  | 0 | 0 | -0.26935 | 0 |  |  |  |  | 0 | 0
80226 | ALCOA G | 1 | South | YES | -0.13149 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.27052 | 0 | 0 |  |  | 0 | 0 | -0.27052 | 0 |  |  |  |  | 0 | 0
39960 | TNTNPONE_18 | 1 | North | YES | 0.091914 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.27185 | 0 | 152.3 | 13.9985 | 152.3 |  |  | 0.27185 | 41.4029 |  |  |  |  | 0 | 0
39970 | TNTNPONE_28 | 1 | North | YES | 0.091914 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.27185 | 0 | 153 | 14.0628 | 153 |  |  | 0.27185 | 41.5931 |  |  |  |  | 0 | 0
8147 | UCAR #2 | 10 | South | YES | -0.13528 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 |  |  |  |  | 0 | 0
8148 | UCAR #1 | 2 | South | YES | -0.13528 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 9 | South | YES | -0.13528 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 8 | South | YES | -0.13528 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 |  |  |  |  | 0 | 0
80138 | CSDR7 | 7 | South | YES | -0.13528 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 6 | South | YES | -0.13528 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 5 | South | YES | -0.13528 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 |  |  |  |  | 0 | 0
80140 | CSDR11 | 11 | South | YES | -0.13528 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.2743 | 0 | 0 |  |  | 0 | 0 | -0.2743 | 0 |  |  |  |  | 0 | 0
80227 | AIRCO G | 1 | South | YES | -0.13582 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.27484 | 0 | 0 |  |  | 0 | 0 | -0.27484 | 0 |  |  |  |  | 0 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.13688 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0 |  |  |  |  | 0 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.13688 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0 |  |  |  |  | 0 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.13824 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.27727 | 22 | 22 |  |  | -3.0412 | 22 | -0.27727 | -6.0998 |  |  |  |  | 0 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | -0.13824 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27727 | 11 | 11 |  |  | -1.5206 | 11 | -0.27727 | -3.0499 |  |  |  |  | 0 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | -0.13824 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27727 | 11 | 11 |  |  | -1.5206 | 11 | -0.27727 | -3.0499 |  |  |  |  | 0 | 0
5512 | RAYBURNCC8 | 1 | South | YES | -0.13957 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.2786 | 49.3 | 49.3 |  |  | -6.8808 | 49.3 | -0.2786 | -13.7349 |  |  |  |  | 0 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.13957 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.2786 | 47.7 | 47.7 |  |  | -6.6575 | 47.7 | -0.2786 | -13.2891 |  |  |  |  | 0 | 0
5511 | RAYBURNCC7 | 1 | South | YES | -0.13957 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.2786 | 47.5 | 47.5 |  |  | -6.6296 | 47.5 | -0.2786 | -13.2334 |  |  |  |  | 0 | 0
5509 | RAYBURNCC10 | 1 | South | YES | -0.13957 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.2786 | 37.3 | 37.3 |  |  | -5.206 | 37.3 | -0.2786 | -10.3917 |  |  |  |  | 0 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.13974 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.27877 | 0 | 0 |  |  | 0 | 0 | -0.27877 | 0 |  |  |  |  | 0 | 0
80265 | LARECU40A | 4 | South | YES | -0.13989 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27892 | 100 | 100 |  |  | -13.9893 | 100 | -0.27892 | -27.8921 |  |  |  |  | 0 | 0
80266 | LARECU50A | 5 | South | YES | -0.13989 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27892 | 100 | 100 |  |  | -13.9893 | 100 | -0.27892 | -27.8921 |  |  |  |  | 0 | 0
80012 | LAR | F | South | YES | -0.13989 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.27892 | 0 | 0 |  |  | 0 | 0 | -0.27892 | 0 |  |  |  |  | 0 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.13998 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 |  |  |  |  | 0 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.13998 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 |  |  |  |  | 0 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.13998 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 |  |  |  |  | 0 | 0
8930 | ICPGN10A | 1 | South | YES | -0.13998 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 |  |  |  |  | 0 | 0
8931 | ICPGN20A | 2 | South | YES | -0.13998 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 |  |  |  |  | 0 | 0
8932 | ICPGN30A | 3 | South | YES | -0.13998 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 |  |  |  |  | 0 | 0
80223 | REYSHR G | 1 | South | YES | -0.13998 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.27901 | 0 | 0 |  |  | 0 | 0 | -0.27901 | 0 |  |  |  |  | 0 | 0
88299 | ZAPATA | F | South | YES | -0.14093 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.27995 | 0 | 0 |  |  | 0 | 0 | -0.27995 | 0 |  |  |  |  | 0 | 0
60018 | DSKY1 | 1 | West | YES | 0.10039 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.28032 | 0 | 84 |  |  |  |  | 0.28032 | 23.5472 |  |  |  |  | 0 | 0
8442 | NBEC7 | 7 | South | YES | -0.14135 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.28037 | 367 | 367 |  |  | -51.8743 | 367 | -0.28037 | -102.8975 |  |  |  |  | 0 | 0
8442 | NBEC7 | MB | South | YES | -0.14135 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.28037 | 0 | 0 |  |  | 0 | 0 | -0.28037 | 0 |  |  |  |  | 0 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.14136 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0 |  |  |  |  | 0 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.14136 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0 |  |  |  |  | 0 | 0
8562 | CNOPST1 | 3 | South | YES | -0.14136 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.28039 | 0 | 0 |  |  | 0 | 0 | -0.28039 | 0 |  |  |  |  | 0 | 0
8174 | VICEC61A | 6 | South | YES | -0.14137 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.28039 | 188 | 188 |  |  | -26.577 | 188 | -0.28039 | -52.7142 |  |  |  |  | 0 | 0
8173 | VICEC51A | 5 | South | YES | -0.14137 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.28039 | 144 | 144 |  |  | -20.3568 | 144 | -0.28039 | -40.3768 |  |  |  |  | 0 | 0
8456 | COSW#1 | 1 | South | YES | -0.14144 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.28047 | 0 | 0 |  |  | 0 | 0 | -0.28047 | 0 |  |  |  |  | 0 | 0
8457 | COSW#2 | 2 | South | YES | -0.14144 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.28047 | 0 | 0 |  |  | 0 | 0 | -0.28047 | 0 |  |  |  |  | 0 | 0
60000 | DSKY2 | 1 | West | YES | 0.10065 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.28059 | 0 | 76.5 |  |  |  |  | 0.28059 | 21.4653 |  |  |  |  | 0 | 0
88508 | FALFURRI | F | South | YES | -0.1416 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.28063 | 0 | 0 |  |  | 0 | 0 | -0.28063 | 0 |  |  |  |  | 0 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.14163 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0 |  |  |  |  | 0 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.14163 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0 |  |  |  |  | 0 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.14163 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.28065 | 0 | 0 |  |  | 0 | 0 | -0.28065 | 0 |  |  |  |  | 0 | 0
80263 | B_DAVIS31A | 3 | South | YES | -0.14163 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.28066 | 180 | 180 |  |  | -25.493 | 180 | -0.28066 | -50.518 |  |  |  |  | 0 | 0
80264 | B_DAVIS41A | 4 | South | YES | -0.14163 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.28066 | 180 | 180 |  |  | -25.493 | 180 | -0.28066 | -50.518 |  |  |  |  | 0 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.14163 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.28066 | 0 | 0 |  |  | 0 | 0 | -0.28066 | 0 |  |  |  |  | 0 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.14163 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.28066 | 0 | 0 |  |  | 0 | 0 | -0.28066 | 0 |  |  |  |  | 0 | 0
8506 | VAL #1 | 1 | South | YES | -0.1417 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.28073 | 0 | 0 |  |  | 0 | 0 | -0.28073 | 0 |  |  |  |  | 0 | 0
8507 | VAL #2 | 2 | South | YES | -0.1417 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.28073 | 0 | 0 |  |  | 0 | 0 | -0.28073 | 0 |  |  |  |  | 0 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.14185 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.28087 | 0 | 0 |  |  | 0 | 0 | -0.28087 | 0 |  |  |  |  | 0 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.14185 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.28087 | 0 | 0 |  |  | 0 | 0 | -0.28087 | 0 |  |  |  |  | 0 | 0
8935 | FGNTS201 | 3 | South | YES | -0.14236 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.28138 | 173 | 173 |  |  | -24.6276 | 173 | -0.28138 | -48.6794 |  |  |  |  | 0 | 0
8934 | FGNTS101 | 2 | South | YES | -0.14236 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.28138 | 147.9 | 147.9 |  |  | -21.0545 | 147.9 | -0.28138 | -41.6167 |  |  |  |  | 0 | 0
8933 | FGNTS001 | 1 | South | YES | -0.14236 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.28138 | 146.5 | 146.5 |  |  | -20.8552 | 146.5 | -0.28138 | -41.2227 |  |  |  |  | 0 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.14239 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.28141 | 0 | 0 |  |  | 0 | 0 | -0.28141 | 0 |  |  |  |  | 0 | 0
8938 | MVGN#3 | 3 | South | YES | -0.14248 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.28151 | 250.9 | 250.9 |  |  | -35.7482 | 250.9 | -0.28151 | -70.6303 |  |  |  |  | 0 | 0
8937 | MVGN#2 | 2 | South | YES | -0.14248 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.28151 | 216.7 | 216.7 |  |  | -30.8754 | 216.7 | -0.28151 | -61.0027 |  |  |  |  | 0 | 0
8936 | MVGN#1 | 1 | South | YES | -0.14248 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.28151 | 216.6 | 216.6 |  |  | -30.8612 | 216.6 | -0.28151 | -60.9746 |  |  |  |  | 0 | 0
8983 | HECN3 | 3 | South | YES | -0.14248 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.28151 | 171.9 | 171.9 |  |  | -24.4923 | 171.9 | -0.28151 | -48.3912 |  |  |  |  | 0 | 0
8981 | HECN1 | 1 | South | YES | -0.14248 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.28151 | 144.8 | 144.8 |  |  | -20.6311 | 144.8 | -0.28151 | -40.7623 |  |  |  |  | 0 | 0
8982 | HECN2 | 2 | South | YES | -0.14248 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.28151 | 144.1 | 144.1 |  |  | -20.5314 | 144.1 | -0.28151 | -40.5653 |  |  |  |  | 0 | 0
5935 | SI_RAY10 | 10 | South | YES | -0.14252 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.28155 | 47 | 47 |  |  | -6.6984 | 47 | -0.28155 | -13.2327 |  |  |  |  | 0 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.14252 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.28155 | 38 | 38 |  |  | -5.4157 | 38 | -0.28155 | -10.6988 |  |  |  |  | 0 | 0
5933 | SI_RAY6 | 6 | South | YES | -0.14252 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.28155 | 19.3 | 19.3 |  |  | -2.7506 | 19.3 | -0.28155 | -5.4339 |  |  |  |  | 0 | 0
80003 | MILHWYS | F | South | YES | -0.14252 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.28155 | 0 | 0 |  |  | 0 | 0 | -0.28155 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 3 | South | YES | -0.14255 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 38 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 4 | South | YES | -0.14255 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 19 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 2 | South | YES | -0.14255 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 41 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 1 | South | YES | -0.14255 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 94 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 4 | South | YES | -0.14255 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 22 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 1 | South | YES | -0.14255 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 94 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 3 | South | YES | -0.14255 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 43 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 2 | South | YES | -0.14255 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 36 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.14255 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 50 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.14255 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 148 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.14255 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 50 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.14255 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.28157 | 0 | 55 |  |  | 0 | 0 | -0.28157 | 0 |  |  |  |  | 0 | 0
60017 | ORNNWP1 | 1 | West | YES | 0.10169 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.28163 | 0 | 80 |  |  |  |  | 0.28163 | 22.5305 |  |  |  |  | 0 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | 0.10557 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.2855 | 0 | 150 |  |  |  |  | 0.2855 | 42.8254 |  |  |  |  | 0 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.10568 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.28562 | 0 | 80 |  |  |  |  | 0.28562 | 22.8493 |  |  |  |  | 0 | 0
60016 | WOODWRD11A | 1 | West | YES | 0.1057 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.28564 | 0 | 80 |  |  |  |  | 0.28564 | 22.8513 |  |  |  |  | 0 | 0
60005 | KING_SE1A | 1 | West | YES | 0.10584 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.28577 | 0 | 40 |  |  |  |  | 0.28577 | 11.4309 |  |  |  |  | 0 | 0
6016 | SWMESA | 1 | West | YES | 0.10584 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.28577 | 0 | 75 |  |  |  |  | 0.28577 | 21.433 |  |  |  |  | 0 | 0
60003 | KING_NE1A | 1 | West | YES | 0.10584 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28577 | 0 | 80 |  |  |  |  | 0.28577 | 22.8619 |  |  |  |  | 0 | 0
60201 | RIO DRCS | F | West | YES | 0.10605 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.28599 | 0 | 0 |  |  |  |  | 0.28599 | 0 |  |  |  |  | 0 | 0
60007 | KING_SW1A | 1 | West | YES | 0.10656 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.2865 | 0 | 80 |  |  |  |  | 0.2865 | 22.9199 |  |  |  |  | 0 | 0
60019 | KING_NW1A | 1 | West | YES | 0.10656 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.2865 | 0 | 80 |  |  |  |  | 0.2865 | 22.9199 |  |  |  |  | 0 | 0
8161 | COLETO0A | 1 | South | YES | -0.14836 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.28739 | 0 | 633 |  |  | 0 | 0 | -0.28739 | 0 |  |  |  |  | 0 | 0
48722 | LEG_2___2 | 2 | North | YES | 0.10828 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.28822 | 0 | 819 | 88.6838 | 819 |  |  | 0.28822 | 236.0519 |  |  |  |  | 0 | 0
48721 | LEG_1___1 | 1 | North | YES | 0.10828 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.28822 | 0 | 827 | 89.55 | 827 |  |  | 0.28822 | 238.3576 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.14996 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.28898 | 8.4 | 8.4 |  |  | -1.2596 | 8.4 | -0.28898 | -2.4275 |  |  |  |  | 0 | 0
88198 | BEEVILLE | F | South | YES | -0.15001 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.28904 | 0 | 0 |  |  | 0 | 0 | -0.28904 | 0 |  |  |  |  | 0 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.15295 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.29198 | 24.3 | 24.3 |  |  | -3.7167 | 24.3 | -0.29198 | -7.0951 |  |  |  |  | 0 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.15295 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.29198 | 24 | 24 |  |  | -3.6708 | 24 | -0.29198 | -7.0075 |  |  |  |  | 0 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.15295 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.29198 | 23.9 | 23.9 |  |  | -3.6555 | 23.9 | -0.29198 | -6.9783 |  |  |  |  | 0 | 0
60057 | CALLAHAN1A | 1 | West | YES | 0.11624 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.29618 | 0 | 114 |  |  |  |  | 0.29618 | 33.7646 |  |  |  |  | 0 | 0
1349 | WESTXWIN_1G | 1 | West | YES | 0.11655 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.29649 | 0 | 6.6 |  |  |  |  | 0.29649 | 1.9568 |  |  |  |  | 0 | 0
1350 | NWPWRG1_1G | 1 | West | YES | 0.11655 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.29649 | 0 | 34.3 |  |  |  |  | 0.29649 | 10.1695 |  |  |  |  | 0 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.1176 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.29754 | 0 | 112.5 |  |  |  |  | 0.29754 | 33.4732 |  |  |  |  | 0 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.1176 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 149.5 |  |  |  |  | 0.29754 | 44.4822 |  |  |  |  | 0 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.1176 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 186 |  |  |  |  | 0.29754 | 55.3424 |  |  |  |  | 0 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.1176 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.29754 | 0 | 214.5 |  |  |  |  | 0.29754 | 63.8223 |  |  |  |  | 0 | 0
1002 | PBCTAGE_1G | A | West | YES | 0.11795 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.29788 | 66 | 66 |  |  |  |  | 0.29788 | 19.6603 |  |  |  |  | 0 | 0
1003 | PBCTBGE_2G | B | West | YES | 0.11795 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.29788 | 66 | 66 |  |  |  |  | 0.29788 | 19.6603 |  |  |  |  | 0 | 0
1004 | PBCTCGE_3G | C | West | YES | 0.11795 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.29788 | 67 | 67 |  |  |  |  | 0.29788 | 19.9581 |  |  |  |  | 0 | 0
1006 | PBCTEGE_5G | E | West | YES | 0.11795 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.29788 | 67 | 67 |  |  |  |  | 0.29788 | 19.9581 |  |  |  |  | 0 | 0
1005 | PBCTDGE_4G | D | West | YES | 0.11795 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.29788 | 68 | 68 |  |  |  |  | 0.29788 | 20.256 |  |  |  |  | 0 | 0
1007 | PB5GEN_6G | 5 | West | YES | 0.11795 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.29788 | 114 | 114 |  |  |  |  | 0.29788 | 33.9586 |  |  |  |  | 0 | 0
1008 | PB6GEN_7G | 6 | West | YES | 0.11795 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.29788 | 515 | 515 |  |  |  |  | 0.29788 | 153.4096 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.11806 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.298 | 0 | 30 |  |  |  |  | 0.298 | 8.94 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.11806 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.298 | 0 | 35 |  |  |  |  | 0.298 | 10.43 |  |  |  |  | 0 | 0
11147 | NOTREES_1G | 1 | West | YES | 0.11829 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.29823 | 0 | 149 |  |  |  |  | 0.29823 | 44.4359 |  |  |  |  | 0 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | 0.11831 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.29825 | 0 | 150 |  |  |  |  | 0.29825 | 44.7374 |  |  |  |  | 0 | 0
1320 | BSP 1 | 1 | West | YES | 0.11914 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.29908 | 0 | 0 |  |  |  |  | 0.29908 | 0 |  |  |  |  | 0 | 0
1326 | STANTONW_8 | 1 | West | YES | 0.11955 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.29948 | 0 | 100.5 |  |  |  |  | 0.29948 | 30.0982 |  |  |  |  | 0 | 0
11022 | TIEHVCG_2G | 1 | West | YES | 0.11967 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.29961 | 132.4 | 132.4 |  |  |  |  | 0.29961 | 39.6681 |  |  |  |  | 0 | 0
11023 | TIEHVCG_3G | 1 | West | YES | 0.11967 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.29961 | 137.4 | 137.4 |  |  |  |  | 0.29961 | 41.1661 |  |  |  |  | 0 | 0
11021 | TIEHVCG_1G | 1 | West | YES | 0.11967 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.29961 | 142.1 | 142.1 |  |  |  |  | 0.29961 | 42.5742 |  |  |  |  | 0 | 0
11024 | TIEHVCG_4G | 1 | West | YES | 0.11967 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.29961 | 147 | 147 |  |  |  |  | 0.29961 | 44.0423 |  |  |  |  | 0 | 0
11020 | TIEHVSG_1G | 1 | West | YES | 0.11967 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.29961 | 208.2 | 208.2 |  |  |  |  | 0.29961 | 62.3783 |  |  |  |  | 0 | 0
11025 | TIEHVSG_2G | 1 | West | YES | 0.11967 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.29961 | 213.2 | 213.2 |  |  |  |  | 0.29961 | 63.8763 |  |  |  |  | 0 | 0
11001 | NAV1CT | 1 | West | YES | 0.11969 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.29963 | 70.4 | 70.4 |  |  |  |  | 0.29963 | 21.0938 |  |  |  |  | 0 | 0
11009 | NAV2CT | 1 | West | YES | 0.11969 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.29963 | 71.4 | 71.4 |  |  |  |  | 0.29963 | 21.3934 |  |  |  |  | 0 | 0
11012 | NAV4CT | 1 | West | YES | 0.11969 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.29963 | 80 | 80 |  |  |  |  | 0.29963 | 23.9702 |  |  |  |  | 0 | 0
11013 | NAV5CT | 1 | West | YES | 0.11969 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.29963 | 80 | 80 |  |  |  |  | 0.29963 | 23.9702 |  |  |  |  | 0 | 0
11011 | NAV3ST | 1 | West | YES | 0.11969 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.29963 | 92.8 | 92.8 |  |  |  |  | 0.29963 | 27.8054 |  |  |  |  | 0 | 0
11014 | NAV6ST | 1 | West | YES | 0.11969 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.29963 | 115 | 115 |  |  |  |  | 0.29963 | 34.4572 |  |  |  |  | 0 | 0
1328 | OCOTILLO_1G | 1 | West | YES | 0.11975 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.29968 | 0 | 58 |  |  |  |  | 0.29968 | 17.3815 |  |  |  |  | 0 | 0
1333 | MCDDONAL_8 | 1 | West | YES | 0.12004 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.29998 | 0 | 214.2 |  |  |  |  | 0.29998 | 64.2561 |  |  |  |  | 0 | 0
1327 | WILDHRSE_1G | 1 | West | YES | 0.1204 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.30033 | 0 | 120 |  |  |  |  | 0.30033 | 36.0398 |  |  |  |  | 0 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | 0.12046 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.30039 | 0 | 120 |  |  |  |  | 0.30039 | 36.047 |  |  |  |  | 0 | 0
11320 | COYOTE_1G | 1 | West | YES | 0.12099 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.30092 | 0 | 225 |  |  |  |  | 0.30092 | 67.708 |  |  |  |  | 0 | 0
11309 | BULLCREK_2G | 1 | West | YES | 0.1211 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.30104 | 0 | 180 |  |  |  |  | 0.30104 | 54.1866 |  |  |  |  | 0 | 0
11310 | BULLCREK_1G | 1 | West | YES | 0.1211 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.30104 | 0 | 180 |  |  |  |  | 0.30104 | 54.1866 |  |  |  |  | 0 | 0
1045 | CALENG1G_1G | 1 | West | YES | 0.12114 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0 |  |  |  |  | 0 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.12114 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0 |  |  |  |  | 0 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.12114 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.30107 | 0 | 0 |  |  |  |  | 0.30107 | 0 |  |  |  |  | 0 | 0
60072 | HHOLLOW41A | 1 | West | YES | 0.12125 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 115 |  |  |  |  | 0.30118 | 34.6359 |  |  |  |  | 0 | 0
60058 | BUFF_GAP1A | 1 | West | YES | 0.12125 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30118 | 0 | 120 |  |  |  |  | 0.30118 | 36.1418 |  |  |  |  | 0 | 0
60063 | BUFF_GAP1B | 1 | West | YES | 0.12125 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.30118 | 0 | 170.2 |  |  |  |  | 0.30118 | 51.2611 |  |  |  |  | 0 | 0
60068 | HHOLLOW21A | 1 | West | YES | 0.12125 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 184 |  |  |  |  | 0.30118 | 55.4174 |  |  |  |  | 0 | 0
60066 | H_HOLLOW1A | 1 | West | YES | 0.12125 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.30118 | 0 | 222 |  |  |  |  | 0.30118 | 66.8623 |  |  |  |  | 0 | 0
60070 | HHOLLOW31A | 1 | West | YES | 0.12125 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.30118 | 0 | 224 |  |  |  |  | 0.30118 | 67.4647 |  |  |  |  | 0 | 0
60060 | CIRELLO | 1 | West | YES | 0.12125 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.30118 | 0 | 233 |  |  |  |  | 0.30118 | 70.1753 |  |  |  |  | 0 | 0
11065 | ELBOWCK_1G | 1 | West | YES | 0.12148 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.30141 | 0 | 121.9 |  |  |  |  | 0.30141 | 36.7423 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 1 | West | YES | 0.12148 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.30141 | 0 | 150 |  |  |  |  | 0.30141 | 45.212 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 2 | West | YES | 0.12148 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.30141 | 0 | 220 |  |  |  |  | 0.30141 | 66.311 |  |  |  |  | 0 | 0
1044 | MRGNFG_6G | F | West | YES | 0.12167 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.3016 | 66 | 66 |  |  |  |  | 0.3016 | 19.9059 |  |  |  |  | 0 | 0
1042 | MRGNDG_4G | D | West | YES | 0.12167 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.3016 | 68 | 68 |  |  |  |  | 0.3016 | 20.5091 |  |  |  |  | 0 | 0
1039 | MRGNAG_1G | A | West | YES | 0.12167 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.3016 | 69 | 69 |  |  |  |  | 0.3016 | 20.8107 |  |  |  |  | 0 | 0
1041 | MRGNCG_3G | C | West | YES | 0.12167 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.3016 | 70 | 70 |  |  |  |  | 0.3016 | 21.1123 |  |  |  |  | 0 | 0
1043 | MRGNEG_5G | E | West | YES | 0.12167 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.3016 | 70 | 70 |  |  |  |  | 0.3016 | 21.1123 |  |  |  |  | 0 | 0
1040 | MRGNBG_2G | B | West | YES | 0.12167 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.3016 | 71 | 71 |  |  |  |  | 0.3016 | 21.4139 |  |  |  |  | 0 | 0
1037 | MORGAN5G_5G | 5 | West | YES | 0.12167 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.3016 | 137 | 137 |  |  |  |  | 0.3016 | 41.3198 |  |  |  |  | 0 | 0
6637 | SNYDERW1A | 1 | West | YES | 0.12174 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.30168 | 0 | 63 |  |  |  |  | 0.30168 | 19.0059 |  |  |  |  | 0 | 0
1073 | SCURRYCW_2G | 2 | West | YES | 0.12187 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.30181 | 0 | 120 |  |  |  |  | 0.30181 | 36.2173 |  |  |  |  | 0 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.12187 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.30181 | 0 | 141 |  |  |  |  | 0.30181 | 42.5553 |  |  |  |  | 0 | 0
1069 | KINDERMG_1G | 1 | West | YES | 0.12189 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0 |  |  |  |  | 0 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.12189 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0 |  |  |  |  | 0 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.12189 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30183 | 0 | 0 |  |  |  |  | 0.30183 | 0 |  |  |  |  | 0 | 0
1062 | CIELOGEN_2G | 1 | West | YES | 0.12189 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.30183 | 0 | 61 |  |  |  |  | 0.30183 | 18.4116 |  |  |  |  | 0 | 0
1061 | CIELOGEN_1G | 1 | West | YES | 0.12189 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.30183 | 0 | 99 |  |  |  |  | 0.30183 | 29.8811 |  |  |  |  | 0 | 0
36998 | RDCNYNG1 | 1 | West | YES | 0.12222 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.30215 | 0 | 84 |  |  |  |  | 0.30215 | 25.381 |  |  |  |  | 0 | 0
1354 | AEPWIND_8 | 1 | West | YES | 0.12229 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.30223 | 0 | 101 |  |  |  |  | 0.30223 | 30.5248 |  |  |  |  | 0 | 0
1343 | TRENTIPP_8 | 1 | West | YES | 0.12229 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.30223 | 0 | 150 |  |  |  |  | 0.30223 | 45.3338 |  |  |  |  | 0 | 0
6407 | TURKTRAK1A | 1 | West | YES | 0.12258 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.30252 | 0 | 169.5 |  |  |  |  | 0.30252 | 51.2771 |  |  |  |  | 0 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.16363 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.30266 | 0 | 396.3 |  |  | 0 | 0 | -0.30266 | 0 |  |  |  |  | 0 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | 0.12356 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 37.5 |  |  |  |  | 0.3035 | 11.3812 |  |  |  |  | 0 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | 0.12356 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 80.5 |  |  |  |  | 0.3035 | 24.4317 |  |  |  |  | 0 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | 0.12356 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 105 |  |  |  |  | 0.3035 | 31.8675 |  |  |  |  | 0 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | 0.12356 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 107.5 |  |  |  |  | 0.3035 | 32.6262 |  |  |  |  | 0 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | 0.12356 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.3035 | 0 | 119 |  |  |  |  | 0.3035 | 36.1165 |  |  |  |  | 0 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | 0.12356 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.3035 | 0 | 135 |  |  |  |  | 0.3035 | 40.9725 |  |  |  |  | 0 | 0
6144 | MCADOO1A | 1 | West | YES | 0.12365 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.30358 | 0 | 150 |  |  |  |  | 0.30358 | 45.5372 |  |  |  |  | 0 | 0
11057 | CHAMPION_1G | 1 | West | YES | 0.12374 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.30368 | 0 | 126.5 |  |  |  |  | 0.30368 | 38.4156 |  |  |  |  | 0 | 0
11059 | INADALE_1G | 1 | West | YES | 0.12374 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.30368 | 0 | 197 |  |  |  |  | 0.30368 | 59.8251 |  |  |  |  | 0 | 0
11056 | ROSCOE_1G | 1 | West | YES | 0.12374 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.30368 | 0 | 209 |  |  |  |  | 0.30368 | 63.4693 |  |  |  |  | 0 | 0
11058 | PYRON_1G | 1 | West | YES | 0.12374 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.30368 | 0 | 249 |  |  |  |  | 0.30368 | 75.6165 |  |  |  |  | 0 | 0
1416 | SWETWATR_1G | 1 | West | YES | 0.12461 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.30455 | 30 | 30 |  |  |  |  | 0.30455 | 9.1364 |  |  |  |  | 0 | 0
1419 | SWETWATR_4G | 4 | West | YES | 0.12461 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.30455 | 61 | 61 |  |  |  |  | 0.30455 | 18.5773 |  |  |  |  | 0 | 0
1418 | SWETWATR_3G | 3 | West | YES | 0.12461 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.30455 | 68 | 68 |  |  |  |  | 0.30455 | 20.7092 |  |  |  |  | 0 | 0
1417 | SWETWATR_2G | 2 | West | YES | 0.12461 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.30455 | 72 | 72 |  |  |  |  | 0.30455 | 21.9274 |  |  |  |  | 0 | 0
60081 | WHRLWIND1A | 1 | West | YES | 0.12555 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.30549 | 0 | 60 |  |  |  |  | 0.30549 | 18.3291 |  |  |  |  | 0 | 0
1437 | MESQUITW_1G | 1 | North | YES | 0.12873 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.30867 | 0 | 400 | 51.4928 | 400 |  |  | 0.30867 | 123.4675 |  |  |  |  | 0 | 0
1438 | MESQUITW_2G | 1 | North | YES | 0.12874 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.30868 | 0 | 236 | 30.3829 | 236 |  |  | 0.30868 | 72.8479 |  |  |  |  | 0 | 0
3382 | BBRN_2G | 2 | North | YES | 0.12876 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.30869 | 0 | 589 | 75.8379 | 589 |  |  | 0.30869 | 181.8206 |  |  |  |  | 0 | 0
3381 | BBRN_1G | 1 | North | YES | 0.12876 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.30869 | 0 | 618 | 79.5718 | 618 |  |  | 0.30869 | 190.7727 |  |  |  |  | 0 | 0
8189 | CUECPL2A | 1 | South | YES | -0.17052 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.30955 | 0 | 0 |  |  | 0 | 0 | -0.30955 | 0 |  |  |  |  | 0 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.12968 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.30961 | 0 | 60 | 7.7806 | 60 |  |  | 0.30961 | 18.5768 |  |  |  |  | 0 | 0
13131 | CALFREST_1G | 1 | North | YES | 0.13002 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.30996 | 150.7 | 150.7 | 19.5945 | 150.7 |  |  | 0.30996 | 46.7109 |  |  |  |  | 0 | 0
13132 | CALFREST_2G | 2 | North | YES | 0.13002 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.30996 | 151 | 151 | 19.6335 | 151 |  |  | 0.30996 | 46.8039 |  |  |  |  | 0 | 0
13133 | CALFREST_3G | 3 | North | YES | 0.13002 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.30996 | 177.4 | 177.4 | 23.0661 | 177.4 |  |  | 0.30996 | 54.9868 |  |  |  |  | 0 | 0
13134 | CALFREST_4G | 4 | North | YES | 0.1302 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.31014 | 151.5 | 151.5 | 19.7255 | 151.5 |  |  | 0.31014 | 46.9859 |  |  |  |  | 0 | 0
13135 | CALFREST_5G | 5 | North | YES | 0.1302 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.31014 | 152.3 | 152.3 | 19.8296 | 152.3 |  |  | 0.31014 | 47.234 |  |  |  |  | 0 | 0
13136 | CALFREST_6G | 6 | North | YES | 0.1302 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.31014 | 177.5 | 177.5 | 23.1107 | 177.5 |  |  | 0.31014 | 55.0494 |  |  |  |  | 0 | 0
1442 | COKFIELD_5 | 1 | North | YES | 0.13041 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.31035 | 0 | 165 | 21.5178 | 165 |  |  | 0.31035 | 51.2074 |  |  |  |  | 0 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.17172 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.31075 | 0 | 562 |  |  | 0 | 0 | -0.31075 | 0 |  |  |  |  | 0 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | -0.17241 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.31143 | 89 | 89 |  |  | -15.344 | 89 | -0.31143 | -27.7175 |  |  |  |  | 0 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.17241 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.31143 | 58 | 58 |  |  | -9.9995 | 58 | -0.31143 | -18.0631 |  |  |  |  | 0 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | -0.17241 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.31143 | 45 | 45 |  |  | -7.7582 | 45 | -0.31143 | -14.0145 |  |  |  |  | 0 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | -0.17241 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.31143 | 44 | 44 |  |  | -7.5858 | 44 | -0.31143 | -13.703 |  |  |  |  | 0 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | -0.17241 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.31143 | 44 | 44 |  |  | -7.5858 | 44 | -0.31143 | -13.703 |  |  |  |  | 0 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | -0.17241 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.31143 | 43 | 43 |  |  | -7.4134 | 43 | -0.31143 | -13.3916 |  |  |  |  | 0 | 0
6100 | OKLA7A | EQ | West | YES | 0.13155 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.31148 | 0 | 0 |  |  |  |  | 0.31148 | 0 |  |  |  |  | 0 | 0
6752 | OKLA0A | 1 | West | YES | 0.13155 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.31148 | 0 | 649.7 |  |  |  |  | 0.31148 | 202.3709 |  |  |  |  | 0 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | -0.17279 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.31182 | 174 | 174 |  |  | -30.0656 | 174 | -0.31182 | -54.2565 |  |  |  |  | 0 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.17279 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.31182 | 155 | 155 |  |  | -26.7826 | 155 | -0.31182 | -48.3319 |  |  |  |  | 0 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.17279 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.31182 | 155 | 155 |  |  | -26.7826 | 155 | -0.31182 | -48.3319 |  |  |  |  | 0 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.17355 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.31258 | 407 | 407 |  |  | -70.6349 | 407 | -0.31258 | -127.2191 |  |  |  |  | 0 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.17363 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.31266 | 216 | 216 |  |  | -37.5049 | 216 | -0.31266 | -67.5349 |  |  |  |  | 0 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.17363 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.31266 | 215 | 215 |  |  | -37.3313 | 215 | -0.31266 | -67.2223 |  |  |  |  | 0 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.17386 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.31289 | 418 | 418 |  |  | -72.6756 | 418 | -0.31289 | -130.7892 |  |  |  |  | 0 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | -0.17386 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.31289 | 400 | 400 |  |  | -69.546 | 400 | -0.31289 | -125.1571 |  |  |  |  | 0 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | -0.17406 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.31308 | 0 | 430 |  |  | 0 | 0 | -0.31308 | 0 |  |  |  |  | 0 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.17406 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.31308 | 0 | 430 |  |  | 0 | 0 | -0.31308 | 0 |  |  |  |  | 0 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.17474 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.31377 | 151 | 151 |  |  | -26.3856 | 151 | -0.31377 | -47.3788 |  |  |  |  | 0 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.17474 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.31377 | 95 | 95 |  |  | -16.6002 | 95 | -0.31377 | -29.8078 |  |  |  |  | 0 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.17474 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.31377 | 61 | 61 |  |  | -10.6591 | 61 | -0.31377 | -19.1398 |  |  |  |  | 0 | 0
3107 | STRYKER_1G | 1 | North | YES | 0.13427 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.31421 | 182 | 182 | 24.4371 | 182 |  |  | 0.31421 | 57.1856 |  |  |  |  | 0 | 0
3108 | STRYKER_2G | 2 | North | YES | 0.13427 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.31421 | 484 | 484 | 64.9867 | 484 |  |  | 0.31421 | 152.076 |  |  |  |  | 0 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.13454 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.31448 | 242 | 242 | 32.5592 | 242 |  |  | 0.31448 | 76.1038 |  |  |  |  | 0 | 0
3309 | ASPN_G | 1 | North | YES | 0.13498 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.31491 | 50 | 50 | 6.7489 | 50 |  |  | 0.31491 | 15.7457 |  |  |  |  | 0 | 0
3348 | CHAMPION_1G | MB | North | YES | 0.13501 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.31495 | 0 | 0 | 0 | 0 |  |  | 0.31495 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.13562 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.13562 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.31555 | 0 | 0 | 0 | 0 |  |  | 0.31555 | 0 |  |  |  |  | 0 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.1357 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.31563 | 366 | 366 | 49.6655 | 366 |  |  | 0.31563 | 115.5223 |  |  |  |  | 0 | 0
13117 | TGATEWAY_2G | 2 | North | YES | 0.13575 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.31569 | 130 | 130 | 17.6478 | 130 |  |  | 0.31569 | 41.0395 |  |  |  |  | 0 | 0
13118 | TGATEWAY_3G | 3 | North | YES | 0.13575 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.31569 | 148 | 148 | 20.0913 | 148 |  |  | 0.31569 | 46.7219 |  |  |  |  | 0 | 0
13116 | TGATEWAY_1G | 1 | North | YES | 0.13575 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.31569 | 151 | 151 | 20.4986 | 151 |  |  | 0.31569 | 47.669 |  |  |  |  | 0 | 0
13119 | TGATEWAY_4G | 4 | North | YES | 0.13575 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.31569 | 399 | 399 | 54.165 | 399 |  |  | 0.31569 | 125.9598 |  |  |  |  | 0 | 0
3097 | MARTLAKE_1G | 1 | North | YES | 0.13627 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 790 | 107.6549 | 790 |  |  | 0.31621 | 249.8048 |  |  |  |  | 0 | 0
3098 | MARTLAKE_2G | 2 | North | YES | 0.13627 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 795 | 108.3362 | 795 |  |  | 0.31621 | 251.3859 |  |  |  |  | 0 | 0
3099 | MARTLAKE_3G | 3 | North | YES | 0.13627 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.31621 | 0 | 804 | 109.5627 | 804 |  |  | 0.31621 | 254.2317 |  |  |  |  | 0 | 0
3126 | TRINIDAD_6G | 1 | North | YES | 0.13717 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.31711 | 224 | 224 | 30.727 | 224 |  |  | 0.31711 | 71.0328 |  |  |  |  | 0 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.13725 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.31718 | 0 | 120 | 16.4696 | 120 |  |  | 0.31718 | 38.062 |  |  |  |  | 0 | 0
344 | MRSSHPRD | 1 | North | YES | 0.13746 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.3174 | 0 | 0 | 0 | 0 |  |  | 0.3174 | 0 |  |  |  |  | 0 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.13746 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.3174 | 0 | 0 | 0 | 0 |  |  | 0.3174 | 0 |  |  |  |  | 0 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.1791 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.31813 | 203 | 203 |  |  | -36.3577 | 203 | -0.31813 | -64.5803 |  |  |  |  | 0 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.1791 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.31813 | 182 | 182 |  |  | -32.5966 | 182 | -0.31813 | -57.8996 |  |  |  |  | 0 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.1791 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.31813 | 149 | 149 |  |  | -26.6862 | 149 | -0.31813 | -47.4013 |  |  |  |  | 0 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.1791 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.31813 | 147 | 147 |  |  | -26.328 | 147 | -0.31813 | -46.7651 |  |  |  |  | 0 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.1791 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.31813 | 146 | 146 |  |  | -26.1489 | 146 | -0.31813 | -46.4469 |  |  |  |  | 0 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.1791 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.31813 | 138 | 138 |  |  | -24.7161 | 138 | -0.31813 | -43.9019 |  |  |  |  | 0 | 0
332 | RWMILLER01 | 1 | North | YES | 0.13821 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.31814 | 73 | 73 | 10.0892 | 73 |  |  | 0.31814 | 23.2246 |  |  |  |  | 0 | 0
336 | RWMILLER05 | 5 | North | YES | 0.13821 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.31814 | 101 | 101 | 13.959 | 101 |  |  | 0.31814 | 32.1326 |  |  |  |  | 0 | 0
335 | RWMILLER04 | 4 | North | YES | 0.13821 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.31814 | 102 | 102 | 14.0972 | 102 |  |  | 0.31814 | 32.4508 |  |  |  |  | 0 | 0
333 | RWMILLER02 | 2 | North | YES | 0.13821 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.31814 | 119 | 119 | 16.4468 | 119 |  |  | 0.31814 | 37.8592 |  |  |  |  | 0 | 0
334 | RWMILLER03 | 3 | North | YES | 0.13821 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.31814 | 208 | 208 | 28.7473 | 208 |  |  | 0.31814 | 66.1741 |  |  |  |  | 0 | 0
1453 | WCPWRCO_1G | 1 | North | YES | 0.14048 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.32041 | 204 | 204 | 28.6571 | 204 |  |  | 0.32041 | 65.3642 |  |  |  |  | 0 | 0
1454 | WCPWRCO_2G | 2 | North | YES | 0.14048 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.32041 | 204 | 204 | 28.6571 | 204 |  |  | 0.32041 | 65.3642 |  |  |  |  | 0 | 0
1455 | WCPWRCO_3G | 3 | North | YES | 0.14048 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.32041 | 242 | 242 | 33.9952 | 242 |  |  | 0.32041 | 77.5399 |  |  |  |  | 0 | 0
503 | NTHTEXAS01 | 1 | North | YES | 0.14048 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.32042 | 18 | 18 | 2.5286 | 18 |  |  | 0.32042 | 5.7675 |  |  |  |  | 0 | 0
504 | NTHTEXAS02 | 2 | North | YES | 0.14048 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.32042 | 18 | 18 | 2.5286 | 18 |  |  | 0.32042 | 5.7675 |  |  |  |  | 0 | 0
505 | NTHTEXAS03 | 3 | North | YES | 0.14048 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.32042 | 38 | 38 | 5.3382 | 38 |  |  | 0.32042 | 12.1758 |  |  |  |  | 0 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.14061 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32054 | 161 | 161 | 22.6379 | 161 |  |  | 0.32054 | 51.6077 |  |  |  |  | 0 | 0
12422 | FPLEFR2B_G | 2 | North | YES | 0.14061 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.32054 | 161 | 161 | 22.6379 | 161 |  |  | 0.32054 | 51.6077 |  |  |  |  | 0 | 0
12421 | FPLEFR2A_G | 1 | North | YES | 0.14061 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.32054 | 162 | 162 | 22.7785 | 162 |  |  | 0.32054 | 51.9282 |  |  |  |  | 0 | 0
12423 | FPLEFR2C_G | 3 | North | YES | 0.14061 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.32054 | 163 | 163 | 22.9191 | 163 |  |  | 0.32054 | 52.2488 |  |  |  |  | 0 | 0
12412 | FPLEFR1B_G | 2 | North | YES | 0.14061 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32054 | 164 | 164 | 23.0597 | 164 |  |  | 0.32054 | 52.5693 |  |  |  |  | 0 | 0
12413 | FPLEFR1C_G | 3 | North | YES | 0.14061 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.32054 | 164 | 164 | 23.0597 | 164 |  |  | 0.32054 | 52.5693 |  |  |  |  | 0 | 0
12414 | FPLEFR1S_G | 4 | North | YES | 0.14061 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.32054 | 414 | 414 | 58.2117 | 414 |  |  | 0.32054 | 132.7055 |  |  |  |  | 0 | 0
12424 | FPLEFR2S_G | 4 | North | YES | 0.14061 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.32054 | 415 | 415 | 58.3523 | 415 |  |  | 0.32054 | 133.026 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.18179 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.32082 | 0 | 0 |  |  | 0 | 0 | -0.32082 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.18179 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.32082 | 0 | 0 |  |  | 0 | 0 | -0.32082 | 0 |  |  |  |  | 0 | 0
581 | JCKCNTY802 | 2 | North | YES | 0.14141 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32135 | 147 | 147 | 20.7876 | 147 |  |  | 0.32135 | 47.2382 |  |  |  |  | 0 | 0
582 | JCKCNTY803 | 3 | North | YES | 0.14141 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32135 | 147 | 147 | 20.7876 | 147 |  |  | 0.32135 | 47.2382 |  |  |  |  | 0 | 0
580 | JCKCNTY801 | 1 | North | YES | 0.14141 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.32135 | 288 | 288 | 40.7267 | 288 |  |  | 0.32135 | 92.5484 |  |  |  |  | 0 | 0
2451 | LKHB1_G | 1 | North | YES | 0.14151 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.32145 | 391 | 391 | 55.332 | 391 |  |  | 0.32145 | 125.6872 |  |  |  |  | 0 | 0
2452 | LKHB2_G | 2 | North | YES | 0.14151 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.32145 | 516 | 516 | 73.0212 | 516 |  |  | 0.32145 | 165.8685 |  |  |  |  | 0 | 0
948 | STEAM1 | 1 | North | YES | 0.14158 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.32151 | 20 | 20 | 2.8316 | 20 |  |  | 0.32151 | 6.4303 |  |  |  |  | 0 | 0
949 | STEAM2 | 1 | North | YES | 0.14158 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.32152 | 26 | 26 | 3.6811 | 26 |  |  | 0.32152 | 8.3594 |  |  |  |  | 0 | 0
950 | STEAM3 | 1 | North | YES | 0.14158 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.32152 | 42 | 42 | 5.9463 | 42 |  |  | 0.32152 | 13.5037 |  |  |  |  | 0 | 0
837 | NEWMAN_G5 | 1 | North | YES | 0.14174 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.32167 | 40 | 40 | 5.6695 | 40 |  |  | 0.32167 | 12.8669 |  |  |  |  | 0 | 0
728 | WOLFRIDGE801 | 1 | North | YES | 0.14175 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.32169 | 0 | 112.5 | 15.947 | 112.5 |  |  | 0.32169 | 36.1899 |  |  |  |  | 0 | 0
845 | OLINGER_G4 | 1 | North | YES | 0.14177 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.3217 | 76 | 76 | 10.7743 | 76 |  |  | 0.3217 | 24.4495 |  |  |  |  | 0 | 0
842 | OLINGER_G1 | 1 | North | YES | 0.14177 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.3217 | 79 | 79 | 11.1996 | 79 |  |  | 0.3217 | 25.4146 |  |  |  |  | 0 | 0
843 | OLINGER_G2 | 1 | North | YES | 0.14177 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.3217 | 110 | 110 | 15.5944 | 110 |  |  | 0.3217 | 35.3874 |  |  |  |  | 0 | 0
844 | OLINGER_G3 | 1 | North | YES | 0.14177 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.3217 | 150 | 150 | 21.265 | 150 |  |  | 0.3217 | 48.2555 |  |  |  |  | 0 | 0
12440 | PARKD_1SVC8 | 1 | North | YES | 0.1418 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.32173 | 0 | 0 | 0 | 0 |  |  | 0.32173 | 0 |  |  |  |  | 0 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.1418 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.32173 | 0 | 0 | 0 | 0 |  |  | 0.32173 | 0 |  |  |  |  | 0 | 0
5925 | DCEAST | EQ | North | YES | 0.14191 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.32185 | 0 | 0 | 0 | 0 |  |  | 0.32185 | 0 |  |  |  |  | 0 | 0
1701 | MOSES_1G | 1 | North | YES | 0.14191 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 558 | 79.1875 | 558 |  |  | 0.32185 | 179.5921 |  |  |  |  | 0 | 0
1702 | MOSES_2G | 2 | North | YES | 0.14191 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 579 | 82.1676 | 579 |  |  | 0.32185 | 186.3509 |  |  |  |  | 0 | 0
1703 | MOSES_3G | 3 | North | YES | 0.14191 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.32185 | 0 | 808 | 114.6657 | 808 |  |  | 0.32185 | 260.0545 |  |  |  |  | 0 | 0
1675 | PEC_1G | 1 | North | YES | 0.14196 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0 |  |  |  |  | 0 | 0
1676 | PEC_2G | 2 | North | YES | 0.14196 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0 |  |  |  |  | 0 | 0
1677 | PEC_3G | 3 | North | YES | 0.14196 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.3219 | 0 | 0 | 0 | 0 |  |  | 0.3219 | 0 |  |  |  |  | 0 | 0
1679 | LAMARPWR_2G | 2 | North | YES | 0.14207 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32201 | 156 | 156 | 22.1635 | 156 |  |  | 0.32201 | 50.2337 |  |  |  |  | 0 | 0
1681 | LAMARPWR_4G | 4 | North | YES | 0.14207 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.32201 | 156 | 156 | 22.1635 | 156 |  |  | 0.32201 | 50.2337 |  |  |  |  | 0 | 0
1682 | LAMARPWR_5G | 5 | North | YES | 0.14207 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.32201 | 157 | 157 | 22.3056 | 157 |  |  | 0.32201 | 50.5557 |  |  |  |  | 0 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.14207 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.32201 | 160 | 160 | 22.7318 | 160 |  |  | 0.32201 | 51.5217 |  |  |  |  | 0 | 0
1680 | LAMARPWR_3G | 3 | North | YES | 0.14207 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.32201 | 196 | 196 | 27.8465 | 196 |  |  | 0.32201 | 63.1141 |  |  |  |  | 0 | 0
1683 | LAMARPWR_6G | 6 | North | YES | 0.14207 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.32201 | 198 | 198 | 28.1307 | 198 |  |  | 0.32201 | 63.7581 |  |  |  |  | 0 | 0
11691 | KMICHICT1_G | 1 | North | YES | 0.14218 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32212 | 144 | 144 | 20.4742 | 144 |  |  | 0.32212 | 46.3851 |  |  |  |  | 0 | 0
11694 | KMICHICT4_G | 4 | North | YES | 0.14218 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.32212 | 144 | 144 | 20.4742 | 144 |  |  | 0.32212 | 46.3851 |  |  |  |  | 0 | 0
11692 | KMICHICT2_G | 2 | North | YES | 0.14218 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.32212 | 146 | 146 | 20.7586 | 146 |  |  | 0.32212 | 47.0293 |  |  |  |  | 0 | 0
11695 | KMICHICT5_G | 5 | North | YES | 0.14218 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.32212 | 148 | 148 | 21.0429 | 148 |  |  | 0.32212 | 47.6736 |  |  |  |  | 0 | 0
11696 | KMICHIST6_G | 6 | North | YES | 0.14218 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.32212 | 310 | 310 | 44.0764 | 310 |  |  | 0.32212 | 99.8568 |  |  |  |  | 0 | 0
11693 | KMICHIST3_G | 3 | North | YES | 0.14218 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.32212 | 312 | 312 | 44.3608 | 312 |  |  | 0.32212 | 100.501 |  |  |  |  | 0 | 0
1689 | VALLEY_3G | 3 | North | YES | 0.14218 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.32212 | 375 | 375 | 53.3182 | 375 |  |  | 0.32212 | 120.7945 |  |  |  |  | 0 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.18316 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.32219 | 0 | 0 |  |  | 0 | 0 | -0.32219 | 0 |  |  |  |  | 0 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.14226 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.3222 | 170 | 170 | 24.1849 | 170 |  |  | 0.3222 | 54.7741 |  |  |  |  | 0 | 0
1688 | VALLEY_2G | 2 | North | YES | 0.14226 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.3222 | 527 | 527 | 74.9731 | 527 |  |  | 0.3222 | 169.7997 |  |  |  |  | 0 | 0
6948 | DENISNDM | 1 | North | YES | 0.14236 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.3223 | 0 | 0 | 0 | 0 |  |  | 0.3223 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 2 | North | YES | 0.14236 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.3223 | 0 | 0 | 0 | 0 |  |  | 0.3223 | 0 |  |  |  |  | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.18349 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.32252 | 0 | 0 |  |  | 0 | 0 | -0.32252 | 0 |  |  |  |  | 0 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.14294 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.32287 | 61 | 61 | 8.7191 | 61 |  |  | 0.32287 | 19.6952 |  |  |  |  | 0 | 0
924 | SPENCER_G5 | 1 | North | YES | 0.14294 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.32287 | 66 | 66 | 9.4338 | 66 |  |  | 0.32287 | 21.3096 |  |  |  |  | 0 | 0
12323 | ENNSTRAC_2G | 2 | North | YES | 0.14304 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.32298 | 116 | 116 | 16.5926 | 116 |  |  | 0.32298 | 37.4653 |  |  |  |  | 0 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | 0.14304 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.32298 | 196 | 196 | 28.0358 | 196 |  |  | 0.32298 | 63.3034 |  |  |  |  | 0 | 0
2371 | COLLIN_1G | MB | North | YES | 0.14311 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.32304 | 0 | 0 | 0 | 0 |  |  | 0.32304 | 0 |  |  |  |  | 0 | 0
2414 | MTCK7_G | 7 | North | YES | 0.14399 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.32392 | 115 | 115 | 16.5585 | 115 |  |  | 0.32392 | 37.2512 |  |  |  |  | 0 | 0
2413 | MTCK6_G | 6 | North | YES | 0.14399 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.32392 | 118 | 118 | 16.9905 | 118 |  |  | 0.32392 | 38.223 |  |  |  |  | 0 | 0
2417 | MTCK8_G | 8 | North | YES | 0.14399 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.32392 | 556 | 556 | 80.0568 | 556 |  |  | 0.32392 | 180.1015 |  |  |  |  | 0 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.14425 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.32419 | 156 | 156 | 22.5032 | 156 |  |  | 0.32419 | 50.5733 |  |  |  |  | 0 | 0
2382 | NTHLK2_G | 2 | North | YES | 0.14425 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.32419 | 181 | 181 | 26.1094 | 181 |  |  | 0.32419 | 58.678 |  |  |  |  | 0 | 0
2383 | NTHLK3_G | 3 | North | YES | 0.14425 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.32419 | 329 | 329 | 47.4586 | 329 |  |  | 0.32419 | 106.6577 |  |  |  |  | 0 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.14433 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.32427 | 0 | 0 | 0 | 0 |  |  | 0.32427 | 0 |  |  |  |  | 0 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.14433 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.32427 | 0 | 0 | 0 | 0 |  |  | 0.32427 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.18533 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.18533 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.18533 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.32436 | 0 | 0 |  |  | 0 | 0 | -0.32436 | 0 |  |  |  |  | 0 | 0
1895 | DECRDOVA_5G | D | North | YES | 0.14465 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.32458 | 68 | 68 | 9.8361 | 68 |  |  | 0.32458 | 22.0718 |  |  |  |  | 0 | 0
1893 | DECRDOVA_3G | B | North | YES | 0.14465 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.32458 | 69 | 69 | 9.9807 | 69 |  |  | 0.32458 | 22.3963 |  |  |  |  | 0 | 0
1894 | DECRDOVA_4G | C | North | YES | 0.14465 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.32458 | 69 | 69 | 9.9807 | 69 |  |  | 0.32458 | 22.3963 |  |  |  |  | 0 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.14465 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.32458 | 70 | 70 | 10.1254 | 70 |  |  | 0.32458 | 22.7209 |  |  |  |  | 0 | 0
1861 | EAGLEMNT_1G | MB | North | YES | 0.1447 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0 |  |  |  |  | 0 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.1447 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0 |  |  |  |  | 0 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.1447 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.32464 | 0 | 0 | 0 | 0 |  |  | 0.32464 | 0 |  |  |  |  | 0 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.18586 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.32488 | 293 | 293 |  |  | -54.4561 | 293 | -0.32488 | -95.1912 |  |  |  |  | 0 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.18586 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.32488 | 154 | 154 |  |  | -28.622 | 154 | -0.32488 | -50.0323 |  |  |  |  | 0 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.18586 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.32488 | 148 | 148 |  |  | -27.5068 | 148 | -0.32488 | -48.0829 |  |  |  |  | 0 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.18586 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.32488 | 148 | 148 |  |  | -27.5068 | 148 | -0.32488 | -48.0829 |  |  |  |  | 0 | 0
1878 | WLFHOLW_2G | 2 | North | YES | 0.14509 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.32503 | 215.7 | 215.7 | 31.2959 | 215.7 |  |  | 0.32503 | 70.1082 |  |  |  |  | 0 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.14509 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.32503 | 217.3 | 217.3 | 31.5281 | 217.3 |  |  | 0.32503 | 70.6283 |  |  |  |  | 0 | 0
1879 | WLFHOLW_3G | 3 | North | YES | 0.14509 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.32503 | 272.4 | 272.4 | 39.5225 | 272.4 |  |  | 0.32503 | 88.5373 |  |  |  |  | 0 | 0
1889 | DECRDOVA_1G | 1 | North | YES | 0.14553 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.32546 | 779 | 779 | 113.3648 | 779 |  |  | 0.32546 | 253.5354 |  |  |  |  | 0 | 0
244 | WHITNYDM01 | 1 | North | YES | 0.14569 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32562 | 0 | 0 | 0 | 0 |  |  | 0.32562 | 0 |  |  |  |  | 0 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.14569 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32562 | 0 | 0 | 0 | 0 |  |  | 0.32562 | 0 |  |  |  |  | 0 | 0
253 | BOSQUESW804 | 2 | North | YES | 0.14734 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.32728 | 80 | 80 | 11.7873 | 80 |  |  | 0.32728 | 26.1822 |  |  |  |  | 0 | 0
251 | BOSQUESW803 | 2 | North | YES | 0.14734 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.32728 | 150 | 150 | 22.1012 | 150 |  |  | 0.32728 | 49.0916 |  |  |  |  | 0 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.14753 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.32747 | 0 | 0 | 0 | 0 |  |  | 0.32747 | 0 |  |  |  |  | 0 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.14753 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.32747 | 0 | 0 | 0 | 0 |  |  | 0.32747 | 0 |  |  |  |  | 0 | 0
1948 | HANDLEY_4G | 4 | North | YES | 0.14783 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.32777 | 435 | 435 | 64.3069 | 435 |  |  | 0.32777 | 142.5794 |  |  |  |  | 0 | 0
1947 | HANDLEY_3G | 3 | North | YES | 0.14804 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.32798 | 395 | 395 | 58.4766 | 395 |  |  | 0.32798 | 129.5516 |  |  |  |  | 0 | 0
1949 | HANDLEY_5G | 5 | North | YES | 0.14804 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.32798 | 435 | 435 | 64.3983 | 435 |  |  | 0.32798 | 142.6707 |  |  |  |  | 0 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.19059 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.32961 | 423.3 | 423.3 |  |  | -80.6746 | 423.3 | -0.32961 | -139.5251 |  |  |  |  | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.19059 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0 |  |  |  |  | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.19059 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0 |  |  |  |  | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.19059 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.32961 | 0 | 0 |  |  | 0 | 0 | -0.32961 | 0 |  |  |  |  | 0 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.19212 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.33115 | 0 | 0 |  |  | 0 | 0 | -0.33115 | 0 |  |  |  |  | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.19212 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.33115 | 0 | 0 |  |  | 0 | 0 | -0.33115 | 0 |  |  |  |  | 0 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.19304 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.33207 | 226.7 | 226.7 |  |  | -43.7619 | 226.7 | -0.33207 | -75.2795 |  |  |  |  | 0 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.19304 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.33207 | 225 | 225 |  |  | -43.4338 | 225 | -0.33207 | -74.715 |  |  |  |  | 0 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.19304 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.33207 | 224.6 | 224.6 |  |  | -43.3566 | 224.6 | -0.33207 | -74.5822 |  |  |  |  | 0 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.19304 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.33207 | 223.9 | 223.9 |  |  | -43.2214 | 223.9 | -0.33207 | -74.3497 |  |  |  |  | 0 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.1952 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.33422 | 0 | 0 |  |  | 0 | 0 | -0.33422 | 0 |  |  |  |  | 0 | 0
1944 | MDLTHELP_4G | 4 | North | YES | 0.15515 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.33509 | 211 | 211 | 32.7371 | 211 |  |  | 0.33509 | 70.7037 |  |  |  |  | 0 | 0
1943 | MDLTHELP_3G | 3 | North | YES | 0.15515 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.33509 | 212 | 212 | 32.8922 | 212 |  |  | 0.33509 | 71.0388 |  |  |  |  | 0 | 0
1937 | MDLTHELP_5G | 5 | North | YES | 0.15515 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.33509 | 224 | 224 | 34.754 | 224 |  |  | 0.33509 | 75.0599 |  |  |  |  | 0 | 0
1938 | MDLTHELP_6G | 6 | North | YES | 0.15515 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.33509 | 226 | 226 | 35.0644 | 226 |  |  | 0.33509 | 75.73 |  |  |  |  | 0 | 0
1942 | MDLTHELP_2G | 2 | North | YES | 0.15582 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.33575 | 216.1 | 216.1 | 33.6718 | 216.1 |  |  | 0.33575 | 72.5561 |  |  |  |  | 0 | 0
1941 | MDLTHELP_1G | 1 | North | YES | 0.15582 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.33575 | 216.4 | 216.4 | 33.7186 | 216.4 |  |  | 0.33575 | 72.6569 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.19713 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.33616 | 50 | 50 |  |  | -9.8566 | 50 | -0.33616 | -16.808 |  |  |  |  | 0 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.1978 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.33683 | 0 | 0 |  |  | 0 | 0 | -0.33683 | 0 |  |  |  |  | 0 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.1978 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.33683 | 0 | 0 |  |  | 0 | 0 | -0.33683 | 0 |  |  |  |  | 0 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.19837 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.3374 | 0 | 436 |  |  | 0 | 0 | -0.3374 | 0 |  |  |  |  | 0 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.19858 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.3376 | 0 | 606 |  |  | 0 | 0 | -0.3376 | 0 |  |  |  |  | 0 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.19858 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.3376 | 0 | 598 |  |  | 0 | 0 | -0.3376 | 0 |  |  |  |  | 0 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | 0.16701 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.34695 | 75 | 75 | 12.5258 | 75 |  |  | 0.34695 | 26.0211 |  |  |  |  | 0 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | 0.16701 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.34695 | 222 | 222 | 37.0764 | 222 |  |  | 0.34695 | 77.0224 |  |  |  |  | 0 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.21272 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0 |  |  |  |  | 0 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.21272 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0 |  |  |  |  | 0 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.21272 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.35175 | 0 | 0 |  |  | 0 | 0 | -0.35175 | 0 |  |  |  |  | 0 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.21458 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.3536 | 329 | 329 |  |  | -70.5955 | 329 | -0.3536 | -116.3356 |  |  |  |  | 0 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.21458 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.3536 | 139 | 139 |  |  | -29.8261 | 139 | -0.3536 | -49.1509 |  |  |  |  | 0 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.21458 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.3536 | 132 | 132 |  |  | -28.324 | 132 | -0.3536 | -46.6757 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.2208 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.35983 | 0 | 0 |  |  | 0 | 0 | -0.35983 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.2208 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.35983 | 0 | 0 |  |  | 0 | 0 | -0.35983 | 0 |  |  |  |  | 0 | 0
9020 | SANDHG5A | 5A | South | YES | -0.22125 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.36028 | 155 | 155 |  |  | -34.2934 | 155 | -0.36028 | -55.8427 |  |  |  |  | 0 | 0
9021 | SANDHG5C | 5C | South | YES | -0.22125 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.36028 | 148 | 148 |  |  | -32.7447 | 148 | -0.36028 | -53.3208 |  |  |  |  | 0 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.22125 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.36028 | 49 | 49 |  |  | -10.8412 | 49 | -0.36028 | -17.6535 |  |  |  |  | 0 | 0
9019 | SANDH_G4 | 4 | South | YES | -0.22125 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.36028 | 47 | 47 |  |  | -10.3987 | 47 | -0.36028 | -16.933 |  |  |  |  | 0 | 0
9017 | SANDH_G2 | 2 | South | YES | -0.22125 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.36028 | 46 | 46 |  |  | -10.1774 | 46 | -0.36028 | -16.5727 |  |  |  |  | 0 | 0
9018 | SANDH_G3 | 3 | South | YES | -0.22125 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.36028 | 46 | 46 |  |  | -10.1774 | 46 | -0.36028 | -16.5727 |  |  |  |  | 0 | 0
9001 | DECKR_G2 | 2 | South | YES | -0.22261 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.36164 | 426 | 426 |  |  | -94.8327 | 426 | -0.36164 | -154.0585 |  |  |  |  | 0 | 0
9000 | DECKR_G1 | 1 | South | YES | -0.22261 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.36164 | 321 | 321 |  |  | -71.4585 | 321 | -0.36164 | -116.0864 |  |  |  |  | 0 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.22486 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.36388 | 175 | 175 |  |  | -39.35 | 175 | -0.36388 | -63.6798 |  |  |  |  | 0 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.22486 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.36388 | 160 | 160 |  |  | -35.9771 | 160 | -0.36388 | -58.2216 |  |  |  |  | 0 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.22486 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.36388 | 158 | 158 |  |  | -35.5274 | 158 | -0.36388 | -57.4938 |  |  |  |  | 0 | 0
9005 | DECKR_G6 | 6 | South | YES | -0.22493 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.36396 | 47 | 47 |  |  | -10.5719 | 47 | -0.36396 | -17.1062 |  |  |  |  | 0 | 0
9003 | DECKR_G4 | 4 | South | YES | -0.22493 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.36396 | 44 | 44 |  |  | -9.8971 | 44 | -0.36396 | -16.0143 |  |  |  |  | 0 | 0
9004 | DECKR_G5 | 5 | South | YES | -0.22493 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.36396 | 44 | 44 |  |  | -9.8971 | 44 | -0.36396 | -16.0143 |  |  |  |  | 0 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.22493 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.36396 | 42 | 42 |  |  | -9.4472 | 42 | -0.36396 | -15.2864 |  |  |  |  | 0 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.22552 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.36454 | 232.6 | 232.6 |  |  | -52.455 | 232.6 | -0.36454 | -84.7929 |  |  |  |  | 0 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.22552 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.36454 | 152.5 | 152.5 |  |  | -34.3912 | 152.5 | -0.36454 | -55.5929 |  |  |  |  | 0 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.22552 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.36454 | 149.5 | 149.5 |  |  | -33.7146 | 149.5 | -0.36454 | -54.4993 |  |  |  |  | 0 | 0
239 | BOSQUESW502 | 1 | North | YES | 0.197 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.37693 | 149 | 149 | 29.3526 | 149 |  |  | 0.37693 | 56.1631 |  |  |  |  | 0 | 0
247 | BOSQUESW501 | 2 | North | YES | 0.197 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.37693 | 156 | 156 | 30.7315 | 156 |  |  | 0.37693 | 58.8016 |  |  |  |  | 0 | 0
238 | BOSQUESW505 | 1 | North | YES | 0.197 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.37693 | 255 | 255 | 50.2342 | 255 |  |  | 0.37693 | 96.1181 |  |  |  |  | 0 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.27156 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.41058 | 0 | 581 |  |  | 0 | 0 | -0.41058 | 0 |  |  |  |  | 0 | 0
3403 | THOUSE_1G | 1 | North | YES | 0.23807 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.41801 | 563 | 563 | 134.0345 | 563 |  |  | 0.41801 | 235.3389 |  |  |  |  | 0 | 0
3404 | THOUSE_2G | 2 | North | YES | 0.23807 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.41801 | 807 | 807 | 192.1241 | 807 |  |  | 0.41801 | 337.333 |  |  |  |  | 0 | 0
3432 | SANDOW_4G | 4 | South | YES | -0.28152 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.42055 | 0 | 580 |  |  | 0 | 0 | -0.42055 | 0 |  |  |  |  | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0

## Zones
Houston | -1
North | 1
South | -1
West | 1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | South | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1073 | SCURRYCW_2G | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3126 | TRINIDAD_6G | GST
3309 | ASPN_G | Bio
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5920 | WELSHDC1 | DCTie
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6096 | NORTHDC7 | DCTie
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NBEC7 | GST
8442 | NBEC7 | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11056 | ROSCOE_1G | Wind
11057 | CHAMPION_1G | Wind
11058 | PYRON_1G | Wind
11059 | INADALE_1G | Wind
11065 | ELBOWCK_1G | Wind
11147 | NOTREES_1G | Wind
11309 | BULLCREK_2G | Wind
11310 | BULLCREK_1G | Wind
11320 | COYOTE_1G | Wind
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
48940 | WARVUE_GT1 | Cogen
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
71061 | L_SWEETW1_5N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
76095 | L_CAPRSI1_1N | Wind
76096 | L_CAPRSI1_2N | Wind
76097 | L_CAPRGE1_1N | Wind
80003 | MILHWYS | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80263 | B_DAVIS31A | CC
80264 | B_DAVIS41A | CC
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
86104 | CID-138 | DCTie
86105 | CID-230 | DCTie
86106 | CUF-230 | DCTie
86107 | CUF-138 | DCTie
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR