## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  | Summary of Key Data points | Value
File Description: Cont_ LongCreek to Sweetwater and LongCreek to AbileneMulberry OL_ Murry to Graham
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K27 |  | Number of units | 645
|  |  | Dec PTDF cutoff point | 543
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  | Dec PTDF cutoff unit | HAMILTON
|  |  | Dec 10% unit | VALLEY_3G
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  | Dec max cumltv zone impact - cumltv zone share | 0.020694
|  |  | Dec max cumltv zone impact - cumltv zone share pt | 126
Step 5 | Enter Dennis' file name into cell K27 |  | Dec max cumltv zone impact - cumltv zone share unit | LEG_2___2
|  |  | North Zonal weighted AWGSF | 0.0056325
Step 6 | click the step one button |  | West Zonal weighted AWGSF | -0.04859
|  |  | Inc PTDF cutoff point | 102
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  | Inc PTDF cutoff unit | OKLA0A
| X6:X30, or to the end of the selected list. |  | Inc 10% unit | MRGNCG_3G
|  |  | Inc max cumltv zone impact - cumltv zone share | 0.021065
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  | Inc max cumltv zone impact - cumltv zone share pt | 28
| of the formulas in columns L:V (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  | Inc max cumltv zone impact - cumltv zone share unit | MRGNFG_6G
| If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct leng |  | North Zonal weighted AWGSF | 0.0056325
| It is only necessary to match the Distributed Slack - Dec worksheet. |  | West Zonal weighted AWGSF | -0.04859
|  |  | Min of zone correlation | 0.029973
Step 9 | Click the step 2 button |  | Bounary gen in West Zone | 0
| The last file saved will still be open, yopu will need to close this file. |  | Bounary gen in soucre zone as % of line | 0%
| This sheet willno longer be open. |  | Bounary gen in North Zone | 0
|  |  | Bounary gen in soucre zone as % of line | 0
|  |  | OL element line rating | 186
|  |  | North Zonal weighted AWGSF | 0.0056325
|  | NW_043009automation.xls | West Zonal weighted AWGSF | -0.04859
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ LongCreek to Sweetwater and LongCreek to AbileneMulberry OL_ Murry to Graham |  | i_PTDF_DEC_pt | 543 |  | LEG_2___2 | Unit at max
1433 | GRHAMSES_1G | 1 | North | YES | 0.069041 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.11763 | 242 | 242 | 16.7079 | 242 |  |  | 0.11763 | 28.4668 | 0.0040193 | 0.0090649 |  |  | i_10pctunit | 43 |  | 126 | # units @ max
1600 | BARTNWND_1G | 1 | North | YES | 0.039674 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.088264 | 0 | 120 | 4.7609 | 120 |  |  | 0.088264 | 10.5917 | 0.0060124 | 0.012438 |  |  | # units | 645 |  | 0.020694 | delta max
344 | MRSSHPRD | 1 | North | YES | 0.023526 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.072116 | 0 | 0 | 0 | 0 |  |  | 0.072116 | 0 | 0.0060124 | 0.012438 | [5 empty] | Delta
345 | MRSSHPRD01 | 2 | North | YES | 0.023526 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.072116 | 0 | 0 | 0 | 0 |  |  | 0.072116 | 0 | 0.0060124 | 0.012438 | Weighted Shift Factors |  |  |  | 1 | 0.0050455
503 | NTHTEXAS01 | 1 | North | YES | 0.013714 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.062304 | 18 | 18 | 0.24685 | 18 |  |  | 0.062304 | 1.1215 | 0.0063114 | 0.012795 | North | 0.0056325 |  |  | 2 | 0.0064253
504 | NTHTEXAS02 | 2 | North | YES | 0.013714 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.062304 | 18 | 18 | 0.24685 | 18 |  |  | 0.062304 | 1.1215 | 0.0066103 | 0.013152 | West | -0.04859 |  |  | 3 | 0.0064253
505 | NTHTEXAS03 | 3 | North | YES | 0.013714 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.062304 | 38 | 38 | 0.52113 | 38 |  |  | 0.062304 | 2.3676 | 0.0072415 | 0.013906 |  |  |  |  | 4 | 0.0064253
332 | RWMILLER01 | 1 | North | YES | 0.012978 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.061568 | 73 | 73 | 0.94739 | 73 |  |  | 0.061568 | 4.4945 | 0.0084539 | 0.015337 |  |  |  |  | 5 | 0.0064834
333 | RWMILLER02 | 2 | North | YES | 0.012978 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.061568 | 119 | 119 | 1.5444 | 119 |  |  | 0.061568 | 7.3266 | 0.01043 | 0.01767 |  |  |  |  | 6 | 0.0065416
334 | RWMILLER03 | 3 | North | YES | 0.012978 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.061568 | 208 | 208 | 2.6994 | 208 |  |  | 0.061568 | 12.8062 | 0.013885 | 0.021748 |  |  |  |  | 7 | 0.0066644
335 | RWMILLER04 | 4 | North | YES | 0.012978 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.061568 | 102 | 102 | 1.3238 | 102 |  |  | 0.061568 | 6.28 | 0.015579 | 0.023748 |  |  |  |  | 8 | 0.0068832
336 | RWMILLER05 | 5 | North | YES | 0.012978 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.061568 | 101 | 101 | 1.3108 | 101 |  |  | 0.061568 | 6.2184 | 0.017257 | 0.025728 |  |  |  |  | 9 | 0.0072398
1479 | WFCOGEN_1G | 1 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0 | 0.017257 | 0.025728 |  |  |  |  | 10 | 0.0078631
1479 | WFCOGEN_1G | 2 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0 | 0.017257 | 0.025728 |  |  |  |  | 11 | 0.0081688
1482 | WFCOGEN_2G | 2 | North | YES | 0.012797 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0 | 0.017257 | 0.025728 |  |  |  |  | 12 | 0.0084714
1482 | WFCOGEN_2G | 1 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0 | 0.017257 | 0.025728 |  |  |  |  | 13 | 0.0084714
580 | JCKCNTY801 | 1 | North | YES | 0.011414 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.060004 | 288 | 288 | 3.2872 | 288 |  |  | 0.060004 | 17.2812 | 0.02204 | 0.031231 |  |  |  |  | 14 | 0.0084714
581 | JCKCNTY802 | 2 | North | YES | 0.011414 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.060004 | 147 | 147 | 1.6779 | 147 |  |  | 0.060004 | 8.8206 | 0.024481 | 0.03404 |  |  |  |  | 15 | 0.0084714
582 | JCKCNTY803 | 3 | North | YES | 0.011414 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.060004 | 147 | 147 | 1.6779 | 147 |  |  | 0.060004 | 8.8206 | 0.026923 | 0.036849 |  |  |  |  | 16 | 0.0084714
1432 | GRHAMSES_2G | 2 | North | YES | 0.01108 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.05967 | 366 | 366 | 4.0553 | 366 |  |  | 0.05967 | 21.8393 | 0.033002 | 0.043803 |  |  |  |  | 17 | 0.0091911
1437 | MESQUITW_1G | 1 | North | YES | 0.01108 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.05967 | 0 | 400 | 4.432 | 400 |  |  | 0.05967 | 23.8681 | 0.039645 | 0.051404 |  |  |  |  | 18 | 0.0095584
1438 | MESQUITW_2G | 1 | North | YES | 0.01108 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.05967 | 0 | 236 | 2.6149 | 236 |  |  | 0.05967 | 14.0822 | 0.043565 | 0.055888 |  |  |  |  | 19 | 0.0099257
1442 | COKFIELD_5 | 1 | North | YES | 0.01108 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.05967 | 0 | 165 | 1.8282 | 165 |  |  | 0.05967 | 9.8456 | 0.046306 | 0.059023 |  |  |  |  | 20 | 0.010801
728 | WOLFRIDGE801 | 1 | North | YES | 0.00863 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.05722 | 0 | 112.5 | 0.97088 | 112.5 |  |  | 0.05722 | 6.4373 | 0.048174 | 0.061073 |  |  |  |  | 21 | 0.011758
1453 | WCPWRCO_1G | 1 | North | YES | 0.007071 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.055661 | 204 | 204 | 1.4425 | 204 |  |  | 0.055661 | 11.3549 | 0.051562 | 0.064689 |  |  |  |  | 22 | 0.012323
1454 | WCPWRCO_2G | 2 | North | YES | 0.007071 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.055661 | 204 | 204 | 1.4425 | 204 |  |  | 0.055661 | 11.3549 | 0.05495 | 0.068305 |  |  |  |  | 23 | 0.012718
1455 | WCPWRCO_3G | 3 | North | YES | 0.007071 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.055661 | 242 | 242 | 1.7112 | 242 |  |  | 0.055661 | 13.47 | 0.05897 | 0.072594 |  |  |  |  | 24 | 0.012899
1861 | EAGLEMNT_1G | MB | North | YES | 0.006645 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0 | 0.05897 | 0.072594 |  |  |  |  | 25 | 0.013127
1862 | EAGLEMNT_2G | MB | North | YES | 0.006645 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0 | 0.05897 | 0.072594 |  |  |  |  | 26 | 0.013354
1863 | EAGLEMNT_3G | MB | North | YES | 0.006645 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0 | 0.05897 | 0.072594 |  |  |  |  | 27 | 0.013624
923 | SPENCER_G4 | 1 | North | YES | 0.006131 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.054721 | 61 | 61 | 0.37399 | 61 |  |  | 0.054721 | 3.338 | 0.059983 | 0.073657 |  |  |  |  | 28 | 0.013624
924 | SPENCER_G5 | 1 | North | YES | 0.006131 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.054721 | 66 | 66 | 0.40465 | 66 |  |  | 0.054721 | 3.6116 | 0.061079 | 0.074807 |  |  |  |  | 29 | 0.013624
6948 | DENISNDM | 1 | North | YES | 0.005237 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.053827 | 0 | 0 | 0 | 0 |  |  | 0.053827 | 0 | 0.061079 | 0.074807 |  |  |  |  | 30 | 0.013624
6948 | DENISNDM | 2 | North | YES | 0.005237 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.053827 | 0 | 0 | 0 | 0 |  |  | 0.053827 | 0 | 0.061079 | 0.074807 |  |  |  |  | 31 | 0.013674
2371 | COLLIN_1G | MB | North | YES | 0.005219 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.053809 | 0 | 0 | 0 | 0 |  |  | 0.053809 | 0 | 0.061079 | 0.074807 |  |  |  |  | 32 | 0.013728
1687 | VALLEY_1G | 1 | North | YES | 0.005154 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.053744 | 170 | 170 | 0.87618 | 170 |  |  | 0.053744 | 9.1365 | 0.063903 | 0.077716 |  |  |  |  | 33 | 0.013728
1688 | VALLEY_2G | 2 | North | YES | 0.005154 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.053744 | 527 | 527 | 2.7162 | 527 |  |  | 0.053744 | 28.3232 | 0.072655 | 0.086736 |  |  |  |  | 34 | 0.013728
2381 | NTHLK1_G | 1 | North | YES | 0.005044 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.053634 | 156 | 156 | 0.78686 | 156 |  |  | 0.053634 | 8.3669 | 0.075246 | 0.0894 |  |  |  |  | 35 | 0.013728
2382 | NTHLK2_G | 2 | North | YES | 0.005044 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.053634 | 181 | 181 | 0.91296 | 181 |  |  | 0.053634 | 9.7078 | 0.078253 | 0.092491 |  |  |  |  | 36 | 0.013814
2383 | NTHLK3_G | 3 | North | YES | 0.005044 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.053634 | 329 | 329 | 1.6595 | 329 |  |  | 0.053634 | 17.6457 | 0.083717 | 0.09811 |  |  |  |  | 37 | 0.01408
1947 | HANDLEY_3G | 3 | North | YES | 0.005036 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.053626 | 395 | 395 | 1.9892 | 395 |  |  | 0.053626 | 21.1824 | 0.090278 | 0.10486 |  |  |  |  | 38 | 0.014154
1949 | HANDLEY_5G | 5 | North | YES | 0.005036 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.053626 | 435 | 435 | 2.1907 | 435 |  |  | 0.053626 | 23.3274 | 0.097502 | 0.11228 |  |  |  |  | 39 | 0.014239
1689 | VALLEY_3G | 3 | North | YES | 0.005034 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.053624 | 375 | 375 | 1.8878 | 375 |  |  | 0.053624 | 20.1091 | 0.10373 | 0.11869 |  |  |  |  | 40 | 0.014393
11691 | KMICHICT1_G | 1 | North | YES | 0.005034 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.053624 | 144 | 144 | 0.7249 | 144 |  |  | 0.053624 | 7.7219 | 0.10612 | 0.12115 |  |  |  |  | 41 | 0.014578
11692 | KMICHICT2_G | 2 | North | YES | 0.005034 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.053624 | 146 | 146 | 0.73496 | 146 |  |  | 0.053624 | 7.8291 | 0.10855 | 0.12364 |  |  |  |  | 42 | 0.014782
11693 | KMICHIST3_G | 3 | North | YES | 0.005034 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.053624 | 312 | 312 | 1.5706 | 312 |  |  | 0.053624 | 16.7308 | 0.11373 | 0.12897 |  |  |  |  | 43 | 0.014957
11694 | KMICHICT4_G | 4 | North | YES | 0.005034 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.053624 | 144 | 144 | 0.7249 | 144 |  |  | 0.053624 | 7.7219 | 0.11612 | 0.13143 |  |  |  |  | 44 | 0.015024
11695 | KMICHICT5_G | 5 | North | YES | 0.005034 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.053624 | 148 | 148 | 0.74503 | 148 |  |  | 0.053624 | 7.9364 | 0.11858 | 0.13395 |  |  |  |  | 45 | 0.015092
11696 | KMICHIST6_G | 6 | North | YES | 0.005034 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.053624 | 310 | 310 | 1.5605 | 310 |  |  | 0.053624 | 16.6235 | 0.12373 | 0.13925 |  |  |  |  | 46 | 0.015238
1948 | HANDLEY_4G | 4 | North | YES | 0.005031 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.053621 | 435 | 435 | 2.1885 | 435 |  |  | 0.053621 | 23.3252 | 0.13095 | 0.14667 |  |  |  |  | 47 | 0.015305
1675 | PEC_1G | 1 | North | YES | 0.005012 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0 | 0.13095 | 0.14667 |  |  |  |  | 48 | 0.015374
1676 | PEC_2G | 2 | North | YES | 0.005012 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0 | 0.13095 | 0.14667 |  |  |  |  | 49 | 0.015519
1677 | PEC_3G | 3 | North | YES | 0.005012 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0 | 0.13095 | 0.14667 |  |  |  |  | 50 | 0.015722
1678 | LAMARPWR_1G | 1 | North | YES | 0.005012 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.053602 | 160 | 160 | 0.80192 | 160 |  |  | 0.053602 | 8.5764 | 0.13361 | 0.14941 |  |  |  |  | 51 | 0.015722
1679 | LAMARPWR_2G | 2 | North | YES | 0.005012 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.053602 | 156 | 156 | 0.78187 | 156 |  |  | 0.053602 | 8.3619 | 0.1362 | 0.15207 |  |  |  |  | 52 | 0.015722
1680 | LAMARPWR_3G | 3 | North | YES | 0.005012 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.053602 | 196 | 196 | 0.98235 | 196 |  |  | 0.053602 | 10.506 | 0.13946 | 0.15541 |  |  |  |  | 53 | 0.015722
1681 | LAMARPWR_4G | 4 | North | YES | 0.005012 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.053602 | 156 | 156 | 0.78187 | 156 |  |  | 0.053602 | 8.3619 | 0.14205 | 0.15808 |  |  |  |  | 54 | 0.015796
1682 | LAMARPWR_5G | 5 | North | YES | 0.005012 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.053602 | 157 | 157 | 0.78688 | 157 |  |  | 0.053602 | 8.4155 | 0.14465 | 0.16076 |  |  |  |  | 55 | 0.015867
1683 | LAMARPWR_6G | 6 | North | YES | 0.005012 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.053602 | 198 | 198 | 0.99238 | 198 |  |  | 0.053602 | 10.6132 | 0.14794 | 0.16414 |  |  |  |  | 56 | 0.015958
1701 | MOSES_1G | 1 | North | YES | 0.004963 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 558 | 2.7694 | 558 |  |  | 0.053553 | 29.8827 | 0.15721 | 0.17365 |  |  |  |  | 57 | 0.016029
1702 | MOSES_2G | 2 | North | YES | 0.004963 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 579 | 2.8736 | 579 |  |  | 0.053553 | 31.0073 | 0.16683 | 0.18353 |  |  |  |  | 58 | 0.016102
1703 | MOSES_3G | 3 | North | YES | 0.004963 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 808 | 4.0101 | 808 |  |  | 0.053553 | 43.271 | 0.18025 | 0.1973 |  |  |  |  | 59 | 0.016193
5925 | DCEAST | EQ | North | YES | 0.004963 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.053553 | 0 | 0 | 0 | 0 |  |  | 0.053553 | 0 | 0.18025 | 0.1973 |  |  |  |  | 60 | 0.016441
842 | OLINGER_G1 | 1 | North | YES | 0.004881 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.053471 | 79 | 79 | 0.3856 | 79 |  |  | 0.053471 | 4.2242 | 0.18156 | 0.19865 |  |  |  |  | 61 | 0.016698
843 | OLINGER_G2 | 1 | North | YES | 0.004881 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.053471 | 110 | 110 | 0.53691 | 110 |  |  | 0.053471 | 5.8818 | 0.18339 | 0.20052 |  |  |  |  | 62 | 0.017057
844 | OLINGER_G3 | 1 | North | YES | 0.004881 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.053471 | 150 | 150 | 0.73215 | 150 |  |  | 0.053471 | 8.0207 | 0.18588 | 0.20308 |  |  |  |  | 63 | 0.017057
845 | OLINGER_G4 | 1 | North | YES | 0.004881 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.053471 | 76 | 76 | 0.37096 | 76 |  |  | 0.053471 | 4.0638 | 0.18714 | 0.20437 |  |  |  |  | 64 | 0.01709
837 | NEWMAN_G5 | 1 | North | YES | 0.004866 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.053456 | 40 | 40 | 0.19464 | 40 |  |  | 0.053456 | 2.1382 | 0.1878 | 0.20505 |  |  |  |  | 65 | 0.017136
948 | STEAM1 | 1 | North | YES | 0.004863 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.053453 | 20 | 20 | 0.09726 | 20 |  |  | 0.053453 | 1.0691 | 0.18814 | 0.20539 |  |  |  |  | 66 | 0.017199
949 | STEAM2 | 1 | North | YES | 0.004863 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.053453 | 26 | 26 | 0.12644 | 26 |  |  | 0.053453 | 1.3898 | 0.18857 | 0.20584 |  |  |  |  | 67 | 0.017231
950 | STEAM3 | 1 | North | YES | 0.004863 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.053453 | 42 | 42 | 0.20425 | 42 |  |  | 0.053453 | 2.245 | 0.18927 | 0.20655 |  |  |  |  | 68 | 0.017247
2451 | LKHB1_G | 1 | North | YES | 0.004769 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.053359 | 391 | 391 | 1.8647 | 391 |  |  | 0.053359 | 20.8635 | 0.19576 | 0.21319 |  |  |  |  | 69 | 0.017256
2452 | LKHB2_G | 2 | North | YES | 0.004769 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.053359 | 516 | 516 | 2.4608 | 516 |  |  | 0.053359 | 27.5334 | 0.20433 | 0.22196 |  |  |  |  | 70 | 0.017266
12411 | FPLEFR1A_G | 1 | North | YES | 0.004751 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.053341 | 161 | 161 | 0.76491 | 161 |  |  | 0.053341 | 8.5879 | 0.207 | 0.2247 |  |  |  |  | 71 | 0.017284
12412 | FPLEFR1B_G | 2 | North | YES | 0.004751 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.053341 | 164 | 164 | 0.77916 | 164 |  |  | 0.053341 | 8.748 | 0.20973 | 0.22748 |  |  |  |  | 72 | 0.017433
12413 | FPLEFR1C_G | 3 | North | YES | 0.004751 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.053341 | 164 | 164 | 0.77916 | 164 |  |  | 0.053341 | 8.748 | 0.21245 | 0.23027 |  |  |  |  | 73 | 0.017631
12414 | FPLEFR1S_G | 4 | North | YES | 0.004751 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.053341 | 414 | 414 | 1.9669 | 414 |  |  | 0.053341 | 22.0833 | 0.21933 | 0.2373 |  |  |  |  | 74 | 0.017692
12421 | FPLEFR2A_G | 1 | North | YES | 0.004751 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.053341 | 162 | 162 | 0.76966 | 162 |  |  | 0.053341 | 8.6413 | 0.22202 | 0.24005 |  |  |  |  | 75 | 0.017753
12422 | FPLEFR2B_G | 2 | North | YES | 0.004751 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.053341 | 161 | 161 | 0.76491 | 161 |  |  | 0.053341 | 8.5879 | 0.22469 | 0.24279 |  |  |  |  | 76 | 0.017815
12423 | FPLEFR2C_G | 3 | North | YES | 0.004751 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.053341 | 163 | 163 | 0.77441 | 163 |  |  | 0.053341 | 8.6946 | 0.2274 | 0.24555 |  |  |  |  | 77 | 0.017971
12424 | FPLEFR2S_G | 4 | North | YES | 0.004751 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.053341 | 415 | 415 | 1.9717 | 415 |  |  | 0.053341 | 22.1366 | 0.23429 | 0.2526 |  |  |  |  | 78 | 0.018032
12440 | PARKD_1SVC8 | 1 | North | YES | 0.004735 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.053325 | 0 | 0 | 0 | 0 |  |  | 0.053325 | 0 | 0.23429 | 0.2526 |  |  |  |  | 79 | 0.018093
12449 | PARKD_2SVC8 | 1 | North | YES | 0.004735 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.053325 | 0 | 0 | 0 | 0 |  |  | 0.053325 | 0 | 0.23429 | 0.2526 |  |  |  |  | 80 | 0.018154
2413 | MTCK6_G | 6 | North | YES | 0.004678 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.053268 | 118 | 118 | 0.552 | 118 |  |  | 0.053268 | 6.2857 | 0.23625 | 0.25461 |  |  |  |  | 81 | 0.018311
2414 | MTCK7_G | 7 | North | YES | 0.004678 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.053268 | 115 | 115 | 0.53797 | 115 |  |  | 0.053268 | 6.1258 | 0.23816 | 0.25656 |  |  |  |  | 82 | 0.018311
2417 | MTCK8_G | 8 | North | YES | 0.004678 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.053268 | 556 | 556 | 2.601 | 556 |  |  | 0.053268 | 29.6171 | 0.2474 | 0.26599 |  |  |  |  | 83 | 0.018311
3097 | MARTLAKE_1G | 1 | North | YES | 0.004479 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 790 | 3.5384 | 790 |  |  | 0.053069 | 41.9247 | 0.26052 | 0.27934 |  |  |  |  | 84 | 0.018353
3098 | MARTLAKE_2G | 2 | North | YES | 0.004479 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 795 | 3.5608 | 795 |  |  | 0.053069 | 42.19 | 0.27372 | 0.29277 |  |  |  |  | 85 | 0.018393
3099 | MARTLAKE_3G | 3 | North | YES | 0.004479 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 804 | 3.6011 | 804 |  |  | 0.053069 | 42.6677 | 0.28708 | 0.30636 |  |  |  |  | 86 | 0.01859
13116 | TGATEWAY_1G | 1 | North | YES | 0.004442 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.053032 | 151 | 151 | 0.67074 | 151 |  |  | 0.053032 | 8.0079 | 0.28958 | 0.30891 |  |  |  |  | 87 | 0.018819
13117 | TGATEWAY_2G | 2 | North | YES | 0.004442 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.053032 | 130 | 130 | 0.57746 | 130 |  |  | 0.053032 | 6.8942 | 0.29174 | 0.31111 |  |  |  |  | 88 | 0.01905
13118 | TGATEWAY_3G | 3 | North | YES | 0.004442 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.053032 | 148 | 148 | 0.65742 | 148 |  |  | 0.053032 | 7.8488 | 0.2942 | 0.3136 |  |  |  |  | 89 | 0.019284
13119 | TGATEWAY_4G | 4 | North | YES | 0.004442 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.053032 | 399 | 399 | 1.7724 | 399 |  |  | 0.053032 | 21.1599 | 0.30083 | 0.32034 |  |  |  |  | 90 | 0.019326
3348 | CHAMPION_1G | MB | North | YES | 0.00441 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.053 | 0 | 0 | 0 | 0 |  |  | 0.053 | 0 | 0.30083 | 0.32034 |  |  |  |  | 91 | 0.019362
3309 | ASPN_G | 1 | North | YES | 0.004406 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.052996 | 50 | 50 | 0.2203 | 50 |  |  | 0.052996 | 2.6498 | 0.30166 | 0.32119 |  |  |  |  | 92 | 0.019403
3107 | STRYKER_1G | 1 | North | YES | 0.004401 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.052991 | 182 | 182 | 0.80098 | 182 |  |  | 0.052991 | 9.6444 | 0.30468 | 0.32426 |  |  |  |  | 93 | 0.019514
3108 | STRYKER_2G | 2 | North | YES | 0.004401 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.052991 | 484 | 484 | 2.1301 | 484 |  |  | 0.052991 | 25.6478 | 0.31272 | 0.33242 |  |  |  |  | 94 | 0.019514
12322 | ENNSTRAC_1G | 1 | North | YES | 0.004392 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.052982 | 196 | 196 | 0.86083 | 196 |  |  | 0.052982 | 10.3845 | 0.31598 | 0.33573 |  |  |  |  | 95 | 0.019528
12323 | ENNSTRAC_2G | 2 | North | YES | 0.004392 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.052982 | 116 | 116 | 0.50947 | 116 |  |  | 0.052982 | 6.1459 | 0.3179 | 0.33769 |  |  |  |  | 96 | 0.019576
1892 | DECRDOVA_2G | A | North | YES | 0.004383 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.052973 | 70 | 70 | 0.30681 | 70 |  |  | 0.052973 | 3.7081 | 0.31906 | 0.33887 |  |  |  |  | 97 | 0.019705
1893 | DECRDOVA_3G | B | North | YES | 0.004383 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.052973 | 69 | 69 | 0.30243 | 69 |  |  | 0.052973 | 3.6552 | 0.32021 | 0.34003 |  |  |  |  | 98 | 0.019756
1894 | DECRDOVA_4G | C | North | YES | 0.004383 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.052973 | 69 | 69 | 0.30243 | 69 |  |  | 0.052973 | 3.6552 | 0.32136 | 0.3412 |  |  |  |  | 99 | 0.019787
1895 | DECRDOVA_5G | D | North | YES | 0.004383 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.052973 | 68 | 68 | 0.29804 | 68 |  |  | 0.052973 | 3.6022 | 0.32249 | 0.34234 |  |  |  |  | 100 | 0.019805
1941 | MDLTHELP_1G | 1 | North | YES | 0.004375 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.052965 | 216.4 | 216.4 | 0.94675 | 216.4 |  |  | 0.052965 | 11.4617 | 0.32608 | 0.34599 |  |  |  |  | 101 | 0.019823
1942 | MDLTHELP_2G | 2 | North | YES | 0.004375 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.052965 | 216.1 | 216.1 | 0.94544 | 216.1 |  |  | 0.052965 | 11.4458 | 0.32967 | 0.34964 |  |  |  |  | 102 | 0.019841
3126 | TRINIDAD_6G | 1 | North | YES | 0.004321 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.052911 | 224 | 224 | 0.9679 | 224 |  |  | 0.052911 | 11.8521 | 0.33339 | 0.35341 |  |  |  |  | 103 | 0.019858
1937 | MDLTHELP_5G | 5 | North | YES | 0.004242 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.052832 | 224 | 224 | 0.95021 | 224 |  |  | 0.052832 | 11.8344 | 0.33711 | 0.35718 |  |  |  |  | 104 | 0.019914
1938 | MDLTHELP_6G | 6 | North | YES | 0.004242 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.052832 | 226 | 226 | 0.95869 | 226 |  |  | 0.052832 | 11.9401 | 0.34086 | 0.36098 |  |  |  |  | 105 | 0.01997
1943 | MDLTHELP_3G | 3 | North | YES | 0.004242 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.052832 | 212 | 212 | 0.8993 | 212 |  |  | 0.052832 | 11.2004 | 0.34438 | 0.36455 |  |  |  |  | 106 | 0.020023
1944 | MDLTHELP_4G | 4 | North | YES | 0.004242 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.052832 | 211 | 211 | 0.89506 | 211 |  |  | 0.052832 | 11.1476 | 0.34789 | 0.3681 |  |  |  |  | 107 | 0.020071
366 | JNSNCNTY802 | 1 | North | YES | 0.004093 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.052683 | 0 | 0 | 0 | 0 |  |  | 0.052683 | 0 | 0.34789 | 0.3681 |  |  |  |  | 108 | 0.02012
367 | JNSNCNTY802 | 2 | North | YES | 0.004093 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.052683 | 0 | 0 | 0 | 0 |  |  | 0.052683 | 0 | 0.34789 | 0.3681 |  |  |  |  | 109 | 0.020166
13134 | CALFREST_4G | 4 | North | YES | 0.004093 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.052683 | 151.5 | 151.5 | 0.62009 | 151.5 |  |  | 0.052683 | 7.9815 | 0.35041 | 0.37064 |  |  |  |  | 110 | 0.020211
13135 | CALFREST_5G | 5 | North | YES | 0.004093 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.052683 | 152.3 | 152.3 | 0.62336 | 152.3 |  |  | 0.052683 | 8.0237 | 0.35294 | 0.3732 |  |  |  |  | 111 | 0.020211
13136 | CALFREST_6G | 6 | North | YES | 0.004093 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.052683 | 177.5 | 177.5 | 0.72651 | 177.5 |  |  | 0.052683 | 9.3513 | 0.35588 | 0.37617 |  |  |  |  | 112 | 0.020211
13131 | CALFREST_1G | 1 | North | YES | 0.004077 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.052667 | 150.7 | 150.7 | 0.6144 | 150.7 |  |  | 0.052667 | 7.937 | 0.35839 | 0.3787 |  |  |  |  | 113 | 0.020236
13132 | CALFREST_2G | 2 | North | YES | 0.004077 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.052667 | 151 | 151 | 0.61563 | 151 |  |  | 0.052667 | 7.9528 | 0.36089 | 0.38123 |  |  |  |  | 114 | 0.020262
13133 | CALFREST_3G | 3 | North | YES | 0.004077 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.052667 | 177.4 | 177.4 | 0.72326 | 177.4 |  |  | 0.052667 | 9.3432 | 0.36384 | 0.38421 |  |  |  |  | 115 | 0.020292
3381 | BBRN_1G | 1 | North | YES | 0.004017 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.052607 | 0 | 618 | 2.4825 | 618 |  |  | 0.052607 | 32.5113 | 0.3741 | 0.39456 |  |  |  |  | 116 | 0.020316
3382 | BBRN_2G | 2 | North | YES | 0.004017 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.052607 | 0 | 589 | 2.366 | 589 |  |  | 0.052607 | 30.9857 | 0.38389 | 0.40443 |  |  |  |  | 117 | 0.020341
1889 | DECRDOVA_1G | 1 | North | YES | 0.003993 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.052583 | 779 | 779 | 3.1105 | 779 |  |  | 0.052583 | 40.9623 | 0.39683 | 0.41747 |  |  |  |  | 118 | 0.020369
244 | WHITNYDM01 | 1 | North | YES | 0.003812 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.052402 | 0 | 0 | 0 | 0 |  |  | 0.052402 | 0 | 0.39683 | 0.41747 |  |  |  |  | 119 | 0.020458
245 | WHITNYDM02 | 2 | North | YES | 0.003812 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.052402 | 0 | 0 | 0 | 0 |  |  | 0.052402 | 0 | 0.39683 | 0.41747 |  |  |  |  | 120 | 0.020542
1643 | SLSTR1PP_1G | 1 | North | YES | 0.003654 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.052244 | 0 | 60 | 0.21924 | 60 |  |  | 0.052244 | 3.1347 | 0.39782 | 0.41847 |  |  |  |  | 121 | 0.020648
48721 | LEG_1___1 | 1 | North | YES | 0.003651 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.052241 | 0 | 827 | 3.0194 | 827 |  |  | 0.052241 | 43.2035 | 0.41156 | 0.43223 |  |  |  |  | 122 | 0.020648
48722 | LEG_2___2 | 2 | North | YES | 0.003651 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.052241 | 0 | 819 | 2.9902 | 819 |  |  | 0.052241 | 42.7856 | 0.42516 | 0.44585 |  |  |  |  | 123 | 0.020648
39960 | TNTNPONE_18 | 1 | North | YES | 0.003514 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.052104 | 0 | 152.3 | 0.53518 | 152.3 |  |  | 0.052104 | 7.9355 | 0.42769 | 0.44838 |  |  |  |  | 124 | 0.02065
39970 | TNTNPONE_28 | 1 | North | YES | 0.003514 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.052104 | 0 | 153 | 0.53764 | 153 |  |  | 0.052104 | 7.9719 | 0.43023 | 0.45092 |  |  |  |  | 125 | 0.020672
251 | BOSQUESW803 | 2 | North | YES | 0.003372 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.051962 | 150 | 150 | 0.5058 | 150 |  |  | 0.051962 | 7.7943 | 0.43272 | 0.4534 |  |  |  |  | 126 | 0.020694
253 | BOSQUESW804 | 2 | North | YES | 0.003372 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.051962 | 80 | 80 | 0.26976 | 80 |  |  | 0.051962 | 4.157 | 0.43405 | 0.45473 |  |  |  |  | 127 | 0.020691
238 | BOSQUESW505 | 1 | North | YES | 0.003321 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.051911 | 255 | 255 | 0.84686 | 255 |  |  | 0.051911 | 13.2374 | 0.43829 | 0.45894 |  |  |  |  | 128 | 0.020688
239 | BOSQUESW502 | 1 | North | YES | 0.003321 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.051911 | 149 | 149 | 0.49483 | 149 |  |  | 0.051911 | 7.7348 | 0.44076 | 0.4614 |  |  |  |  | 129 | 0.020679
247 | BOSQUESW501 | 2 | North | YES | 0.003321 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.051911 | 156 | 156 | 0.51808 | 156 |  |  | 0.051911 | 8.0982 | 0.44335 | 0.46398 |  |  |  |  | 130 | 0.020674
3403 | THOUSE_1G | 1 | North | YES | 0.003296 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.051886 | 563 | 563 | 1.8556 | 563 |  |  | 0.051886 | 29.2119 | 0.4527 | 0.47328 |  |  |  |  | 131 | 0.020654
3404 | THOUSE_2G | 2 | North | YES | 0.003296 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.051886 | 807 | 807 | 2.6599 | 807 |  |  | 0.051886 | 41.8722 | 0.46611 | 0.48662 |  |  |  |  | 132 | 0.020642
3416 | LAKE_CRK1_G | 1 | North | YES | 0.003177 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.051767 | 75 | 75 | 0.23827 | 75 |  |  | 0.051767 | 3.8825 | 0.46735 | 0.48785 |  |  |  |  | 133 | 0.02063
3417 | LAKE_CRK2_G | 2 | North | YES | 0.003177 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.051767 | 222 | 222 | 0.70529 | 222 |  |  | 0.051767 | 11.4923 | 0.47104 | 0.49151 |  |  |  |  | 134 | 0.020582
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.003174 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.051764 | 32 | 32 | 0.10157 | 32 |  |  | 0.051764 | 1.6565 | 0.47157 | 0.49204 |  |  |  |  | 135 | 0.020512
990 | GIBN_CREK_G1 | 1 | North | YES | 0.003173 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.051763 | 0 | 463 | 1.4691 | 463 |  |  | 0.051763 | 23.9664 | 0.47926 | 0.49967 |  |  |  |  | 136 | 0.020503
32886 | BRYN_ATKINS3 | MB | North | YES | 0.003171 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0 | 0.47926 | 0.49967 |  |  |  |  | 137 | 0.020475
32887 | BRYN_ATKINS6 | MB | North | YES | 0.003171 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0 | 0.47926 | 0.49967 |  |  |  |  | 138 | 0.020471
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.003171 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.051761 | 17 | 17 | 0.053907 | 17 |  |  | 0.051761 | 0.87994 | 0.47954 | 0.49995 |  |  |  |  | 139 | 0.020413
32890 | BRYN_ATKINS4 | MB | North | YES | 0.003171 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0 | 0.47954 | 0.49995 |  |  |  |  | 140 | 0.020413
32891 | BRYN_ATKINS5 | MB | North | YES | 0.003171 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0 | 0.47954 | 0.49995 |  |  |  |  | 141 | 0.020413
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.003164 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.051754 | 48 | 48 | 0.15187 | 48 |  |  | 0.051754 | 2.4842 | 0.48034 | 0.50074 |  |  |  |  | 142 | 0.020411
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.003164 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.051754 | 46 | 46 | 0.14554 | 46 |  |  | 0.051754 | 2.3807 | 0.4811 | 0.5015 |  |  |  |  | 143 | 0.020411
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.003164 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.051754 | 105 | 105 | 0.33222 | 105 |  |  | 0.051754 | 5.4342 | 0.48285 | 0.50323 |  |  |  |  | 144 | 0.020411
1877 | WLFHOLW_1G | 1 | North | YES | 0.003099 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.051689 | 217.3 | 217.3 | 0.67341 | 217.3 |  |  | 0.051689 | 11.2321 | 0.48646 | 0.50681 |  |  |  |  | 145 | 0.020405
1878 | WLFHOLW_2G | 2 | North | YES | 0.003099 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.051689 | 215.7 | 215.7 | 0.66845 | 215.7 |  |  | 0.051689 | 11.1494 | 0.49004 | 0.51036 |  |  |  |  | 146 | 0.020399
1879 | WLFHOLW_3G | 3 | North | YES | 0.003099 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.051689 | 272.4 | 272.4 | 0.84417 | 272.4 |  |  | 0.051689 | 14.0801 | 0.49456 | 0.51484 |  |  |  |  | 147 | 0.020385
48671 | FTR_GT1_5105 | 1 | North | YES | 0.003066 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.051656 | 154.2 | 154.2 | 0.47278 | 154.2 |  |  | 0.051656 | 7.9654 | 0.49713 | 0.51738 |  |  |  |  | 148 | 0.020353
48672 | FTR_GT2_5110 | 2 | North | YES | 0.003066 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.051656 | 159 | 159 | 0.48749 | 159 |  |  | 0.051656 | 8.2133 | 0.49977 | 0.52 |  |  |  |  | 149 | 0.020321
48673 | FTR_GT3_5085 | 3 | North | YES | 0.003066 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.051656 | 158 | 158 | 0.48443 | 158 |  |  | 0.051656 | 8.1617 | 0.50239 | 0.52259 |  |  |  |  | 150 | 0.02028
48674 | FTR_CN4_5095 | 4 | North | YES | 0.003066 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.051656 | 380 | 380 | 1.1651 | 380 |  |  | 0.051656 | 19.6294 | 0.5087 | 0.52885 |  |  |  |  | 151 | 0.020255
1898 | COMCHEPK_1G | 1 | North | YES | 0.002865 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.051455 | 0 | 0 | 0 | 0 |  |  | 0.051455 | 0 | 0.5087 | 0.52885 |  |  |  |  | 152 | 0.02023
1899 | COMCHEPK_2G | 2 | North | YES | 0.002865 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.051455 | 0 | 0 | 0 | 0 |  |  | 0.051455 | 0 | 0.5087 | 0.52885 |  |  |  |  | 153 | 0.020205
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.002553 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 | 0.5087 | 0.52885 |  |  |  |  | 154 | 0.020144
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.002553 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 | 0.5087 | 0.52885 |  |  |  |  | 155 | 0.020144
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.002553 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 | 0.5087 | 0.52885 |  |  |  |  | 156 | 0.020144
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.002553 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 | 0.5087 | 0.52885 |  |  |  |  | 157 | 0.020144
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.002553 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 | 0.5087 | 0.52885 |  |  |  |  | 158 | 0.020144
48885 | THW_5152 | B | Houston | YES | 0.002496 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.051086 | 59 | 59 |  |  |  |  | 0.051086 | 3.0141 | 0.50968 | 0.52981 |  |  |  |  | 159 | 0.020144
48885 | THW_5152 | A | Houston | YES | 0.002496 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.051086 | 58 | 58 |  |  |  |  | 0.051086 | 2.963 | 0.51064 | 0.53075 |  |  |  |  | 160 | 0.020144
48886 | THW_5354 | D | Houston | YES | 0.002496 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.051086 | 58 | 58 |  |  |  |  | 0.051086 | 2.963 | 0.51161 | 0.53169 |  |  |  |  | 161 | 0.020144
48886 | THW_5354 | C | Houston | YES | 0.002496 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.051086 | 57 | 57 |  |  |  |  | 0.051086 | 2.9119 | 0.51255 | 0.53262 |  |  |  |  | 162 | 0.020124
48887 | THW_5556 | E | Houston | YES | 0.002496 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.051086 | 59 | 59 |  |  |  |  | 0.051086 | 3.0141 | 0.51353 | 0.53358 |  |  |  |  | 163 | 0.020104
48887 | THW_5556 | F | Houston | YES | 0.002496 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.051086 | 57 | 57 |  |  |  |  | 0.051086 | 2.9119 | 0.51448 | 0.53451 |  |  |  |  | 164 | 0.020085
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.002492 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.051082 | 398 | 398 |  |  |  |  | 0.051082 | 20.3307 | 0.52109 | 0.54098 |  |  |  |  | 165 | 0.020065
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.002488 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.051078 | 162.8 | 162.8 |  |  |  |  | 0.051078 | 8.3155 | 0.5238 | 0.54363 |  |  |  |  | 166 | 0.020045
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.002488 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.051078 | 161.4 | 161.4 |  |  |  |  | 0.051078 | 8.244 | 0.52648 | 0.54625 |  |  |  |  | 167 | 0.020026
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.002488 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.051078 | 158.9 | 158.9 |  |  |  |  | 0.051078 | 8.1163 | 0.52912 | 0.54884 |  |  |  |  | 168 | 0.019889
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.002488 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.051078 | 269.2 | 269.2 |  |  |  |  | 0.051078 | 13.7503 | 0.53359 | 0.55322 |  |  |  |  | 169 | 0.019833
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837 | 0.53644 | 0.55601 |  |  |  |  | 170 | 0.019778
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837 | 0.5393 | 0.55881 |  |  |  |  | 171 | 0.019723
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837 | 0.54216 | 0.56161 |  |  |  |  | 172 | 0.019631
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.002477 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.051067 | 0 | 0 |  |  |  |  | 0.051067 | 0 | 0.54216 | 0.56161 |  |  |  |  | 173 | 0.019571
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.002474 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.051064 | 744 | 744 |  |  |  |  | 0.051064 | 37.9918 | 0.55451 | 0.57371 |  |  |  |  | 174 | 0.019511
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.002474 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 | 0.55451 | 0.57371 |  |  |  |  | 175 | 0.019452
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.002474 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 | 0.55451 | 0.57371 |  |  |  |  | 176 | 0.019452
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.002474 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 | 0.55451 | 0.57371 |  |  |  |  | 177 | 0.019193
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.002474 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 | 0.55451 | 0.57371 |  |  |  |  | 178 | 0.019193
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.002474 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 | 0.55451 | 0.57371 |  |  |  |  | 179 | 0.019193
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.002474 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 | 0.55451 | 0.57371 |  |  |  |  | 180 | 0.019193
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.002474 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 | 0.55451 | 0.57371 |  |  |  |  | 181 | 0.019193
48651 | EP_1_2 | 1 | Houston | YES | 0.002473 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0 | 0.55451 | 0.57371 |  |  |  |  | 182 | 0.019193
48651 | EP_1_2 | 2 | Houston | YES | 0.002473 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0 | 0.55451 | 0.57371 |  |  |  |  | 183 | 0.019193
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.002473 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0 | 0.55451 | 0.57371 |  |  |  |  | 184 | 0.019193
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.002468 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.051058 | 12 | 12 |  |  |  |  | 0.051058 | 0.6127 | 0.55471 | 0.5739 |  |  |  |  | 185 | 0.019193
49803 | EXN_15GT | 1 | Houston | YES | 0.002468 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 186 | 0.019193
49804 | EXN_16GT | 2 | Houston | YES | 0.002468 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 187 | 0.019193
49805 | EXN_17GT | 3 | Houston | YES | 0.002468 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 188 | 0.019189
49826 | EXN938GT | 5 | Houston | YES | 0.002468 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 189 | 0.019189
49828 | EXN941GT | 10 | Houston | YES | 0.002468 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 190 | 0.019189
49829 | EXN942GT | 11 | Houston | YES | 0.002468 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 191 | 0.019189
49830 | EXN943GT | 12 | Houston | YES | 0.002468 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 192 | 0.019189
49831 | EXN944GT | 13 | Houston | YES | 0.002468 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 193 | 0.019189
49832 | EXN945GT | 9 | Houston | YES | 0.002468 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 194 | 0.019189
49837 | EXN_GT | 4 | Houston | YES | 0.002468 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 195 | 0.019189
49838 | EXN_14GT | 14 | Houston | YES | 0.002468 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 | 0.55471 | 0.5739 |  |  |  |  | 196 | 0.019189
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.002462 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.051052 | 746 | 746 |  |  |  |  | 0.051052 | 38.085 | 0.5671 | 0.58603 |  |  |  |  | 197 | 0.019189
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.002456 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.051046 | 107 | 107 |  |  |  |  | 0.051046 | 5.4619 | 0.56888 | 0.58777 |  |  |  |  | 198 | 0.019189
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.002456 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.051046 | 108 | 108 |  |  |  |  | 0.051046 | 5.513 | 0.57067 | 0.58952 |  |  |  |  | 199 | 0.019189
48875 | THW_3132 | A | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075 | 0.57159 | 0.59042 |  |  |  |  | 200 | 0.018926
48875 | THW_3132 | B | Houston | YES | 0.002456 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.051046 | 53 | 53 |  |  |  |  | 0.051046 | 2.7054 | 0.57247 | 0.59128 |  |  |  |  | 201 | 0.018888
48877 | THW_3334 | C | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075 | 0.57338 | 0.59217 |  |  |  |  | 202 | 0.01885
48877 | THW_3334 | D | Houston | YES | 0.002456 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.051046 | 57 | 57 |  |  |  |  | 0.051046 | 2.9096 | 0.57433 | 0.5931 |  |  |  |  | 203 | 0.018831
48879 | THW_4142 | E | Houston | YES | 0.002456 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.051046 | 56 | 56 |  |  |  |  | 0.051046 | 2.8586 | 0.57526 | 0.59401 |  |  |  |  | 204 | 0.018812
48879 | THW_4142 | F | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075 | 0.57617 | 0.5949 |  |  |  |  | 205 | 0.018792
48881 | THW_4344 | G | Houston | YES | 0.002456 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.051046 | 58 | 58 |  |  |  |  | 0.051046 | 2.9607 | 0.57713 | 0.59585 |  |  |  |  | 206 | 0.018772
48881 | THW_4344 | H | Houston | YES | 0.002456 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.051046 | 58 | 58 |  |  |  |  | 0.051046 | 2.9607 | 0.5781 | 0.59679 |  |  |  |  | 207 | 0.018752
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.002444 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.051034 | 0 | 0 |  |  |  |  | 0.051034 | 0 | 0.5781 | 0.59679 |  |  |  |  | 208 | 0.018733
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.002444 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.051034 | 0 | 0 |  |  |  |  | 0.051034 | 0 | 0.5781 | 0.59679 |  |  |  |  | 209 | 0.018712
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.002442 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.051032 | 42 | 42 |  |  |  |  | 0.051032 | 2.1434 | 0.5788 | 0.59747 |  |  |  |  | 210 | 0.018692
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.002442 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.051032 | 42 | 42 |  |  |  |  | 0.051032 | 2.1434 | 0.57949 | 0.59816 |  |  |  |  | 211 | 0.018692
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.002442 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.051032 | 39 | 39 |  |  |  |  | 0.051032 | 1.9903 | 0.58014 | 0.59879 |  |  |  |  | 212 | 0.018692
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.002442 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.051032 | 39 | 39 |  |  |  |  | 0.051032 | 1.9903 | 0.58079 | 0.59942 |  |  |  |  | 213 | 0.018677
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.002441 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.051031 | 0 | 0 |  |  |  |  | 0.051031 | 0 | 0.58079 | 0.59942 |  |  |  |  | 214 | 0.018662
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.002433 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0 | 0.58079 | 0.59942 |  |  |  |  | 215 | 0.018648
48821 | SHELLG2 | 2 | Houston | YES | 0.002433 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0 | 0.58079 | 0.59942 |  |  |  |  | 216 | 0.018634
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.002433 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0 | 0.58079 | 0.59942 |  |  |  |  | 217 | 0.018634
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.002433 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0 | 0.58079 | 0.59942 |  |  |  |  | 218 | 0.018634
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.002428 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 | 0.58079 | 0.59942 |  |  |  |  | 219 | 0.018634
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.002428 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 | 0.58079 | 0.59942 |  |  |  |  | 220 | 0.018634
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.002428 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 | 0.58079 | 0.59942 |  |  |  |  | 221 | 0.018634
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.002428 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 | 0.58079 | 0.59942 |  |  |  |  | 222 | 0.018634
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.002428 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 | 0.58079 | 0.59942 |  |  |  |  | 223 | 0.018634
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.002428 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 | 0.58079 | 0.59942 |  |  |  |  | 224 | 0.018634
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.002428 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 | 0.58079 | 0.59942 |  |  |  |  | 225 | 0.018634
48845 | SOL_GT1 | 1 | Houston | YES | 0.002428 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.051018 | 16.2 | 16.2 |  |  |  |  | 0.051018 | 0.8265 | 0.58106 | 0.59969 |  |  |  |  | 226 | 0.018634
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.002428 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.051018 | 213 | 213 |  |  |  |  | 0.051018 | 10.8669 | 0.5846 | 0.60315 |  |  |  |  | 227 | 0.018634
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.002428 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.051018 | 228 | 228 |  |  |  |  | 0.051018 | 11.6322 | 0.58838 | 0.60685 |  |  |  |  | 228 | 0.018634
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.002427 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.051017 | 0 | 0 |  |  |  |  | 0.051017 | 0 | 0.58838 | 0.60685 |  |  |  |  | 229 | 0.018628
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.002427 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.051017 | 0 | 0 |  |  |  |  | 0.051017 | 0 | 0.58838 | 0.60685 |  |  |  |  | 230 | 0.018551
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.002427 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.051017 | 165 | 165 |  |  |  |  | 0.051017 | 8.4178 | 0.59112 | 0.60953 |  |  |  |  | 231 | 0.018468
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.002427 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.051017 | 176 | 176 |  |  |  |  | 0.051017 | 8.979 | 0.59405 | 0.61239 |  |  |  |  | 232 | 0.018468
48855 | SRB_GT211035 | B1 | Houston | YES | 0.002427 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.051017 | 18 | 18 |  |  |  |  | 0.051017 | 0.91831 | 0.59435 | 0.61268 |  |  |  |  | 233 | 0.018468
48855 | SRB_GT211035 | B2 | Houston | YES | 0.002427 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.051017 | 12 | 12 |  |  |  |  | 0.051017 | 0.61221 | 0.59454 | 0.61288 |  |  |  |  | 234 | 0.018408
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.002423 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.051013 | 0 | 0 |  |  |  |  | 0.051013 | 0 | 0.59454 | 0.61288 |  |  |  |  | 235 | 0.018344
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.002418 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.051008 | 163.2 | 163.2 |  |  |  |  | 0.051008 | 8.3245 | 0.59725 | 0.61553 |  |  |  |  | 236 | 0.018338
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.002418 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.051008 | 157.1 | 157.1 |  |  |  |  | 0.051008 | 8.0134 | 0.59986 | 0.61808 |  |  |  |  | 237 | 0.018333
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.002418 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.051008 | 157.5 | 157.5 |  |  |  |  | 0.051008 | 8.0338 | 0.60248 | 0.62064 |  |  |  |  | 238 | 0.018333
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.002418 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.051008 | 157 | 157 |  |  |  |  | 0.051008 | 8.0083 | 0.60509 | 0.62319 |  |  |  |  | 239 | 0.018274
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.002418 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.051008 | 282 | 282 |  |  |  |  | 0.051008 | 14.3843 | 0.60977 | 0.62777 |  |  |  |  | 240 | 0.018216
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.002415 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.051005 | 0 | 0 |  |  |  |  | 0.051005 | 0 | 0.60977 | 0.62777 |  |  |  |  | 241 | 0.018158
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.002415 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.051005 | 0 | 0 |  |  |  |  | 0.051005 | 0 | 0.60977 | 0.62777 |  |  |  |  | 242 | 0.018101
48691 | GBY_73741085 | B | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972 | 0.61055 | 0.62853 |  |  |  |  | 243 | 0.017998
48691 | GBY_73741085 | A | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972 | 0.61133 | 0.6293 |  |  |  |  | 244 | 0.017998
48692 | GBY_81821075 | D | Houston | YES | 0.002413 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.051003 | 55 | 55 |  |  |  |  | 0.051003 | 2.8052 | 0.61225 | 0.63019 |  |  |  |  | 245 | 0.017998
48692 | GBY_81821075 | C | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972 | 0.61303 | 0.63095 |  |  |  |  | 246 | 0.017981
48693 | GBY_83841065 | F | Houston | YES | 0.002413 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.051003 | 54 | 54 |  |  |  |  | 0.051003 | 2.7542 | 0.61392 | 0.63183 |  |  |  |  | 247 | 0.017963
48693 | GBY_83841065 | E | Houston | YES | 0.002413 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.051003 | 57 | 57 |  |  |  |  | 0.051003 | 2.9072 | 0.61487 | 0.63276 |  |  |  |  | 248 | 0.017943
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.0024 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 | 0.61487 | 0.63276 |  |  |  |  | 249 | 0.017926
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.0024 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 | 0.61487 | 0.63276 |  |  |  |  | 250 | 0.017906
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.0024 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 | 0.61487 | 0.63276 |  |  |  |  | 251 | 0.017885
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.0024 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 | 0.61487 | 0.63276 |  |  |  |  | 252 | 0.017885
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.002393 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | 0.61487 | 0.63276 |  |  |  |  | 253 | 0.017885
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.002393 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | 0.61487 | 0.63276 |  |  |  |  | 254 | 0.017885
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.002393 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | 0.61487 | 0.63276 |  |  |  |  | 255 | 0.017885
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.002393 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | 0.61487 | 0.63276 |  |  |  |  | 256 | 0.017885
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.002393 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | 0.61487 | 0.63276 |  |  |  |  | 257 | 0.017885
48772 | PHR_GN2_2 | MB | Houston | YES | 0.002372 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.050962 | 0 | 0 |  |  |  |  | 0.050962 | 0 | 0.61487 | 0.63276 |  |  |  |  | 258 | 0.017885
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.002342 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 259 | 0.017885
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.002342 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 260 | 0.017885
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.002342 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 261 | 0.017885
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.002342 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 262 | 0.017885
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.002342 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 263 | 0.017885
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.002342 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 264 | 0.017885
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.002342 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 265 | 0.017885
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.002342 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 266 | 0.017885
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.002342 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 267 | 0.017885
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.002342 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 268 | 0.017885
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.002342 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 269 | 0.017885
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.002342 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 270 | 0.017885
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.002342 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 271 | 0.017885
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.002342 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 272 | 0.017885
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.002342 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | 0.61487 | 0.63276 |  |  |  |  | 273 | 0.017885
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.002281 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.050871 | 166 | 166 |  |  |  |  | 0.050871 | 8.4446 | 0.61763 | 0.63544 |  |  |  |  | 274 | 0.017885
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.002281 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.050871 | 166 | 166 |  |  |  |  | 0.050871 | 8.4446 | 0.62038 | 0.63813 |  |  |  |  | 275 | 0.017885
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.002281 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.050871 | 248 | 248 |  |  |  |  | 0.050871 | 12.6161 | 0.6245 | 0.64215 |  |  |  |  | 276 | 0.017885
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.002281 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.050871 | 546 | 546 |  |  |  |  | 0.050871 | 27.7757 | 0.63357 | 0.651 |  |  |  |  | 277 | 0.017817
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.002281 | 618.1 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.050871 | 0 | 654 |  |  |  |  | 0.050871 | 33.2698 | 0.64443 | 0.66159 |  |  |  |  | 278 | 0.017749
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.002281 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.050871 | 13 | 13 |  |  |  |  | 0.050871 | 0.66133 | 0.64465 | 0.6618 |  |  |  |  | 279 | 0.017647
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.002268 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.050858 | 0 | 0 |  |  |  |  | 0.050858 | 0 | 0.64465 | 0.6618 |  |  |  |  | 280 | 0.017424
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.00226 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.05085 | 167.7 | 167.7 |  |  |  |  | 0.05085 | 8.5276 | 0.64744 | 0.66452 |  |  |  |  | 281 | 0.017156
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.00226 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.05085 | 166.4 | 166.4 |  |  |  |  | 0.05085 | 8.4615 | 0.6502 | 0.66721 |  |  |  |  | 282 | 0.017151
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.00226 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.05085 | 252.4 | 252.4 |  |  |  |  | 0.05085 | 12.8346 | 0.65439 | 0.6713 |  |  |  |  | 283 | 0.017151
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.002259 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 651 |  |  |  |  | 0.050849 | 33.1028 | 0.6652 | 0.68184 |  |  |  |  | 284 | 0.017081
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.002259 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 564 |  |  |  |  | 0.050849 | 28.679 | 0.67457 | 0.69097 |  |  |  |  | 285 | 0.017012
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.002259 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 603 |  |  |  |  | 0.050849 | 30.6621 | 0.68459 | 0.70074 |  |  |  |  | 286 | 0.016907
48730 | MNS_GT | 1 | Houston | YES | 0.002251 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.050841 | 0 | 0 |  |  |  |  | 0.050841 | 0 | 0.68459 | 0.70074 |  |  |  |  | 287 | 0.016635
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.002139 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 | 0.68459 | 0.70074 |  |  |  |  | 288 | 0.0164
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.002139 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 | 0.68459 | 0.70074 |  |  |  |  | 289 | 0.016149
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.002139 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 | 0.68459 | 0.70074 |  |  |  |  | 290 | 0.016149
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.002139 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 | 0.68459 | 0.70074 |  |  |  |  | 291 | 0.016149
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.002105 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.050695 | 0 | 0 |  |  |  |  | 0.050695 | 0 | 0.68459 | 0.70074 |  |  |  |  | 292 | 0.016149
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.002105 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.050695 | 0 | 0 |  |  |  |  | 0.050695 | 0 | 0.68459 | 0.70074 |  |  |  |  | 293 | 0.016149
13432 | SANDOW_5G | 5 | South | YES | 0.002098 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.050688 | 0 | 581 |  |  |  |  | 0.050688 | 29.4499 | 0.69424 | 0.71011 |  |  |  |  | 294 | 0.016149
49851 | DOW17000 | 37 | Houston | YES | 0.002065 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 295 | 0.016149
49858 | DOW38100 | 31 | Houston | YES | 0.002065 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 296 | 0.016149
49859 | DOW38200 | 33 | Houston | YES | 0.002065 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 297 | 0.015877
49860 | DOW38300 | 32 | Houston | YES | 0.002065 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 298 | 0.015877
49862 | DOW39100 | 36 | Houston | YES | 0.002065 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 299 | 0.015877
49863 | DOW39200 | 35 | Houston | YES | 0.002065 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 300 | 0.015877
49865 | DOW41000 | 41 | Houston | YES | 0.002065 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 301 | 0.015877
49866 | DOW42000 | 42 | Houston | YES | 0.002065 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 302 | 0.015877
49869 | DOW49000 | 45 | Houston | YES | 0.002065 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 303 | 0.015877
49870 | DOW61000 | 61 | Houston | YES | 0.002065 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 304 | 0.015877
49871 | DOW62000 | 62 | Houston | YES | 0.002065 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 305 | 0.015877
49872 | DOW63000 | 63 | Houston | YES | 0.002065 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 306 | 0.015877
49873 | DOW64000 | 64 | Houston | YES | 0.002065 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 307 | 0.015877
49876 | DOW65000 | 65 | Houston | YES | 0.002065 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 308 | 0.015877
49877 | DOW66000 | 66 | Houston | YES | 0.002065 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 309 | 0.015877
49878 | DOW67000 | 67 | Houston | YES | 0.002065 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 310 | 0.015877
49882 | DOW81000 | 81 | Houston | YES | 0.002065 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 311 | 0.015877
49884 | DOW82000 | 82 | Houston | YES | 0.002065 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 312 | 0.015877
49885 | DOW83000 | 83 | Houston | YES | 0.002065 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 313 | 0.015877
49886 | DOW84000 | 84 | Houston | YES | 0.002065 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | 0.69424 | 0.71011 |  |  |  |  | 314 | 0.015877
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.001897 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.050487 | 0 | 0 |  |  |  |  | 0.050487 | 0 | 0.69424 | 0.71011 |  |  |  |  | 315 | 0.015877
48731 | CBE_GT1 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 | 0.6955 | 0.71133 |  |  |  |  | 316 | 0.015877
48732 | CBE_GT2 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 | 0.69676 | 0.71256 |  |  |  |  | 317 | 0.015877
48733 | CBE_ST12 | 1 | Houston | YES | 0.001871 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.050461 | 105 | 105 |  |  |  |  | 0.050461 | 5.2984 | 0.6985 | 0.71424 |  |  |  |  | 318 | 0.015877
48734 | CBE_GT3 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 | 0.69977 | 0.71546 |  |  |  |  | 319 | 0.015836
48735 | CBE_GT4 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 | 0.70103 | 0.71669 |  |  |  |  | 320 | 0.015795
48736 | CBE_ST34 | 1 | Houston | YES | 0.001871 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.050461 | 105 | 105 |  |  |  |  | 0.050461 | 5.2984 | 0.70277 | 0.71837 |  |  |  |  | 321 | 0.015739
5911 | STP_GN1___1 | 1 | Houston | YES | 0.001843 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.050433 | 0 | 0 |  |  |  |  | 0.050433 | 0 | 0.70277 | 0.71837 |  |  |  |  | 322 | 0.015698
5912 | STP_GN2___2 | 2 | Houston | YES | 0.001843 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.050433 | 0 | 0 |  |  |  |  | 0.050433 | 0 | 0.70277 | 0.71837 |  |  |  |  | 323 | 0.015657
3432 | SANDOW_4G | 4 | South | YES | 0.001827 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.050417 | 0 | 580 |  |  |  |  | 0.050417 | 29.242 | 0.71241 | 0.72768 |  |  |  |  | 324 | 0.0156
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.001468 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 606 |  |  |  |  | 0.050058 | 30.3353 | 0.72247 | 0.73734 |  |  |  |  | 325 | 0.0156
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.001468 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 598 |  |  |  |  | 0.050058 | 29.9348 | 0.7324 | 0.74688 |  |  |  |  | 326 | 0.0156
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.001468 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 436 |  |  |  |  | 0.050058 | 21.8254 | 0.73964 | 0.75383 |  |  |  |  | 327 | 0.015278
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.001467 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.050057 | 158 | 158 |  |  |  |  | 0.050057 | 7.909 | 0.74227 | 0.75635 |  |  |  |  | 328 | 0.014873
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.001467 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.050057 | 160 | 160 |  |  |  |  | 0.050057 | 8.0092 | 0.74493 | 0.7589 |  |  |  |  | 329 | 0.014474
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.001467 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.050057 | 175 | 175 |  |  |  |  | 0.050057 | 8.76 | 0.74783 | 0.76169 |  |  |  |  | 330 | 0.014182
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 | 0.74866 | 0.76248 |  |  |  |  | 331 | 0.014077
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 | 0.74949 | 0.76328 |  |  |  |  | 332 | 0.01397
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 | 0.75032 | 0.76407 |  |  |  |  | 333 | 0.013853
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 | 0.75115 | 0.76487 |  |  |  |  | 334 | 0.013818
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.001364 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.049954 | 152.5 | 152.5 |  |  |  |  | 0.049954 | 7.618 | 0.75369 | 0.76729 |  |  |  |  | 335 | 0.013783
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.001364 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.049954 | 149.5 | 149.5 |  |  |  |  | 0.049954 | 7.4682 | 0.75617 | 0.76967 |  |  |  |  | 336 | 0.013748
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.001364 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.049954 | 232.6 | 232.6 |  |  |  |  | 0.049954 | 11.6194 | 0.76003 | 0.77337 |  |  |  |  | 337 | 0.013713
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.001262 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.049852 | 132 | 132 |  |  |  |  | 0.049852 | 6.5805 | 0.76223 | 0.77547 |  |  |  |  | 338 | 0.013606
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.001262 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.049852 | 139 | 139 |  |  |  |  | 0.049852 | 6.9295 | 0.76453 | 0.77767 |  |  |  |  | 339 | 0.013501
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.001262 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.049852 | 329 | 329 |  |  |  |  | 0.049852 | 16.4014 | 0.77 | 0.7829 |  |  |  |  | 340 | 0.013338
8134 | FOR #1 | 1 | South | YES | 0.001172 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 341 | 0.013241
8138 | FOR #2 | 2 | South | YES | 0.001172 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 342 | 0.013139
8153 | FOR #3 | 3 | South | YES | 0.001172 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 343 | 0.012897
8154 | FOR #4 | 4 | South | YES | 0.001172 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 344 | 0.012897
8155 | FOR #5 | 5 | South | YES | 0.001172 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 345 | 0.012897
8156 | FOR #6 | 6 | South | YES | 0.001172 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 346 | 0.012897
8157 | FOR #7 | 7 | South | YES | 0.001172 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 347 | 0.012897
80051 | FOR #8 | 8 | South | YES | 0.001172 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 348 | 0.012897
80052 | FOR #9 | 9 | South | YES | 0.001172 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 349 | 0.012897
80053 | FOR #10 | 10 | South | YES | 0.001172 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | 0.77 | 0.7829 |  |  |  |  | 350 | 0.012897
9002 | DECKR_G3 | 3 | South | YES | 0.001161 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.049751 | 42 | 42 |  |  |  |  | 0.049751 | 2.0896 | 0.7707 | 0.78356 |  |  |  |  | 351 | 0.012897
9003 | DECKR_G4 | 4 | South | YES | 0.001161 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.049751 | 44 | 44 |  |  |  |  | 0.049751 | 2.1891 | 0.77143 | 0.78426 |  |  |  |  | 352 | 0.012897
9004 | DECKR_G5 | 5 | South | YES | 0.001161 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.049751 | 44 | 44 |  |  |  |  | 0.049751 | 2.1891 | 0.77216 | 0.78496 |  |  |  |  | 353 | 0.012897
9005 | DECKR_G6 | 6 | South | YES | 0.001161 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.049751 | 47 | 47 |  |  |  |  | 0.049751 | 2.3383 | 0.77294 | 0.7857 |  |  |  |  | 354 | 0.012865
80226 | ALCOA G | 1 | South | YES | 0.001152 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.049742 | 0 | 0 |  |  |  |  | 0.049742 | 0 | 0.77294 | 0.7857 |  |  |  |  | 355 | 0.012831
9000 | DECKR_G1 | 1 | South | YES | 0.00112 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.04971 | 321 | 321 |  |  |  |  | 0.04971 | 15.957 | 0.77827 | 0.79078 |  |  |  |  | 356 | 0.012798
9001 | DECKR_G2 | 2 | South | YES | 0.00112 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.04971 | 426 | 426 |  |  |  |  | 0.04971 | 21.1766 | 0.78535 | 0.79752 |  |  |  |  | 357 | 0.012762
9016 | SANDH_G1 | 1 | South | YES | 0.001118 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.049708 | 49 | 49 |  |  |  |  | 0.049708 | 2.4357 | 0.78616 | 0.7983 |  |  |  |  | 358 | 0.012762
9017 | SANDH_G2 | 2 | South | YES | 0.001118 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.049708 | 46 | 46 |  |  |  |  | 0.049708 | 2.2866 | 0.78692 | 0.79903 |  |  |  |  | 359 | 0.012512
9018 | SANDH_G3 | 3 | South | YES | 0.001118 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.049708 | 46 | 46 |  |  |  |  | 0.049708 | 2.2866 | 0.78769 | 0.79976 |  |  |  |  | 360 | 0.01218
9019 | SANDH_G4 | 4 | South | YES | 0.001118 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.049708 | 47 | 47 |  |  |  |  | 0.049708 | 2.3363 | 0.78847 | 0.8005 |  |  |  |  | 361 | 0.012141
9020 | SANDHG5A | 5A | South | YES | 0.001118 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.049708 | 155 | 155 |  |  |  |  | 0.049708 | 7.7048 | 0.79104 | 0.80295 |  |  |  |  | 362 | 0.012106
9021 | SANDHG5C | 5C | South | YES | 0.001118 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.049708 | 148 | 148 |  |  |  |  | 0.049708 | 7.3568 | 0.7935 | 0.8053 |  |  |  |  | 363 | 0.01207
8147 | UCAR #2 | 10 | South | YES | 0.001077 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | 0.7935 | 0.8053 |  |  |  |  | 364 | 0.012033
8148 | UCAR #1 | 2 | South | YES | 0.001077 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | 0.7935 | 0.8053 |  |  |  |  | 365 | 0.011912
80137 | CSDR89 | 9 | South | YES | 0.001077 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | 0.7935 | 0.8053 |  |  |  |  | 366 | 0.011797
80137 | CSDR89 | 8 | South | YES | 0.001077 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | 0.7935 | 0.8053 |  |  |  |  | 367 | 0.011797
80138 | CSDR7 | 7 | South | YES | 0.001077 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | 0.7935 | 0.8053 |  |  |  |  | 368 | 0.011797
80139 | CSDR56 | 6 | South | YES | 0.001077 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | 0.7935 | 0.8053 |  |  |  |  | 369 | 0.011797
80139 | CSDR56 | 5 | South | YES | 0.001077 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | 0.7935 | 0.8053 |  |  |  |  | 370 | 0.011797
80140 | CSDR11 | 11 | South | YES | 0.001077 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | 0.7935 | 0.8053 |  |  |  |  | 371 | 0.011797
80227 | AIRCO G | 1 | South | YES | 0.001061 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.049651 | 0 | 0 |  |  |  |  | 0.049651 | 0 | 0.7935 | 0.8053 |  |  |  |  | 372 | 0.011797
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.00106 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.04965 | 0 | 0 |  |  |  |  | 0.04965 | 0 | 0.7935 | 0.8053 |  |  |  |  | 373 | 0.011797
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.00106 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.04965 | 0 | 0 |  |  |  |  | 0.04965 | 0 | 0.7935 | 0.8053 |  |  |  |  | 374 | 0.011797
80224 | VISTRONG1 | 1 | South | YES | 0.001057 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.049647 | 0 | 0 |  |  |  |  | 0.049647 | 0 | 0.7935 | 0.8053 |  |  |  |  | 375 | 0.011797
80225 | VISTRONG2 | 2 | South | YES | 0.001057 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.049647 | 0 | 0 |  |  |  |  | 0.049647 | 0 | 0.7935 | 0.8053 |  |  |  |  | 376 | 0.011797
8066 | DUP1V#1 | 1 | South | YES | 0.001033 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.049623 | 0 | 0 |  |  |  |  | 0.049623 | 0 | 0.7935 | 0.8053 |  |  |  |  | 377 | 0.011797
8173 | VICEC51A | 5 | South | YES | 0.001014 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.049604 | 144 | 144 |  |  |  |  | 0.049604 | 7.143 | 0.79589 | 0.80757 |  |  |  |  | 378 | 0.011797
8174 | VICEC61A | 6 | South | YES | 0.001014 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.049604 | 188 | 188 |  |  |  |  | 0.049604 | 9.3256 | 0.79901 | 0.81054 |  |  |  |  | 379 | 0.011797
5508 | RAYBURNCC9 | 1 | South | YES | 0.001006 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.049596 | 47.7 | 47.7 |  |  |  |  | 0.049596 | 2.3657 | 0.79981 | 0.81129 |  |  |  |  | 380 | 0.011797
5509 | RAYBURNCC10 | 1 | South | YES | 0.001006 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.049596 | 37.3 | 37.3 |  |  |  |  | 0.049596 | 1.8499 | 0.80043 | 0.81188 |  |  |  |  | 381 | 0.01168
5511 | RAYBURNCC7 | 1 | South | YES | 0.001006 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.049596 | 47.5 | 47.5 |  |  |  |  | 0.049596 | 2.3558 | 0.80122 | 0.81263 |  |  |  |  | 382 | 0.011527
5512 | RAYBURNCC8 | 1 | South | YES | 0.001006 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.049596 | 49.3 | 49.3 |  |  |  |  | 0.049596 | 2.4451 | 0.80203 | 0.81341 |  |  |  |  | 383 | 0.011488
5503 | RAYBURNGEN3 | 1 | South | YES | 0.000967 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.049557 | 22 | 22 |  |  |  |  | 0.049557 | 1.0903 | 0.8024 | 0.81376 |  |  |  |  | 384 | 0.011457
5505 | RAYBURNGEN1 | 1 | South | YES | 0.000967 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.049557 | 11 | 11 |  |  |  |  | 0.049557 | 0.54513 | 0.80258 | 0.81393 |  |  |  |  | 385 | 0.011419
5506 | RAYBURNGEN2 | 1 | South | YES | 0.000967 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.049557 | 11 | 11 |  |  |  |  | 0.049557 | 0.54513 | 0.80276 | 0.81411 |  |  |  |  | 386 | 0.011378
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.00096 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.04955 | 223.9 | 223.9 |  |  |  |  | 0.04955 | 11.0943 | 0.80648 | 0.81764 |  |  |  |  | 387 | 0.01136
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.00096 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.04955 | 225 | 225 |  |  |  |  | 0.04955 | 11.1488 | 0.81022 | 0.82119 |  |  |  |  | 388 | 0.011351
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.00096 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.04955 | 224.6 | 224.6 |  |  |  |  | 0.04955 | 11.129 | 0.81395 | 0.82473 |  |  |  |  | 389 | 0.011342
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.00096 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.04955 | 226.7 | 226.7 |  |  |  |  | 0.04955 | 11.233 | 0.81772 | 0.82831 |  |  |  |  | 390 | 0.011156
8189 | CUECPL2A | 1 | South | YES | 0.000953 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.049543 | 0 | 0 |  |  |  |  | 0.049543 | 0 | 0.81772 | 0.82831
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.000944 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.049534 | 0 | 0 |  |  |  |  | 0.049534 | 0 | 0.81772 | 0.82831
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.000944 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.049534 | 0 | 0 |  |  |  |  | 0.049534 | 0 | 0.81772 | 0.82831
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.000914 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.049504 | 148 | 148 |  |  |  |  | 0.049504 | 7.3266 | 0.82017 | 0.83064
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.000914 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.049504 | 148 | 148 |  |  |  |  | 0.049504 | 7.3266 | 0.82263 | 0.83298
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.000914 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.049504 | 154 | 154 |  |  |  |  | 0.049504 | 7.6237 | 0.82519 | 0.8354
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.000914 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.049504 | 293 | 293 |  |  |  |  | 0.049504 | 14.5047 | 0.83006 | 0.84002
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.000882 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 | 0.83006 | 0.84002
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.000882 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 | 0.83006 | 0.84002
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.000882 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 | 0.83006 | 0.84002
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.000868 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.049458 | 147 | 147 |  |  |  |  | 0.049458 | 7.2704 | 0.8325 | 0.84234
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.000868 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.049458 | 138 | 138 |  |  |  |  | 0.049458 | 6.8252 | 0.83479 | 0.84451
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.000868 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.049458 | 146 | 146 |  |  |  |  | 0.049458 | 7.2209 | 0.83721 | 0.84681
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.000868 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.049458 | 149 | 149 |  |  |  |  | 0.049458 | 7.3693 | 0.83969 | 0.84916
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.000868 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.049458 | 182 | 182 |  |  |  |  | 0.049458 | 9.0014 | 0.84271 | 0.85202
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.000868 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.049458 | 203 | 203 |  |  |  |  | 0.049458 | 10.04 | 0.84608 | 0.85522
8161 | COLETO0A | 1 | South | YES | 0.000851 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.049441 | 0 | 633 |  |  |  |  | 0.049441 | 31.2963 | 0.8566 | 0.86519
8926 | LGE_GT10A | 1 | South | YES | 0.000843 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | 0.8566 | 0.86519
8927 | LGE_GT20A | 2 | South | YES | 0.000843 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | 0.8566 | 0.86519
8928 | LGE_STG0A | 3 | South | YES | 0.000843 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | 0.8566 | 0.86519
8930 | ICPGN10A | 1 | South | YES | 0.000843 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | 0.8566 | 0.86519
8931 | ICPGN20A | 2 | South | YES | 0.000843 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | 0.8566 | 0.86519
8932 | ICPGN30A | 3 | South | YES | 0.000843 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | 0.8566 | 0.86519
80223 | REYSHR G | 1 | South | YES | 0.000843 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | 0.8566 | 0.86519
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.000816 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.049406 | 0 | 0 |  |  |  |  | 0.049406 | 0 | 0.8566 | 0.86519
8442 | NBEC7 | 7 | South | YES | 0.000796 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.049386 | 367 | 367 |  |  |  |  | 0.049386 | 18.1247 | 0.86269 | 0.87096
8442 | NBEC7 | MB | South | YES | 0.000796 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 | 0.86269 | 0.87096
8560 | CNOPGT1 | 1 | South | YES | 0.000796 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 | 0.86269 | 0.87096
8561 | CNOPGT2 | 2 | South | YES | 0.000796 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 | 0.86269 | 0.87096
8562 | CNOPST1 | 3 | South | YES | 0.000796 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 | 0.86269 | 0.87096
8456 | COSW#1 | 1 | South | YES | 0.000793 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.049383 | 0 | 0 |  |  |  |  | 0.049383 | 0 | 0.86269 | 0.87096
8457 | COSW#2 | 2 | South | YES | 0.000793 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.049383 | 0 | 0 |  |  |  |  | 0.049383 | 0 | 0.86269 | 0.87096
8459 | B_DAVIS0B | MB | South | YES | 0.00079 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.04938 | 0 | 0 |  |  |  |  | 0.04938 | 0 | 0.86269 | 0.87096
8460 | B_DAVIS0A | MB | South | YES | 0.00079 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.04938 | 0 | 0 |  |  |  |  | 0.04938 | 0 | 0.86269 | 0.87096
80263 | B_DAVIS31A | 3 | South | YES | 0.00079 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.04938 | 180 | 180 |  |  |  |  | 0.04938 | 8.8884 | 0.86568 | 0.87379
80264 | B_DAVIS41A | 4 | South | YES | 0.00079 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.04938 | 180 | 180 |  |  |  |  | 0.04938 | 8.8884 | 0.86867 | 0.87662
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.000788 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.049378 | 0 | 0 |  |  |  |  | 0.049378 | 0 | 0.86867 | 0.87662
8506 | VAL #1 | 1 | South | YES | 0.00078 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 | 0.86867 | 0.87662
8507 | VAL #2 | 2 | South | YES | 0.00078 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 | 0.86867 | 0.87662
8511 | OXY_CC0A | 1 | South | YES | 0.00078 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 | 0.86867 | 0.87662
8461 | KOCH_UP0A | 1 | South | YES | 0.000774 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.049364 | 0 | 0 |  |  |  |  | 0.049364 | 0 | 0.86867 | 0.87662
80080 | GWINDT11A | 3 | South | YES | 0.000757 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 38 |  |  |  |  | 0.049347 | 1.8752 | 0.8693 | 0.87722
80080 | GWINDT11A | 4 | South | YES | 0.000757 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 19 |  |  |  |  | 0.049347 | 0.9376 | 0.86962 | 0.87752
80080 | GWINDT11A | 2 | South | YES | 0.000757 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 41 |  |  |  |  | 0.049347 | 2.0232 | 0.8703 | 0.87816
80080 | GWINDT11A | 1 | South | YES | 0.000757 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 94 |  |  |  |  | 0.049347 | 4.6386 | 0.87186 | 0.87964
80081 | GWINDT21A | 4 | South | YES | 0.000757 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 22 |  |  |  |  | 0.049347 | 1.0856 | 0.87223 | 0.87998
80081 | GWINDT21A | 1 | South | YES | 0.000757 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 94 |  |  |  |  | 0.049347 | 4.6386 | 0.87379 | 0.88146
80081 | GWINDT21A | 3 | South | YES | 0.000757 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 43 |  |  |  |  | 0.049347 | 2.1219 | 0.8745 | 0.88214
80081 | GWINDT21A | 2 | South | YES | 0.000757 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 36 |  |  |  |  | 0.049347 | 1.7765 | 0.8751 | 0.8827
80180 | PNSCALT11A | 2 | South | YES | 0.000757 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 50 |  |  |  |  | 0.049347 | 2.4674 | 0.87593 | 0.88349
80180 | PNSCALT11A | 1 | South | YES | 0.000757 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 148 |  |  |  |  | 0.049347 | 7.3034 | 0.87839 | 0.88581
80181 | PNSCALT21A | 2 | South | YES | 0.000757 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 50 |  |  |  |  | 0.049347 | 2.4674 | 0.87922 | 0.8866
80181 | PNSCALT21A | 1 | South | YES | 0.000757 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 55 |  |  |  |  | 0.049347 | 2.7141 | 0.88013 | 0.88746
8517 | CELANEBI0A | 1 | South | YES | 0.000754 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.049344 | 0 | 0 |  |  |  |  | 0.049344 | 0 | 0.88013 | 0.88746
5932 | SI_RAY9 | 9 | South | YES | 0.000732 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.049322 | 38 | 38 |  |  |  |  | 0.049322 | 1.8742 | 0.88076 | 0.88806
5933 | SI_RAY6 | 6 | South | YES | 0.000732 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.049322 | 19.3 | 19.3 |  |  |  |  | 0.049322 | 0.95192 | 0.88108 | 0.88836
5935 | SI_RAY10 | 10 | South | YES | 0.000732 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.049322 | 47 | 47 |  |  |  |  | 0.049322 | 2.3181 | 0.88186 | 0.8891
80003 | MILHWYS | F | South | YES | 0.000732 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.049322 | 0 | 0 |  |  |  |  | 0.049322 | 0 | 0.88186 | 0.8891
5401 | CALAVER_JKS1 | 1 | South | YES | 0.000705 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.049295 | 0 | 562 |  |  |  |  | 0.049295 | 27.7039 | 0.8912 | 0.89792
8936 | MVGN#1 | 1 | South | YES | 0.000692 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.049282 | 216.6 | 216.6 |  |  |  |  | 0.049282 | 10.6745 | 0.8948 | 0.90132
8937 | MVGN#2 | 2 | South | YES | 0.000692 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.049282 | 216.7 | 216.7 |  |  |  |  | 0.049282 | 10.6795 | 0.8984 | 0.90472
8938 | MVGN#3 | 3 | South | YES | 0.000692 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.049282 | 250.9 | 250.9 |  |  |  |  | 0.049282 | 12.3649 | 0.90256 | 0.90866
8981 | HECN1 | 1 | South | YES | 0.000691 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.049281 | 144.8 | 144.8 |  |  |  |  | 0.049281 | 7.1359 | 0.90497 | 0.91093
8982 | HECN2 | 2 | South | YES | 0.000691 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.049281 | 144.1 | 144.1 |  |  |  |  | 0.049281 | 7.1014 | 0.90736 | 0.91319
8983 | HECN3 | 3 | South | YES | 0.000691 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.049281 | 171.9 | 171.9 |  |  |  |  | 0.049281 | 8.4714 | 0.91022 | 0.91589
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.000676 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.049266 | 155 | 155 |  |  |  |  | 0.049266 | 7.6363 | 0.91279 | 0.91832
5477 | BRA_AVR1_ST | 1 | South | YES | 0.000676 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.049266 | 174 | 174 |  |  |  |  | 0.049266 | 8.5723 | 0.91568 | 0.92105
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.000676 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.049266 | 155 | 155 |  |  |  |  | 0.049266 | 7.6363 | 0.91825 | 0.92348
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.000654 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.049244 | 61 | 61 |  |  |  |  | 0.049244 | 3.0039 | 0.91927 | 0.92444
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.000654 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.049244 | 95 | 95 |  |  |  |  | 0.049244 | 4.6782 | 0.92085 | 0.92593
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.000654 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.049244 | 151 | 151 |  |  |  |  | 0.049244 | 7.4359 | 0.92335 | 0.9283
5903 | SANMIGUELGEN | 1 | South | YES | 0.000649 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.049239 | 0 | 396.3 |  |  |  |  | 0.049239 | 19.5135 | 0.92994 | 0.93451
88198 | BEEVILLE | F | South | YES | 0.000599 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.049189 | 0 | 0 |  |  |  |  | 0.049189 | 0 | 0.92994 | 0.93451
8933 | FGNTS001 | 1 | South | YES | 0.000596 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.049186 | 146.5 | 146.5 |  |  |  |  | 0.049186 | 7.2058 | 0.93237 | 0.93681
8934 | FGNTS101 | 2 | South | YES | 0.000596 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.049186 | 147.9 | 147.9 |  |  |  |  | 0.049186 | 7.2746 | 0.93483 | 0.93912
8935 | FGNTS201 | 3 | South | YES | 0.000596 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.049186 | 173 | 173 |  |  |  |  | 0.049186 | 8.5092 | 0.9377 | 0.94183
5111 | CALAVER_JTD1 | 1 | South | YES | 0.000595 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.049185 | 0 | 430 |  |  |  |  | 0.049185 | 21.1496 | 0.94484 | 0.94857
5112 | CALAVER_JTD2 | 2 | South | YES | 0.000595 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.049185 | 0 | 430 |  |  |  |  | 0.049185 | 21.1496 | 0.95198 | 0.9553
5396 | CALAVER_OWS1 | 1 | South | YES | 0.000579 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.049169 | 418 | 418 |  |  |  |  | 0.049169 | 20.5527 | 0.95892 | 0.96185
5397 | CALAVER_OWS2 | 2 | South | YES | 0.000579 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.049169 | 400 | 400 |  |  |  |  | 0.049169 | 19.6677 | 0.96557 | 0.96811
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.000577 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.049167 | 215 | 215 |  |  |  |  | 0.049167 | 10.571 | 0.96914 | 0.97148
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.000577 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.049167 | 216 | 216 |  |  |  |  | 0.049167 | 10.6201 | 0.97273 | 0.97486
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.00055 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.04914 | 407 | 407 |  |  |  |  | 0.04914 | 20.0001 | 0.97949 | 0.98123
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.000506 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 | 0.97949 | 0.98123
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.000506 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 | 0.97949 | 0.98123
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.000506 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 | 0.97949 | 0.98123
5264 | LEON_LCP3G3 | 3 | South | YES | 0.000461 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.049051 | 58 | 58 |  |  |  |  | 0.049051 | 2.845 | 0.98045 | 0.98213
5265 | LEON_LCP4G4 | 4 | South | YES | 0.000461 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.049051 | 89 | 89 |  |  |  |  | 0.049051 | 4.3656 | 0.98193 | 0.98352
5266 | LEON_LCPCT1 | 1 | South | YES | 0.000461 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.049051 | 44 | 44 |  |  |  |  | 0.049051 | 2.1583 | 0.98266 | 0.98421
5267 | LEON_LCPCT2 | 2 | South | YES | 0.000461 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.049051 | 44 | 44 |  |  |  |  | 0.049051 | 2.1583 | 0.98339 | 0.9849
5268 | LEON_LCPCT3 | 3 | South | YES | 0.000461 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.049051 | 43 | 43 |  |  |  |  | 0.049051 | 2.1092 | 0.9841 | 0.98557
5269 | LEON_LCPCT4 | 4 | South | YES | 0.000461 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.049051 | 45 | 45 |  |  |  |  | 0.049051 | 2.2073 | 0.98485 | 0.98627
88508 | FALFURRI | F | South | YES | 0.000116 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.048706 | 0 | 0 |  |  |  |  | 0.048706 | 0 | 0.98485 | 0.98627
5728 | FALCONHYDRO2 | 2 | South | YES | 2.9e-05 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 | 0.98485 | 0.98627
5729 | FALCONHYDRO3 | 3 | South | YES | 2.9e-05 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 | 0.98485 | 0.98627
8048 | FALCONHYDRO1 | 1 | South | YES | 2.9e-05 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 | 0.98485 | 0.98627
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.04859 | 15 | 15 |  |  |  |  | 0.04859 | 0.72885 | 0.9851 | 0.9865
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | 0.9851 | 0.9865
88299 | ZAPATA | F | South | YES | -0.000513 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.048077 | 0 | 0 |  |  |  |  | 0.048077 | 0 | 0.9851 | 0.9865
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.000655 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047935 | 0 | 0 |  |  |  |  | 0.047935 | 0 | 0.9851 | 0.9865
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.000655 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047935 | 0 | 0 |  |  |  |  | 0.047935 | 0 | 0.9851 | 0.9865
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.001081 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.047509 | 0 | 0 |  |  |  |  | 0.047509 | 0 | 0.9851 | 0.9865
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.001081 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.047509 | 0 | 0 |  |  |  |  | 0.047509 | 0 | 0.9851 | 0.9865
5890 | PEARSALLGEN1 | 1 | South | YES | -0.001202 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.047388 | 24 | 24 |  |  |  |  | 0.047388 | 1.1373 | 0.9855 | 0.98687
5891 | PEARSALLGEN2 | 1 | South | YES | -0.001202 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.047388 | 24.3 | 24.3 |  |  |  |  | 0.047388 | 1.1515 | 0.9859 | 0.98723
5892 | PEARSALLGEN3 | 1 | South | YES | -0.001202 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.047388 | 23.9 | 23.9 |  |  |  |  | 0.047388 | 1.1326 | 0.9863 | 0.98759
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.001217 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.047373 | 423.3 | 423.3 |  |  |  |  | 0.047373 | 20.0531 | 0.99333 | 0.99398
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.001264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 | 0.99333 | 0.99398
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.001264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 | 0.99333 | 0.99398
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.001264 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 | 0.99333 | 0.99398
80012 | LAR | F | South | YES | -0.001312 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.047278 | 0 | 0 |  |  |  |  | 0.047278 | 0 | 0.99333 | 0.99398
80265 | LARECU40A | 4 | South | YES | -0.001313 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.047277 | 100 | 100 |  |  |  |  | 0.047277 | 4.7277 | 0.99499 | 0.99549
80266 | LARECU50A | 5 | South | YES | -0.001313 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.047277 | 100 | 100 |  |  |  |  | 0.047277 | 4.7277 | 0.99665 | 0.99699
58909 | PEARSALLSCG1 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99679 | 0.99712
58909 | PEARSALLSCG1 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99693 | 0.99724
58909 | PEARSALLSCG1 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99707 | 0.99737
58909 | PEARSALLSCG1 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99721 | 0.99749
58909 | PEARSALLSCG1 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99735 | 0.99762
58909 | PEARSALLSCG1 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99749 | 0.99774
58919 | PEARSALLSCG2 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99763 | 0.99787
58919 | PEARSALLSCG2 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99777 | 0.99799
58919 | PEARSALLSCG2 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99791 | 0.99812
58919 | PEARSALLSCG2 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99805 | 0.99824
58919 | PEARSALLSCG2 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99819 | 0.99837
58919 | PEARSALLSCG2 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99833 | 0.9985
58929 | PEARSALLSCG3 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99847 | 0.99862
58929 | PEARSALLSCG3 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.9986 | 0.99875
58929 | PEARSALLSCG3 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99874 | 0.99887
58929 | PEARSALLSCG3 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99888 | 0.999
58929 | PEARSALLSCG3 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99902 | 0.99912
58929 | PEARSALLSCG3 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99916 | 0.99925
58949 | PEARSALLSCG4 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.9993 | 0.99937
58949 | PEARSALLSCG4 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99944 | 0.9995
58949 | PEARSALLSCG4 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99958 | 0.99962
58949 | PEARSALLSCG4 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99972 | 0.99975
58949 | PEARSALLSCG4 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 0.99986 | 0.99987
58949 | PEARSALLSCG4 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | 1 | 1
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.002087 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.046503 | 0 | 0 |  |  |  |  | 0.046503 | 0 | 1 | 1
8262 | ELPS | 1 | South | YES | -0.009524 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.039066 | 0 | 0 |  |  |  |  | 0.039066 | 0 | 1 | 1
8032 | AMISTADHYD1 | 1 | South | YES | -0.013289 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 | 1 | 1
8033 | AMISTADHYD2 | 2 | South | YES | -0.013289 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 | 1 | 1
88253 | HAMILTON | F | South | YES | -0.013289 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 | 1 | 1
6100 | OKLA7A | EQ | West | YES | -0.02434 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.029973 | 0 | 0 |  |  | 0 | 0 | -0.029973 | 0
6752 | OKLA0A | 1 | West | YES | -0.02434 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.029973 | 0 | 649.7 |  |  | 0 | 0 | -0.029973 | 0
11056 | ROSCOE_1G | 1 | West | YES | -0.038521 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.044154 | 0 | 209 |  |  | 0 | 0 | -0.044154 | 0
11057 | CHAMPION_1G | 1 | West | YES | -0.038521 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.044154 | 0 | 126.5 |  |  | 0 | 0 | -0.044154 | 0
11058 | PYRON_1G | 1 | West | YES | -0.038521 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.044154 | 0 | 249 |  |  | 0 | 0 | -0.044154 | 0
11059 | INADALE_1G | 1 | West | YES | -0.038521 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.044154 | 0 | 197 |  |  | 0 | 0 | -0.044154 | 0
60202 | FRNDDRCS | F | West | YES | -0.038909 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.044542 | 0 | 0 |  |  | 0 | 0 | -0.044542 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.042803 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.048436 | 0 | 112.5 |  |  | 0 | 0 | -0.048436 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.042803 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 149.5 |  |  | 0 | 0 | -0.048436 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.042803 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 186 |  |  | 0 | 0 | -0.048436 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.042803 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 214.5 |  |  | 0 | 0 | -0.048436 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | -0.043314 | 30 | 0 | 150 |  | 1.02 | Wind | -1 | 0.048947 | 0 | 150 |  |  | 0 | 0 | -0.048947 | 0
60000 | DSKY2 | 1 | West | YES | -0.043529 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.049162 | 0 | 76.5 |  |  | 0 | 0 | -0.049162 | 0
60018 | DSKY1 | 1 | West | YES | -0.043565 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.049198 | 0 | 84 |  |  | 0 | 0 | -0.049198 | 0
60017 | ORNNWP1 | 1 | West | YES | -0.043874 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.049507 | 0 | 80 |  |  | 0 | 0 | -0.049507 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | -0.044788 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.050421 | 0 | 150 |  |  | 0 | 0 | -0.050421 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.044816 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.050449 | 0 | 80 |  |  | 0 | 0 | -0.050449 | 0
60016 | WOODWRD11A | 1 | West | YES | -0.044823 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.050456 | 0 | 80 |  |  | 0 | 0 | -0.050456 | 0
6016 | SWMESA | 1 | West | YES | -0.04485 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.050483 | 0 | 75 |  |  | 0 | 0 | -0.050483 | 0
60003 | KING_NE1A | 1 | West | YES | -0.04485 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050483 | 0 | 80 |  |  | 0 | 0 | -0.050483 | 0
60005 | KING_SE1A | 1 | West | YES | -0.04485 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.050483 | 0 | 40 |  |  | 0 | 0 | -0.050483 | 0
60201 | RIO DRCS | F | West | YES | -0.044909 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.050542 | 0 | 0 |  |  | 0 | 0 | -0.050542 | 0
60007 | KING_SW1A | 1 | West | YES | -0.045015 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050648 | 0 | 80 |  |  | 0 | 0 | -0.050648 | 0
60019 | KING_NW1A | 1 | West | YES | -0.045015 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050648 | 0 | 80 |  |  | 0 | 0 | -0.050648 | 0
60058 | BUFF_GAP1A | 1 | West | YES | -0.045356 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.050989 | 0 | 120 |  |  | 0 | 0 | -0.050989 | 0
60060 | CIRELLO | 1 | West | YES | -0.045356 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.050989 | 0 | 233 |  |  | 0 | 0 | -0.050989 | 0
60063 | BUFF_GAP1B | 1 | West | YES | -0.045356 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.050989 | 0 | 170.2 |  |  | 0 | 0 | -0.050989 | 0
60066 | H_HOLLOW1A | 1 | West | YES | -0.045356 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.050989 | 0 | 222 |  |  | 0 | 0 | -0.050989 | 0
60068 | HHOLLOW21A | 1 | West | YES | -0.045356 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 184 |  |  | 0 | 0 | -0.050989 | 0
60070 | HHOLLOW31A | 1 | West | YES | -0.045356 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 224 |  |  | 0 | 0 | -0.050989 | 0
60072 | HHOLLOW41A | 1 | West | YES | -0.045356 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 115 |  |  | 0 | 0 | -0.050989 | 0
1416 | SWETWATR_1G | 1 | West | YES | -0.045937 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.05157 | 30 | 30 |  |  | -1.3781 | 30 | -0.05157 | -1.5471
1417 | SWETWATR_2G | 2 | West | YES | -0.045937 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.05157 | 72 | 72 |  |  | -3.3075 | 72 | -0.05157 | -3.713
1418 | SWETWATR_3G | 3 | West | YES | -0.045937 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.05157 | 68 | 68 |  |  | -3.1237 | 68 | -0.05157 | -3.5067
1419 | SWETWATR_4G | 4 | West | YES | -0.045937 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.05157 | 61 | 61 |  |  | -2.8022 | 61 | -0.05157 | -3.1457
1058 | LONGSHORE_5 | 1 | West | YES | -0.046157 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.05179 | 0 | 150 |  |  | 0 | 0 | -0.05179 | 0
1058 | LONGSHORE_5 | 2 | West | YES | -0.046157 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.05179 | 0 | 220 |  |  | 0 | 0 | -0.05179 | 0
11065 | ELBOWCK_1G | 1 | West | YES | -0.046157 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.05179 | 0 | 121.9 |  |  | 0 | 0 | -0.05179 | 0
1045 | CALENG1G_1G | 1 | West | YES | -0.046446 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0
1046 | CALENG2G_2G | 2 | West | YES | -0.046446 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0
1047 | CALENG3G_3G | 3 | West | YES | -0.046446 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0
11001 | NAV1CT | 1 | West | YES | -0.046978 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.052611 | 70.4 | 70.4 |  |  | -3.3073 | 70.4 | -0.052611 | -3.7038
11009 | NAV2CT | 1 | West | YES | -0.046978 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.052611 | 71.4 | 71.4 |  |  | -3.3542 | 71.4 | -0.052611 | -3.7564
11011 | NAV3ST | 1 | West | YES | -0.046978 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.052611 | 92.8 | 92.8 |  |  | -4.3596 | 92.8 | -0.052611 | -4.8823
11012 | NAV4CT | 1 | West | YES | -0.046978 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.052611 | 80 | 80 |  |  | -3.7582 | 80 | -0.052611 | -4.2088
11013 | NAV5CT | 1 | West | YES | -0.046978 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.052611 | 80 | 80 |  |  | -3.7582 | 80 | -0.052611 | -4.2088
11014 | NAV6ST | 1 | West | YES | -0.046978 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.052611 | 115 | 115 |  |  | -5.4025 | 115 | -0.052611 | -6.0502
11020 | TIEHVSG_1G | 1 | West | YES | -0.046987 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.05262 | 208.2 | 208.2 |  |  | -9.7827 | 208.2 | -0.05262 | -10.9554
11021 | TIEHVCG_1G | 1 | West | YES | -0.046987 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.05262 | 142.1 | 142.1 |  |  | -6.6769 | 142.1 | -0.05262 | -7.4772
11022 | TIEHVCG_2G | 1 | West | YES | -0.046987 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.05262 | 132.4 | 132.4 |  |  | -6.2211 | 132.4 | -0.05262 | -6.9668
11023 | TIEHVCG_3G | 1 | West | YES | -0.046987 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.05262 | 137.4 | 137.4 |  |  | -6.456 | 137.4 | -0.05262 | -7.2299
11024 | TIEHVCG_4G | 1 | West | YES | -0.046987 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.05262 | 147 | 147 |  |  | -6.9071 | 147 | -0.05262 | -7.7351
11025 | TIEHVSG_2G | 1 | West | YES | -0.046987 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.05262 | 213.2 | 213.2 |  |  | -10.0176 | 213.2 | -0.05262 | -11.2185
71051 | L_BITTCR1_1N | W1 | West | YES | -0.047437 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 37.5 |  |  | 0 | 0 | -0.05307 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | -0.047437 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 107.5 |  |  | 0 | 0 | -0.05307 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | -0.047437 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 135 |  |  | 0 | 0 | -0.05307 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | -0.047437 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 119 |  |  | 0 | 0 | -0.05307 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | -0.047437 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 105 |  |  | 0 | 0 | -0.05307 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | -0.047437 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 80.5 |  |  | 0 | 0 | -0.05307 | 0
1002 | PBCTAGE_1G | A | West | YES | -0.047875 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.053508 | 66 | 66 |  |  | -3.1597 | 66 | -0.053508 | -3.5315
1003 | PBCTBGE_2G | B | West | YES | -0.047875 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.053508 | 66 | 66 |  |  | -3.1597 | 66 | -0.053508 | -3.5315
1004 | PBCTCGE_3G | C | West | YES | -0.047875 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.053508 | 67 | 67 |  |  | -3.2076 | 67 | -0.053508 | -3.585
1005 | PBCTDGE_4G | D | West | YES | -0.047875 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.053508 | 68 | 68 |  |  | -3.2555 | 68 | -0.053508 | -3.6385
1006 | PBCTEGE_5G | E | West | YES | -0.047875 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.053508 | 67 | 67 |  |  | -3.2076 | 67 | -0.053508 | -3.585
1007 | PB5GEN_6G | 5 | West | YES | -0.047875 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.053508 | 114 | 114 |  |  | -5.4577 | 114 | -0.053508 | -6.0999
1008 | PB6GEN_7G | 6 | West | YES | -0.047875 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.053508 | 515 | 515 |  |  | -24.6556 | 515 | -0.053508 | -27.5564
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.048204 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.053837 | 0 | 35 |  |  | 0 | 0 | -0.053837 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.048204 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.053837 | 0 | 30 |  |  | 0 | 0 | -0.053837 | 0
11147 | NOTREES_1G | 1 | West | YES | -0.048921 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.054554 | 0 | 149 |  |  | 0 | 0 | -0.054554 | 0
1326 | STANTONW_8 | 1 | West | YES | -0.051389 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.057022 | 0 | 100.5 |  |  | 0 | 0 | -0.057022 | 0
1328 | OCOTILLO_1G | 1 | West | YES | -0.053498 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.059131 | 0 | 58 |  |  | 0 | 0 | -0.059131 | 0
1349 | WESTXWIN_1G | 1 | West | YES | -0.053676 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.059309 | 0 | 6.6 |  |  | 0 | 0 | -0.059309 | 0
1350 | NWPWRG1_1G | 1 | West | YES | -0.053676 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.059309 | 0 | 34.3 |  |  | 0 | 0 | -0.059309 | 0
1333 | MCDDONAL_8 | 1 | West | YES | -0.054171 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.059804 | 0 | 214.2 |  |  | 0 | 0 | -0.059804 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.055296 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.060929 | 137 | 137 |  |  | -7.5756 | 137 | -0.060929 | -8.3472
1039 | MRGNAG_1G | A | West | YES | -0.055296 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.060929 | 69 | 69 |  |  | -3.8154 | 69 | -0.060929 | -4.2041
1040 | MRGNBG_2G | B | West | YES | -0.055296 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.060929 | 71 | 71 |  |  | -3.926 | 71 | -0.060929 | -4.3259
1041 | MRGNCG_3G | C | West | YES | -0.055296 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.060929 | 70 | 70 |  |  | -3.8707 | 70 | -0.060929 | -4.265
1042 | MRGNDG_4G | D | West | YES | -0.055296 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.060929 | 68 | 68 |  |  | -3.7601 | 68 | -0.060929 | -4.1431
1043 | MRGNEG_5G | E | West | YES | -0.055296 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.060929 | 70 | 70 |  |  | -3.8707 | 70 | -0.060929 | -4.265
1044 | MRGNFG_6G | F | West | YES | -0.055296 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.060929 | 66 | 66 |  |  | -3.6495 | 66 | -0.060929 | -4.0213
1320 | BSP 1 | 1 | West | YES | -0.055685 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.061318 | 0 | 0 |  |  | 0 | 0 | -0.061318 | 0
1327 | WILDHRSE_1G | 1 | West | YES | -0.05766 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.063293 | 0 | 120 |  |  | 0 | 0 | -0.063293 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.059128 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.064761 | 0 | 120 |  |  | 0 | 0 | -0.064761 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.063919 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.069552 | 0 | 225 |  |  | 0 | 0 | -0.069552 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.064627 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.07026 | 0 | 180 |  |  | 0 | 0 | -0.07026 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.064627 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.07026 | 0 | 180 |  |  | 0 | 0 | -0.07026 | 0
6637 | SNYDERW1A | 1 | West | YES | -0.068953 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.074586 | 0 | 63 |  |  | 0 | 0 | -0.074586 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.072453 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.078086 | 0 | 141 |  |  | 0 | 0 | -0.078086 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.072453 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.078086 | 0 | 120 |  |  | 0 | 0 | -0.078086 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.072731 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.078364 | 0 | 99 |  |  | 0 | 0 | -0.078364 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.072731 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.078364 | 0 | 61 |  |  | 0 | 0 | -0.078364 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.072731 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.072731 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.072731 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.079616 | 22.8 | 0 | 114 |  | 1.04 | Wind | -1 | 0.085249 | 0 | 114 |  |  | 0 | 0 | -0.085249 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.081016 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.086649 | 0 | 150 |  |  | 0 | 0 | -0.086649 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.081016 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.086649 | 0 | 101 |  |  | 0 | 0 | -0.086649 | 0
36998 | RDCNYNG1 | 1 | West | YES | -0.082833 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.088466 | 0 | 84 |  |  | 0 | 0 | -0.088466 | 0
6407 | TURKTRAK1A | 1 | West | YES | -0.091498 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.097131 | 0 | 169.5 |  |  | 0 | 0 | -0.097131 | 0
6144 | MCADOO1A | 1 | West | YES | -0.12715 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.13278 | 0 | 150 |  |  | 0 | 0 | -0.13278 | 0
60081 | WHRLWIND1A | 1 | West | YES | -0.14207 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.1477 | 0 | 60 |  |  | 0 | 0 | -0.1477 | 0
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ LongCreek to Sweetwater and LongCreek to AbileneMulberry OL_ Murry to Graham |  | i_PTDF_INC_pt | 102 |  | MRGNFG_6G | Unit at max
60081 | WHRLWIND1A | 1 | West | YES | -0.14207 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.1477 | 0 | 60 |  |  | 0 | 0 | -0.1477 | 0 | 0 | 0 |  |  | i_10pctunit | 25 |  | 28 | # units @ max
6144 | MCADOO1A | 1 | West | YES | -0.12715 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.13278 | 0 | 150 |  |  | 0 | 0 | -0.13278 | 0 | 0 | 0 | [5 empty] | 0.021065 | delta max
6407 | TURKTRAK1A | 1 | West | YES | -0.091498 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.097131 | 0 | 169.5 |  |  | 0 | 0 | -0.097131 | 0 | 0 | 0 | [5 empty] | Delta
36998 | RDCNYNG1 | 1 | West | YES | -0.082833 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.088466 | 0 | 84 |  |  | 0 | 0 | -0.088466 | 0 | 0 | 0 | Weighted Shift Factors |  |  |  | 1 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.081016 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.086649 | 0 | 150 |  |  | 0 | 0 | -0.086649 | 0 | 0 | 0 | North | 0.0056325 |  |  | 2 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.081016 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.086649 | 0 | 101 |  |  | 0 | 0 | -0.086649 | 0 | 0 | 0 | West | -0.04859 |  |  | 3 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.079616 | 22.8 | 0 | 114 |  | 1.04 | Wind | -1 | 0.085249 | 0 | 114 |  |  | 0 | 0 | -0.085249 | 0 | 0 | 0 |  |  |  |  | 4 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.072731 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.078364 | 0 | 99 |  |  | 0 | 0 | -0.078364 | 0 | 0 | 0 |  |  |  |  | 5 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.072731 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.078364 | 0 | 61 |  |  | 0 | 0 | -0.078364 | 0 | 0 | 0 |  |  |  |  | 6 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.072731 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0 | 0 | 0 |  |  |  |  | 7 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.072731 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0 | 0 | 0 |  |  |  |  | 8 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.072731 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0 | 0 | 0 |  |  |  |  | 9 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.072453 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.078086 | 0 | 141 |  |  | 0 | 0 | -0.078086 | 0 | 0 | 0 |  |  |  |  | 10 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.072453 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.078086 | 0 | 120 |  |  | 0 | 0 | -0.078086 | 0 | 0 | 0 |  |  |  |  | 11 | 0
6637 | SNYDERW1A | 1 | West | YES | -0.068953 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.074586 | 0 | 63 |  |  | 0 | 0 | -0.074586 | 0 | 0 | 0 |  |  |  |  | 12 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.064627 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.07026 | 0 | 180 |  |  | 0 | 0 | -0.07026 | 0 | 0 | 0 |  |  |  |  | 13 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.064627 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.07026 | 0 | 180 |  |  | 0 | 0 | -0.07026 | 0 | 0 | 0 |  |  |  |  | 14 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.063919 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.069552 | 0 | 225 |  |  | 0 | 0 | -0.069552 | 0 | 0 | 0 |  |  |  |  | 15 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.059128 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.064761 | 0 | 120 |  |  | 0 | 0 | -0.064761 | 0 | 0 | 0 |  |  |  |  | 16 | 0
1327 | WILDHRSE_1G | 1 | West | YES | -0.05766 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.063293 | 0 | 120 |  |  | 0 | 0 | -0.063293 | 0 | 0 | 0 |  |  |  |  | 17 | 0
1320 | BSP 1 | 1 | West | YES | -0.055685 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.061318 | 0 | 0 |  |  | 0 | 0 | -0.061318 | 0 | 0 | 0 |  |  |  |  | 18 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.055296 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.060929 | 137 | 137 |  |  | -7.5756 | 137 | -0.060929 | -8.3472 | 0.042351 | 0.047588 |  |  |  |  | 19 | 0
1039 | MRGNAG_1G | A | West | YES | -0.055296 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.060929 | 69 | 69 |  |  | -3.8154 | 69 | -0.060929 | -4.2041 | 0.06368 | 0.071556 |  |  |  |  | 20 | 0
1040 | MRGNBG_2G | B | West | YES | -0.055296 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.060929 | 71 | 71 |  |  | -3.926 | 71 | -0.060929 | -4.3259 | 0.085629 | 0.096218 |  |  |  |  | 21 | 0
1041 | MRGNCG_3G | C | West | YES | -0.055296 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.060929 | 70 | 70 |  |  | -3.8707 | 70 | -0.060929 | -4.265 | 0.10727 | 0.12053 |  |  |  |  | 22 | 0.0052375
1042 | MRGNDG_4G | D | West | YES | -0.055296 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.060929 | 68 | 68 |  |  | -3.7601 | 68 | -0.060929 | -4.1431 | 0.12829 | 0.14415 |  |  |  |  | 23 | 0.0078754
1043 | MRGNEG_5G | E | West | YES | -0.055296 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.060929 | 70 | 70 |  |  | -3.8707 | 70 | -0.060929 | -4.265 | 0.14993 | 0.16847 |  |  |  |  | 24 | 0.01059
1044 | MRGNFG_6G | F | West | YES | -0.055296 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.060929 | 66 | 66 |  |  | -3.6495 | 66 | -0.060929 | -4.0213 | 0.17033 | 0.19139 |  |  |  |  | 25 | 0.013266
1333 | MCDDONAL_8 | 1 | West | YES | -0.054171 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.059804 | 0 | 214.2 |  |  | 0 | 0 | -0.059804 | 0 | 0.17033 | 0.19139 |  |  |  |  | 26 | 0.015866
1349 | WESTXWIN_1G | 1 | West | YES | -0.053676 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.059309 | 0 | 6.6 |  |  | 0 | 0 | -0.059309 | 0 | 0.17033 | 0.19139 |  |  |  |  | 27 | 0.018542
1350 | NWPWRG1_1G | 1 | West | YES | -0.053676 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.059309 | 0 | 34.3 |  |  | 0 | 0 | -0.059309 | 0 | 0.17033 | 0.19139 |  |  |  |  | 28 | 0.021065
1328 | OCOTILLO_1G | 1 | West | YES | -0.053498 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.059131 | 0 | 58 |  |  | 0 | 0 | -0.059131 | 0 | 0.17033 | 0.19139 |  |  |  |  | 29 | 0.021065
1326 | STANTONW_8 | 1 | West | YES | -0.051389 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.057022 | 0 | 100.5 |  |  | 0 | 0 | -0.057022 | 0 | 0.17033 | 0.19139 |  |  |  |  | 30 | 0.021065
11147 | NOTREES_1G | 1 | West | YES | -0.048921 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.054554 | 0 | 149 |  |  | 0 | 0 | -0.054554 | 0 | 0.17033 | 0.19139 |  |  |  |  | 31 | 0.021065
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.048204 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.053837 | 0 | 35 |  |  | 0 | 0 | -0.053837 | 0 | 0.17033 | 0.19139 |  |  |  |  | 32 | 0.021065
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.048204 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.053837 | 0 | 30 |  |  | 0 | 0 | -0.053837 | 0 | 0.17033 | 0.19139 |  |  |  |  | 33 | 0.021065
1002 | PBCTAGE_1G | A | West | YES | -0.047875 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.053508 | 66 | 66 |  |  | -3.1597 | 66 | -0.053508 | -3.5315 | 0.19073 | 0.21153 |  |  |  |  | 34 | 0.021065
1003 | PBCTBGE_2G | B | West | YES | -0.047875 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.053508 | 66 | 66 |  |  | -3.1597 | 66 | -0.053508 | -3.5315 | 0.21113 | 0.23166 |  |  |  |  | 35 | 0.021065
1004 | PBCTCGE_3G | C | West | YES | -0.047875 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.053508 | 67 | 67 |  |  | -3.2076 | 67 | -0.053508 | -3.585 | 0.23185 | 0.2521 |  |  |  |  | 36 | 0.021065
1005 | PBCTDGE_4G | D | West | YES | -0.047875 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.053508 | 68 | 68 |  |  | -3.2555 | 68 | -0.053508 | -3.6385 | 0.25287 | 0.27284 |  |  |  |  | 37 | 0.020796
1006 | PBCTEGE_5G | E | West | YES | -0.047875 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.053508 | 67 | 67 |  |  | -3.2076 | 67 | -0.053508 | -3.585 | 0.27358 | 0.29328 |  |  |  |  | 38 | 0.020527
1007 | PB5GEN_6G | 5 | West | YES | -0.047875 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.053508 | 114 | 114 |  |  | -5.4577 | 114 | -0.053508 | -6.0999 | 0.30882 | 0.32806 |  |  |  |  | 39 | 0.020253
1008 | PB6GEN_7G | 6 | West | YES | -0.047875 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.053508 | 515 | 515 |  |  | -24.6556 | 515 | -0.053508 | -27.5564 | 0.46802 | 0.48516 |  |  |  |  | 40 | 0.019976
71051 | L_BITTCR1_1N | W1 | West | YES | -0.047437 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 37.5 |  |  | 0 | 0 | -0.05307 | 0 | 0.46802 | 0.48516 |  |  |  |  | 41 | 0.019703
71054 | L_SWEETW1_1N | W1 | West | YES | -0.047437 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 107.5 |  |  | 0 | 0 | -0.05307 | 0 | 0.46802 | 0.48516 |  |  |  |  | 42 | 0.019238
71057 | L_SWEETW1_2N | W1 | West | YES | -0.047437 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 135 |  |  | 0 | 0 | -0.05307 | 0 | 0.46802 | 0.48516 |  |  |  |  | 43 | 0.017138
71059 | L_SWEETW1_3N | W1 | West | YES | -0.047437 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 119 |  |  | 0 | 0 | -0.05307 | 0 | 0.46802 | 0.48516 |  |  |  |  | 44 | 0.017138
71060 | L_SWEETW1_4N | W1 | West | YES | -0.047437 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 105 |  |  | 0 | 0 | -0.05307 | 0 | 0.46802 | 0.48516 |  |  |  |  | 45 | 0.017138
71061 | L_SWEETW1_5N | W1 | West | YES | -0.047437 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 80.5 |  |  | 0 | 0 | -0.05307 | 0 | 0.46802 | 0.48516 |  |  |  |  | 46 | 0.017138
11020 | TIEHVSG_1G | 1 | West | YES | -0.046987 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.05262 | 208.2 | 208.2 |  |  | -9.7827 | 208.2 | -0.05262 | -10.9554 | 0.53238 | 0.54762 |  |  |  |  | 47 | 0.017138
11021 | TIEHVCG_1G | 1 | West | YES | -0.046987 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.05262 | 142.1 | 142.1 |  |  | -6.6769 | 142.1 | -0.05262 | -7.4772 | 0.57631 | 0.59024 |  |  |  |  | 48 | 0.017138
11022 | TIEHVCG_2G | 1 | West | YES | -0.046987 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.05262 | 132.4 | 132.4 |  |  | -6.2211 | 132.4 | -0.05262 | -6.9668 | 0.61724 | 0.62996 |  |  |  |  | 49 | 0.017138
11023 | TIEHVCG_3G | 1 | West | YES | -0.046987 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.05262 | 137.4 | 137.4 |  |  | -6.456 | 137.4 | -0.05262 | -7.2299 | 0.65971 | 0.67118 |  |  |  |  | 50 | 0.015235
11024 | TIEHVCG_4G | 1 | West | YES | -0.046987 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.05262 | 147 | 147 |  |  | -6.9071 | 147 | -0.05262 | -7.7351 | 0.70515 | 0.71528 |  |  |  |  | 51 | 0.013936
11025 | TIEHVSG_2G | 1 | West | YES | -0.046987 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.05262 | 213.2 | 213.2 |  |  | -10.0176 | 213.2 | -0.05262 | -11.2185 | 0.77106 | 0.77924 |  |  |  |  | 52 | 0.012726
11001 | NAV1CT | 1 | West | YES | -0.046978 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.052611 | 70.4 | 70.4 |  |  | -3.3073 | 70.4 | -0.052611 | -3.7038 | 0.79282 | 0.80035 |  |  |  |  | 53 | 0.01147
11009 | NAV2CT | 1 | West | YES | -0.046978 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.052611 | 71.4 | 71.4 |  |  | -3.3542 | 71.4 | -0.052611 | -3.7564 | 0.81489 | 0.82177 |  |  |  |  | 54 | 0.010127
11011 | NAV3ST | 1 | West | YES | -0.046978 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.052611 | 92.8 | 92.8 |  |  | -4.3596 | 92.8 | -0.052611 | -4.8823 | 0.84358 | 0.8496 |  |  |  |  | 55 | 0.0081781
11012 | NAV4CT | 1 | West | YES | -0.046978 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.052611 | 80 | 80 |  |  | -3.7582 | 80 | -0.052611 | -4.2088 | 0.86831 | 0.8736 |  |  |  |  | 56 | 0.007531
11013 | NAV5CT | 1 | West | YES | -0.046978 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.052611 | 80 | 80 |  |  | -3.7582 | 80 | -0.052611 | -4.2088 | 0.89304 | 0.89759 |  |  |  |  | 57 | 0.0068748
11014 | NAV6ST | 1 | West | YES | -0.046978 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.052611 | 115 | 115 |  |  | -5.4025 | 115 | -0.052611 | -6.0502 | 0.92859 | 0.93209 |  |  |  |  | 58 | 0.0060218
1045 | CALENG1G_1G | 1 | West | YES | -0.046446 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0 | 0.92859 | 0.93209 |  |  |  |  | 59 | 0.0052865
1046 | CALENG2G_2G | 2 | West | YES | -0.046446 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0 | 0.92859 | 0.93209 |  |  |  |  | 60 | 0.0045512
1047 | CALENG3G_3G | 3 | West | YES | -0.046446 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0 | 0.92859 | 0.93209 |  |  |  |  | 61 | 0.0034942
1058 | LONGSHORE_5 | 1 | West | YES | -0.046157 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.05179 | 0 | 150 |  |  | 0 | 0 | -0.05179 | 0 | 0.92859 | 0.93209 |  |  |  |  | 62 | 0.0034942
1058 | LONGSHORE_5 | 2 | West | YES | -0.046157 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.05179 | 0 | 220 |  |  | 0 | 0 | -0.05179 | 0 | 0.92859 | 0.93209 |  |  |  |  | 63 | 0.0034942
11065 | ELBOWCK_1G | 1 | West | YES | -0.046157 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.05179 | 0 | 121.9 |  |  | 0 | 0 | -0.05179 | 0 | 0.92859 | 0.93209 |  |  |  |  | 64 | 0.0034942
1416 | SWETWATR_1G | 1 | West | YES | -0.045937 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.05157 | 30 | 30 |  |  | -1.3781 | 30 | -0.05157 | -1.5471 | 0.93787 | 0.94091 |  |  |  |  | 65 | 0.0034942
1417 | SWETWATR_2G | 2 | West | YES | -0.045937 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.05157 | 72 | 72 |  |  | -3.3075 | 72 | -0.05157 | -3.713 | 0.96012 | 0.96207 |  |  |  |  | 66 | 0.0034942
1418 | SWETWATR_3G | 3 | West | YES | -0.045937 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.05157 | 68 | 68 |  |  | -3.1237 | 68 | -0.05157 | -3.5067 | 0.98114 | 0.98207 |  |  |  |  | 67 | 0.0034942
1419 | SWETWATR_4G | 4 | West | YES | -0.045937 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.05157 | 61 | 61 |  |  | -2.8022 | 61 | -0.05157 | -3.1457 | 1 | 1 |  |  |  |  | 68 | 0.0030404
60058 | BUFF_GAP1A | 1 | West | YES | -0.045356 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.050989 | 0 | 120 |  |  | 0 | 0 | -0.050989 | 0 | 1 | 1 |  |  |  |  | 69 | 0.0019513
60060 | CIRELLO | 1 | West | YES | -0.045356 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.050989 | 0 | 233 |  |  | 0 | 0 | -0.050989 | 0 | 1 | 1 |  |  |  |  | 70 | 0.0009227
60063 | BUFF_GAP1B | 1 | West | YES | -0.045356 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.050989 | 0 | 170.2 |  |  | 0 | 0 | -0.050989 | 0 | 1 | 1 |  |  |  |  | 71 | 0
60066 | H_HOLLOW1A | 1 | West | YES | -0.045356 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.050989 | 0 | 222 |  |  | 0 | 0 | -0.050989 | 0 | 1 | 1 |  |  |  |  | 72 | 0
60068 | HHOLLOW21A | 1 | West | YES | -0.045356 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 184 |  |  | 0 | 0 | -0.050989 | 0 | 1 | 1 |  |  |  |  | 73 | 0
60070 | HHOLLOW31A | 1 | West | YES | -0.045356 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 224 |  |  | 0 | 0 | -0.050989 | 0 | 1 | 1 |  |  |  |  | 74 | 0
60072 | HHOLLOW41A | 1 | West | YES | -0.045356 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 115 |  |  | 0 | 0 | -0.050989 | 0 | 1 | 1 |  |  |  |  | 75 | 0
60007 | KING_SW1A | 1 | West | YES | -0.045015 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050648 | 0 | 80 |  |  | 0 | 0 | -0.050648 | 0 | 1 | 1 |  |  |  |  | 76 | 0
60019 | KING_NW1A | 1 | West | YES | -0.045015 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050648 | 0 | 80 |  |  | 0 | 0 | -0.050648 | 0 | 1 | 1 |  |  |  |  | 77 | 0
60201 | RIO DRCS | F | West | YES | -0.044909 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.050542 | 0 | 0 |  |  | 0 | 0 | -0.050542 | 0 | 1 | 1 |  |  |  |  | 78 | 0
6016 | SWMESA | 1 | West | YES | -0.04485 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.050483 | 0 | 75 |  |  | 0 | 0 | -0.050483 | 0 | 1 | 1 |  |  |  |  | 79 | 0
60003 | KING_NE1A | 1 | West | YES | -0.04485 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050483 | 0 | 80 |  |  | 0 | 0 | -0.050483 | 0 | 1 | 1 |  |  |  |  | 80 | 0
60005 | KING_SE1A | 1 | West | YES | -0.04485 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.050483 | 0 | 40 |  |  | 0 | 0 | -0.050483 | 0 | 1 | 1 |  |  |  |  | 81 | 0
60016 | WOODWRD11A | 1 | West | YES | -0.044823 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.050456 | 0 | 80 |  |  | 0 | 0 | -0.050456 | 0 | 1 | 1 |  |  |  |  | 82 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.044816 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.050449 | 0 | 80 |  |  | 0 | 0 | -0.050449 | 0 | 1 | 1 |  |  |  |  | 83 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | -0.044788 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.050421 | 0 | 150 |  |  | 0 | 0 | -0.050421 | 0 | 1 | 1 |  |  |  |  | 84 | 0
60017 | ORNNWP1 | 1 | West | YES | -0.043874 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.049507 | 0 | 80 |  |  | 0 | 0 | -0.049507 | 0 | 1 | 1 |  |  |  |  | 85 | 0
60018 | DSKY1 | 1 | West | YES | -0.043565 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.049198 | 0 | 84 |  |  | 0 | 0 | -0.049198 | 0 | 1 | 1 |  |  |  |  | 86 | 0
60000 | DSKY2 | 1 | West | YES | -0.043529 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.049162 | 0 | 76.5 |  |  | 0 | 0 | -0.049162 | 0 | 1 | 1 |  |  |  |  | 87 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | -0.043314 | 30 | 0 | 150 |  | 1.02 | Wind | -1 | 0.048947 | 0 | 150 |  |  | 0 | 0 | -0.048947 | 0 | 1 | 1 |  |  |  |  | 88 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.042803 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.048436 | 0 | 112.5 |  |  | 0 | 0 | -0.048436 | 0 | 1 | 1 |  |  |  |  | 89 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.042803 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 149.5 |  |  | 0 | 0 | -0.048436 | 0 | 1 | 1 |  |  |  |  | 90 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.042803 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 186 |  |  | 0 | 0 | -0.048436 | 0 | 1 | 1 |  |  |  |  | 91 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.042803 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 214.5 |  |  | 0 | 0 | -0.048436 | 0 | 1 | 1 |  |  |  |  | 92 | 0
60202 | FRNDDRCS | F | West | YES | -0.038909 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.044542 | 0 | 0 |  |  | 0 | 0 | -0.044542 | 0 | 1 | 1 |  |  |  |  | 93 | 0
11056 | ROSCOE_1G | 1 | West | YES | -0.038521 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.044154 | 0 | 209 |  |  | 0 | 0 | -0.044154 | 0 | 1 | 1 |  |  |  |  | 94 | 0
11057 | CHAMPION_1G | 1 | West | YES | -0.038521 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.044154 | 0 | 126.5 |  |  | 0 | 0 | -0.044154 | 0 | 1 | 1 |  |  |  |  | 95 | 0
11058 | PYRON_1G | 1 | West | YES | -0.038521 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.044154 | 0 | 249 |  |  | 0 | 0 | -0.044154 | 0 | 1 | 1 |  |  |  |  | 96 | 0
11059 | INADALE_1G | 1 | West | YES | -0.038521 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.044154 | 0 | 197 |  |  | 0 | 0 | -0.044154 | 0 | 1 | 1 |  |  |  |  | 97 | 0
6100 | OKLA7A | EQ | West | YES | -0.02434 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.029973 | 0 | 0 |  |  | 0 | 0 | -0.029973 | 0 | 1 | 1 |  |  |  |  | 98 | 0
6752 | OKLA0A | 1 | West | YES | -0.02434 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.029973 | 0 | 649.7 |  |  | 0 | 0 | -0.029973 | 0 | 1 | 1 |  |  |  |  | 99 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.013289 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 | [6 empty] | 100 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.013289 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 | [6 empty] | 101 | 0
88253 | HAMILTON | F | South | YES | -0.013289 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 | [6 empty] | 102 | 0
8262 | ELPS | 1 | South | YES | -0.009524 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.039066 | 0 | 0 |  |  |  |  | 0.039066 | 0 | [6 empty] | 103 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.002087 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.046503 | 0 | 0 |  |  |  |  | 0.046503 | 0 | [6 empty] | 104 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 105 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 106 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 107 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 108 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 109 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 110 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 111 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 112 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 113 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 114 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 115 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 116 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 117 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 118 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 119 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 120 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 121 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 122 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 123 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 124 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 125 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 126 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 127 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | [6 empty] | 128 | 0
80265 | LARECU40A | 4 | South | YES | -0.001313 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.047277 | 100 | 100 |  |  |  |  | 0.047277 | 4.7277 | [6 empty] | 129 | 0
80266 | LARECU50A | 5 | South | YES | -0.001313 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.047277 | 100 | 100 |  |  |  |  | 0.047277 | 4.7277 | [6 empty] | 130 | 0
80012 | LAR | F | South | YES | -0.001312 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.047278 | 0 | 0 |  |  |  |  | 0.047278 | 0 | [6 empty] | 131 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.001264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 | [6 empty] | 132 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.001264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 | [6 empty] | 133 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.001264 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 | [6 empty] | 134 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.001217 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.047373 | 423.3 | 423.3 |  |  |  |  | 0.047373 | 20.0531 | [6 empty] | 135 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.001202 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.047388 | 24 | 24 |  |  |  |  | 0.047388 | 1.1373 | [6 empty] | 136 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.001202 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.047388 | 24.3 | 24.3 |  |  |  |  | 0.047388 | 1.1515 | [6 empty] | 137 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.001202 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.047388 | 23.9 | 23.9 |  |  |  |  | 0.047388 | 1.1326 | [6 empty] | 138 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.001081 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.047509 | 0 | 0 |  |  |  |  | 0.047509 | 0 | [6 empty] | 139 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.001081 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.047509 | 0 | 0 |  |  |  |  | 0.047509 | 0 | [6 empty] | 140 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.000655 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047935 | 0 | 0 |  |  |  |  | 0.047935 | 0 | [6 empty] | 141 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.000655 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047935 | 0 | 0 |  |  |  |  | 0.047935 | 0 | [6 empty] | 142 | 0
88299 | ZAPATA | F | South | YES | -0.000513 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.048077 | 0 | 0 |  |  |  |  | 0.048077 | 0 | [6 empty] | 143 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.04859 | 15 | 15 |  |  |  |  | 0.04859 | 0.72885 | [6 empty] | 144 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 145 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 146 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 147 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 148 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 149 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 150 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 151 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 152 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 | [6 empty] | 153 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | 2.9e-05 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 | [6 empty] | 154 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 2.9e-05 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 | [6 empty] | 155 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 2.9e-05 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 | [6 empty] | 156 | 0
88508 | FALFURRI | F | South | YES | 0.000116 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.048706 | 0 | 0 |  |  |  |  | 0.048706 | 0 | [6 empty] | 157 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | 0.000461 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.049051 | 58 | 58 |  |  |  |  | 0.049051 | 2.845 | [6 empty] | 158 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | 0.000461 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.049051 | 89 | 89 |  |  |  |  | 0.049051 | 4.3656 | [6 empty] | 159 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | 0.000461 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.049051 | 44 | 44 |  |  |  |  | 0.049051 | 2.1583 | [6 empty] | 160 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | 0.000461 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.049051 | 44 | 44 |  |  |  |  | 0.049051 | 2.1583 | [6 empty] | 161 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | 0.000461 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.049051 | 43 | 43 |  |  |  |  | 0.049051 | 2.1092 | [6 empty] | 162 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | 0.000461 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.049051 | 45 | 45 |  |  |  |  | 0.049051 | 2.2073 | [6 empty] | 163 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.000506 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 | [6 empty] | 164 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.000506 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 | [6 empty] | 165 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.000506 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 | [6 empty] | 166 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.00055 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.04914 | 407 | 407 |  |  |  |  | 0.04914 | 20.0001 | [6 empty] | 167 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.000577 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.049167 | 215 | 215 |  |  |  |  | 0.049167 | 10.571 | [6 empty] | 168 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.000577 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.049167 | 216 | 216 |  |  |  |  | 0.049167 | 10.6201 | [6 empty] | 169 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | 0.000579 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.049169 | 418 | 418 |  |  |  |  | 0.049169 | 20.5527 | [6 empty] | 170 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | 0.000579 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.049169 | 400 | 400 |  |  |  |  | 0.049169 | 19.6677 | [6 empty] | 171 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | 0.000595 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.049185 | 0 | 430 |  |  |  |  | 0.049185 | 21.1496 | [6 empty] | 172 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | 0.000595 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.049185 | 0 | 430 |  |  |  |  | 0.049185 | 21.1496 | [6 empty] | 173 | 0
8933 | FGNTS001 | 1 | South | YES | 0.000596 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.049186 | 146.5 | 146.5 |  |  |  |  | 0.049186 | 7.2058 | [6 empty] | 174 | 0
8934 | FGNTS101 | 2 | South | YES | 0.000596 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.049186 | 147.9 | 147.9 |  |  |  |  | 0.049186 | 7.2746 | [6 empty] | 175 | 0
8935 | FGNTS201 | 3 | South | YES | 0.000596 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.049186 | 173 | 173 |  |  |  |  | 0.049186 | 8.5092 | [6 empty] | 176 | 0
88198 | BEEVILLE | F | South | YES | 0.000599 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.049189 | 0 | 0 |  |  |  |  | 0.049189 | 0 | [6 empty] | 177 | 0
5903 | SANMIGUELGEN | 1 | South | YES | 0.000649 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.049239 | 0 | 396.3 |  |  |  |  | 0.049239 | 19.5135 | [6 empty] | 178 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.000654 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.049244 | 61 | 61 |  |  |  |  | 0.049244 | 3.0039 | [6 empty] | 179 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.000654 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.049244 | 95 | 95 |  |  |  |  | 0.049244 | 4.6782 | [6 empty] | 180 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.000654 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.049244 | 151 | 151 |  |  |  |  | 0.049244 | 7.4359 | [6 empty] | 181 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.000676 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.049266 | 155 | 155 |  |  |  |  | 0.049266 | 7.6363 | [6 empty] | 182 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | 0.000676 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.049266 | 174 | 174 |  |  |  |  | 0.049266 | 8.5723 | [6 empty] | 183 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.000676 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.049266 | 155 | 155 |  |  |  |  | 0.049266 | 7.6363 | [6 empty] | 184 | 0
8981 | HECN1 | 1 | South | YES | 0.000691 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.049281 | 144.8 | 144.8 |  |  |  |  | 0.049281 | 7.1359 | [6 empty] | 185 | 0
8982 | HECN2 | 2 | South | YES | 0.000691 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.049281 | 144.1 | 144.1 |  |  |  |  | 0.049281 | 7.1014 | [6 empty] | 186 | 0
8983 | HECN3 | 3 | South | YES | 0.000691 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.049281 | 171.9 | 171.9 |  |  |  |  | 0.049281 | 8.4714 | [6 empty] | 187 | 0
8936 | MVGN#1 | 1 | South | YES | 0.000692 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.049282 | 216.6 | 216.6 |  |  |  |  | 0.049282 | 10.6745 | [6 empty] | 188 | 0
8937 | MVGN#2 | 2 | South | YES | 0.000692 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.049282 | 216.7 | 216.7 |  |  |  |  | 0.049282 | 10.6795 | [6 empty] | 189 | 0
8938 | MVGN#3 | 3 | South | YES | 0.000692 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.049282 | 250.9 | 250.9 |  |  |  |  | 0.049282 | 12.3649 | [6 empty] | 190 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | 0.000705 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.049295 | 0 | 562 |  |  |  |  | 0.049295 | 27.7039 | [6 empty] | 191 | 0
5932 | SI_RAY9 | 9 | South | YES | 0.000732 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.049322 | 38 | 38 |  |  |  |  | 0.049322 | 1.8742 | [6 empty] | 192 | 0
5933 | SI_RAY6 | 6 | South | YES | 0.000732 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.049322 | 19.3 | 19.3 |  |  |  |  | 0.049322 | 0.95192 | [6 empty] | 193 | 0
5935 | SI_RAY10 | 10 | South | YES | 0.000732 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.049322 | 47 | 47 |  |  |  |  | 0.049322 | 2.3181 | [6 empty] | 194 | 0
80003 | MILHWYS | F | South | YES | 0.000732 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.049322 | 0 | 0 |  |  |  |  | 0.049322 | 0 | [6 empty] | 195 | 0
8517 | CELANEBI0A | 1 | South | YES | 0.000754 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.049344 | 0 | 0 |  |  |  |  | 0.049344 | 0 | [6 empty] | 196 | 0
80080 | GWINDT11A | 3 | South | YES | 0.000757 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 38 |  |  |  |  | 0.049347 | 1.8752 | [6 empty] | 197 | 0
80080 | GWINDT11A | 4 | South | YES | 0.000757 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 19 |  |  |  |  | 0.049347 | 0.9376 | [6 empty] | 198 | 0
80080 | GWINDT11A | 2 | South | YES | 0.000757 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 41 |  |  |  |  | 0.049347 | 2.0232 | [6 empty] | 199 | 0
80080 | GWINDT11A | 1 | South | YES | 0.000757 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 94 |  |  |  |  | 0.049347 | 4.6386 | [6 empty] | 200 | 0
80081 | GWINDT21A | 4 | South | YES | 0.000757 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 22 |  |  |  |  | 0.049347 | 1.0856 | [6 empty] | 201 | 0
80081 | GWINDT21A | 1 | South | YES | 0.000757 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 94 |  |  |  |  | 0.049347 | 4.6386 | [6 empty] | 202 | 0
80081 | GWINDT21A | 3 | South | YES | 0.000757 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 43 |  |  |  |  | 0.049347 | 2.1219 | [6 empty] | 203 | 0
80081 | GWINDT21A | 2 | South | YES | 0.000757 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 36 |  |  |  |  | 0.049347 | 1.7765 | [6 empty] | 204 | 0
80180 | PNSCALT11A | 2 | South | YES | 0.000757 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 50 |  |  |  |  | 0.049347 | 2.4674 | [6 empty] | 205 | 0
80180 | PNSCALT11A | 1 | South | YES | 0.000757 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 148 |  |  |  |  | 0.049347 | 7.3034 | [6 empty] | 206 | 0
80181 | PNSCALT21A | 2 | South | YES | 0.000757 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 50 |  |  |  |  | 0.049347 | 2.4674 | [6 empty] | 207 | 0
80181 | PNSCALT21A | 1 | South | YES | 0.000757 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 55 |  |  |  |  | 0.049347 | 2.7141 | [6 empty] | 208 | 0
8461 | KOCH_UP0A | 1 | South | YES | 0.000774 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.049364 | 0 | 0 |  |  |  |  | 0.049364 | 0 | [6 empty] | 209 | 0
8506 | VAL #1 | 1 | South | YES | 0.00078 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 | [6 empty] | 210 | 0
8507 | VAL #2 | 2 | South | YES | 0.00078 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 | [6 empty] | 211 | 0
8511 | OXY_CC0A | 1 | South | YES | 0.00078 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 | [6 empty] | 212 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.000788 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.049378 | 0 | 0 |  |  |  |  | 0.049378 | 0 | [6 empty] | 213 | 0
8459 | B_DAVIS0B | MB | South | YES | 0.00079 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.04938 | 0 | 0 |  |  |  |  | 0.04938 | 0 | [6 empty] | 214 | 0
8460 | B_DAVIS0A | MB | South | YES | 0.00079 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.04938 | 0 | 0 |  |  |  |  | 0.04938 | 0 | [6 empty] | 215 | 0
80263 | B_DAVIS31A | 3 | South | YES | 0.00079 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.04938 | 180 | 180 |  |  |  |  | 0.04938 | 8.8884 | [6 empty] | 216 | 0
80264 | B_DAVIS41A | 4 | South | YES | 0.00079 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.04938 | 180 | 180 |  |  |  |  | 0.04938 | 8.8884 | [6 empty] | 217 | 0
8456 | COSW#1 | 1 | South | YES | 0.000793 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.049383 | 0 | 0 |  |  |  |  | 0.049383 | 0 | [6 empty] | 218 | 0
8457 | COSW#2 | 2 | South | YES | 0.000793 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.049383 | 0 | 0 |  |  |  |  | 0.049383 | 0 | [6 empty] | 219 | 0
8442 | NBEC7 | 7 | South | YES | 0.000796 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.049386 | 367 | 367 |  |  |  |  | 0.049386 | 18.1247 | [6 empty] | 220 | 0
8442 | NBEC7 | MB | South | YES | 0.000796 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 | [6 empty] | 221 | 0
8560 | CNOPGT1 | 1 | South | YES | 0.000796 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 | [6 empty] | 222 | 0
8561 | CNOPGT2 | 2 | South | YES | 0.000796 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 | [6 empty] | 223 | 0
8562 | CNOPST1 | 3 | South | YES | 0.000796 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 | [6 empty] | 224 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.000816 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.049406 | 0 | 0 |  |  |  |  | 0.049406 | 0 | [6 empty] | 225 | 0
8926 | LGE_GT10A | 1 | South | YES | 0.000843 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | [6 empty] | 226 | 0
8927 | LGE_GT20A | 2 | South | YES | 0.000843 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | [6 empty] | 227 | 0
8928 | LGE_STG0A | 3 | South | YES | 0.000843 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | [6 empty] | 228 | 0
8930 | ICPGN10A | 1 | South | YES | 0.000843 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | [6 empty] | 229 | 0
8931 | ICPGN20A | 2 | South | YES | 0.000843 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | [6 empty] | 230 | 0
8932 | ICPGN30A | 3 | South | YES | 0.000843 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | [6 empty] | 231 | 0
80223 | REYSHR G | 1 | South | YES | 0.000843 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 | [6 empty] | 232 | 0
8161 | COLETO0A | 1 | South | YES | 0.000851 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.049441 | 0 | 633 |  |  |  |  | 0.049441 | 31.2963 | [6 empty] | 233 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.000868 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.049458 | 147 | 147 |  |  |  |  | 0.049458 | 7.2704 | [6 empty] | 234 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.000868 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.049458 | 138 | 138 |  |  |  |  | 0.049458 | 6.8252 | [6 empty] | 235 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.000868 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.049458 | 146 | 146 |  |  |  |  | 0.049458 | 7.2209 | [6 empty] | 236 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.000868 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.049458 | 149 | 149 |  |  |  |  | 0.049458 | 7.3693 | [6 empty] | 237 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.000868 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.049458 | 182 | 182 |  |  |  |  | 0.049458 | 9.0014 | [6 empty] | 238 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.000868 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.049458 | 203 | 203 |  |  |  |  | 0.049458 | 10.04 | [6 empty] | 239 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.000882 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 | [6 empty] | 240 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.000882 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 | [6 empty] | 241 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.000882 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 | [6 empty] | 242 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.000914 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.049504 | 148 | 148 |  |  |  |  | 0.049504 | 7.3266 | [6 empty] | 243 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.000914 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.049504 | 148 | 148 |  |  |  |  | 0.049504 | 7.3266 | [6 empty] | 244 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.000914 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.049504 | 154 | 154 |  |  |  |  | 0.049504 | 7.6237 | [6 empty] | 245 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.000914 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.049504 | 293 | 293 |  |  |  |  | 0.049504 | 14.5047 | [6 empty] | 246 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.000944 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.049534 | 0 | 0 |  |  |  |  | 0.049534 | 0 | [6 empty] | 247 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.000944 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.049534 | 0 | 0 |  |  |  |  | 0.049534 | 0 | [6 empty] | 248 | 0
8189 | CUECPL2A | 1 | South | YES | 0.000953 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.049543 | 0 | 0 |  |  |  |  | 0.049543 | 0 | [6 empty] | 249 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.00096 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.04955 | 223.9 | 223.9 |  |  |  |  | 0.04955 | 11.0943 | [6 empty] | 250 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.00096 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.04955 | 225 | 225 |  |  |  |  | 0.04955 | 11.1488 | [6 empty] | 251 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.00096 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.04955 | 224.6 | 224.6 |  |  |  |  | 0.04955 | 11.129 | [6 empty] | 252 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.00096 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.04955 | 226.7 | 226.7 |  |  |  |  | 0.04955 | 11.233 | [6 empty] | 253 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | 0.000967 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.049557 | 22 | 22 |  |  |  |  | 0.049557 | 1.0903 | [6 empty] | 254 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | 0.000967 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.049557 | 11 | 11 |  |  |  |  | 0.049557 | 0.54513 | [6 empty] | 255 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | 0.000967 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.049557 | 11 | 11 |  |  |  |  | 0.049557 | 0.54513 | [6 empty] | 256 | 0
5508 | RAYBURNCC9 | 1 | South | YES | 0.001006 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.049596 | 47.7 | 47.7 |  |  |  |  | 0.049596 | 2.3657 | [6 empty] | 257 | 0
5509 | RAYBURNCC10 | 1 | South | YES | 0.001006 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.049596 | 37.3 | 37.3 |  |  |  |  | 0.049596 | 1.8499 | [6 empty] | 258 | 0
5511 | RAYBURNCC7 | 1 | South | YES | 0.001006 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.049596 | 47.5 | 47.5 |  |  |  |  | 0.049596 | 2.3558 | [6 empty] | 259 | 0
5512 | RAYBURNCC8 | 1 | South | YES | 0.001006 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.049596 | 49.3 | 49.3 |  |  |  |  | 0.049596 | 2.4451 | [6 empty] | 260 | 0
8173 | VICEC51A | 5 | South | YES | 0.001014 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.049604 | 144 | 144 |  |  |  |  | 0.049604 | 7.143 | [6 empty] | 261 | 0
8174 | VICEC61A | 6 | South | YES | 0.001014 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.049604 | 188 | 188 |  |  |  |  | 0.049604 | 9.3256 | [6 empty] | 262 | 0
8066 | DUP1V#1 | 1 | South | YES | 0.001033 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.049623 | 0 | 0 |  |  |  |  | 0.049623 | 0 | [6 empty] | 263 | 0
80224 | VISTRONG1 | 1 | South | YES | 0.001057 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.049647 | 0 | 0 |  |  |  |  | 0.049647 | 0 | [6 empty] | 264 | 0
80225 | VISTRONG2 | 2 | South | YES | 0.001057 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.049647 | 0 | 0 |  |  |  |  | 0.049647 | 0 | [6 empty] | 265 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.00106 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.04965 | 0 | 0 |  |  |  |  | 0.04965 | 0 | [6 empty] | 266 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.00106 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.04965 | 0 | 0 |  |  |  |  | 0.04965 | 0 | [6 empty] | 267 | 0
80227 | AIRCO G | 1 | South | YES | 0.001061 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.049651 | 0 | 0 |  |  |  |  | 0.049651 | 0 | [6 empty] | 268 | 0
8147 | UCAR #2 | 10 | South | YES | 0.001077 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | [6 empty] | 269 | 0
8148 | UCAR #1 | 2 | South | YES | 0.001077 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | [6 empty] | 270 | 0
80137 | CSDR89 | 9 | South | YES | 0.001077 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | [6 empty] | 271 | 0
80137 | CSDR89 | 8 | South | YES | 0.001077 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | [6 empty] | 272 | 0
80138 | CSDR7 | 7 | South | YES | 0.001077 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | [6 empty] | 273 | 0
80139 | CSDR56 | 6 | South | YES | 0.001077 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | [6 empty] | 274 | 0
80139 | CSDR56 | 5 | South | YES | 0.001077 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | [6 empty] | 275 | 0
80140 | CSDR11 | 11 | South | YES | 0.001077 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 | [6 empty] | 276 | 0
9016 | SANDH_G1 | 1 | South | YES | 0.001118 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.049708 | 49 | 49 |  |  |  |  | 0.049708 | 2.4357 | [6 empty] | 277 | 0
9017 | SANDH_G2 | 2 | South | YES | 0.001118 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.049708 | 46 | 46 |  |  |  |  | 0.049708 | 2.2866 | [6 empty] | 278 | 0
9018 | SANDH_G3 | 3 | South | YES | 0.001118 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.049708 | 46 | 46 |  |  |  |  | 0.049708 | 2.2866 | [6 empty] | 279 | 0
9019 | SANDH_G4 | 4 | South | YES | 0.001118 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.049708 | 47 | 47 |  |  |  |  | 0.049708 | 2.3363 | [6 empty] | 280 | 0
9020 | SANDHG5A | 5A | South | YES | 0.001118 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.049708 | 155 | 155 |  |  |  |  | 0.049708 | 7.7048 | [6 empty] | 281 | 0
9021 | SANDHG5C | 5C | South | YES | 0.001118 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.049708 | 148 | 148 |  |  |  |  | 0.049708 | 7.3568 | [6 empty] | 282 | 0
9000 | DECKR_G1 | 1 | South | YES | 0.00112 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.04971 | 321 | 321 |  |  |  |  | 0.04971 | 15.957 | [6 empty] | 283 | 0
9001 | DECKR_G2 | 2 | South | YES | 0.00112 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.04971 | 426 | 426 |  |  |  |  | 0.04971 | 21.1766 | [6 empty] | 284 | 0
80226 | ALCOA G | 1 | South | YES | 0.001152 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.049742 | 0 | 0 |  |  |  |  | 0.049742 | 0 | [6 empty] | 285 | 0
9002 | DECKR_G3 | 3 | South | YES | 0.001161 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.049751 | 42 | 42 |  |  |  |  | 0.049751 | 2.0896 | [6 empty] | 286 | 0
9003 | DECKR_G4 | 4 | South | YES | 0.001161 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.049751 | 44 | 44 |  |  |  |  | 0.049751 | 2.1891 | [6 empty] | 287 | 0
9004 | DECKR_G5 | 5 | South | YES | 0.001161 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.049751 | 44 | 44 |  |  |  |  | 0.049751 | 2.1891 | [6 empty] | 288 | 0
9005 | DECKR_G6 | 6 | South | YES | 0.001161 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.049751 | 47 | 47 |  |  |  |  | 0.049751 | 2.3383 | [6 empty] | 289 | 0
8134 | FOR #1 | 1 | South | YES | 0.001172 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 290 | 0
8138 | FOR #2 | 2 | South | YES | 0.001172 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 291 | 0
8153 | FOR #3 | 3 | South | YES | 0.001172 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 292 | 0
8154 | FOR #4 | 4 | South | YES | 0.001172 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 293 | 0
8155 | FOR #5 | 5 | South | YES | 0.001172 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 294 | 0
8156 | FOR #6 | 6 | South | YES | 0.001172 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 295 | 0
8157 | FOR #7 | 7 | South | YES | 0.001172 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 296 | 0
80051 | FOR #8 | 8 | South | YES | 0.001172 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 297 | 0
80052 | FOR #9 | 9 | South | YES | 0.001172 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 298 | 0
80053 | FOR #10 | 10 | South | YES | 0.001172 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 | [6 empty] | 299 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.001262 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.049852 | 132 | 132 |  |  |  |  | 0.049852 | 6.5805 | [6 empty] | 300 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.001262 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.049852 | 139 | 139 |  |  |  |  | 0.049852 | 6.9295 | [6 empty] | 301 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.001262 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.049852 | 329 | 329 |  |  |  |  | 0.049852 | 16.4014 | [6 empty] | 302 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.001364 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.049954 | 152.5 | 152.5 |  |  |  |  | 0.049954 | 7.618 | [6 empty] | 303 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.001364 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.049954 | 149.5 | 149.5 |  |  |  |  | 0.049954 | 7.4682 | [6 empty] | 304 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.001364 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.049954 | 232.6 | 232.6 |  |  |  |  | 0.049954 | 11.6194 | [6 empty] | 305 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 | [6 empty] | 306 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 | [6 empty] | 307 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 | [6 empty] | 308 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 | [6 empty] | 309 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.001467 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.050057 | 158 | 158 |  |  |  |  | 0.050057 | 7.909 | [6 empty] | 310 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.001467 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.050057 | 160 | 160 |  |  |  |  | 0.050057 | 8.0092 | [6 empty] | 311 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.001467 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.050057 | 175 | 175 |  |  |  |  | 0.050057 | 8.76 | [6 empty] | 312 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.001468 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 606 |  |  |  |  | 0.050058 | 30.3353 | [6 empty] | 313 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.001468 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 598 |  |  |  |  | 0.050058 | 29.9348 | [6 empty] | 314 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.001468 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 436 |  |  |  |  | 0.050058 | 21.8254 | [6 empty] | 315 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.001827 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.050417 | 0 | 580 |  |  |  |  | 0.050417 | 29.242 | [6 empty] | 316 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | 0.001843 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.050433 | 0 | 0 |  |  |  |  | 0.050433 | 0 | [6 empty] | 317 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | 0.001843 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.050433 | 0 | 0 |  |  |  |  | 0.050433 | 0 | [6 empty] | 318 | 0
48731 | CBE_GT1 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 | [6 empty] | 319 | 0
48732 | CBE_GT2 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 | [6 empty] | 320 | 0
48733 | CBE_ST12 | 1 | Houston | YES | 0.001871 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.050461 | 105 | 105 |  |  |  |  | 0.050461 | 5.2984 | [6 empty] | 321 | 0
48734 | CBE_GT3 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 | [6 empty] | 322 | 0
48735 | CBE_GT4 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 | [6 empty] | 323 | 0
48736 | CBE_ST34 | 1 | Houston | YES | 0.001871 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.050461 | 105 | 105 |  |  |  |  | 0.050461 | 5.2984 | [6 empty] | 324 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.001897 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.050487 | 0 | 0 |  |  |  |  | 0.050487 | 0 | [6 empty] | 325 | 0
49851 | DOW17000 | 37 | Houston | YES | 0.002065 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 326 | 0
49858 | DOW38100 | 31 | Houston | YES | 0.002065 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 327 | 0
49859 | DOW38200 | 33 | Houston | YES | 0.002065 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 328 | 0
49860 | DOW38300 | 32 | Houston | YES | 0.002065 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 329 | 0
49862 | DOW39100 | 36 | Houston | YES | 0.002065 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 330 | 0
49863 | DOW39200 | 35 | Houston | YES | 0.002065 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 331 | 0
49865 | DOW41000 | 41 | Houston | YES | 0.002065 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 332 | 0
49866 | DOW42000 | 42 | Houston | YES | 0.002065 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 333 | 0
49869 | DOW49000 | 45 | Houston | YES | 0.002065 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 334 | 0
49870 | DOW61000 | 61 | Houston | YES | 0.002065 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 335 | 0
49871 | DOW62000 | 62 | Houston | YES | 0.002065 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 336 | 0
49872 | DOW63000 | 63 | Houston | YES | 0.002065 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 337 | 0
49873 | DOW64000 | 64 | Houston | YES | 0.002065 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 338 | 0
49876 | DOW65000 | 65 | Houston | YES | 0.002065 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 339 | 0
49877 | DOW66000 | 66 | Houston | YES | 0.002065 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 340 | 0
49878 | DOW67000 | 67 | Houston | YES | 0.002065 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 341 | 0
49882 | DOW81000 | 81 | Houston | YES | 0.002065 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 342 | 0
49884 | DOW82000 | 82 | Houston | YES | 0.002065 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 343 | 0
49885 | DOW83000 | 83 | Houston | YES | 0.002065 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 344 | 0
49886 | DOW84000 | 84 | Houston | YES | 0.002065 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 | [6 empty] | 345 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.002098 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.050688 | 0 | 581 |  |  |  |  | 0.050688 | 29.4499 | [6 empty] | 346 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.002105 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.050695 | 0 | 0 |  |  |  |  | 0.050695 | 0 | [6 empty] | 347 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.002105 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.050695 | 0 | 0 |  |  |  |  | 0.050695 | 0 | [6 empty] | 348 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.002139 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 | [6 empty] | 349 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.002139 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 | [6 empty] | 350 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.002139 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 | [6 empty] | 351 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.002139 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 | [6 empty] | 352 | 0
48730 | MNS_GT | 1 | Houston | YES | 0.002251 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.050841 | 0 | 0 |  |  |  |  | 0.050841 | 0 | [6 empty] | 353 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.002259 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 651 |  |  |  |  | 0.050849 | 33.1028 | [6 empty] | 354 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.002259 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 564 |  |  |  |  | 0.050849 | 28.679 | [6 empty] | 355 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.002259 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 603 |  |  |  |  | 0.050849 | 30.6621 | [6 empty] | 356 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.00226 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.05085 | 167.7 | 167.7 |  |  |  |  | 0.05085 | 8.5276 | [6 empty] | 357 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.00226 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.05085 | 166.4 | 166.4 |  |  |  |  | 0.05085 | 8.4615 | [6 empty] | 358 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.00226 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.05085 | 252.4 | 252.4 |  |  |  |  | 0.05085 | 12.8346 | [6 empty] | 359 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.002268 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.050858 | 0 | 0 |  |  |  |  | 0.050858 | 0 | [6 empty] | 360 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.002281 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.050871 | 166 | 166 |  |  |  |  | 0.050871 | 8.4446 | [6 empty] | 361 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.002281 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.050871 | 166 | 166 |  |  |  |  | 0.050871 | 8.4446 | [6 empty] | 362 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.002281 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.050871 | 248 | 248 |  |  |  |  | 0.050871 | 12.6161 | [6 empty] | 363 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.002281 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.050871 | 546 | 546 |  |  |  |  | 0.050871 | 27.7757 | [6 empty] | 364 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.002281 | 618.1 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.050871 | 0 | 654 |  |  |  |  | 0.050871 | 33.2698 | [6 empty] | 365 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.002281 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.050871 | 13 | 13 |  |  |  |  | 0.050871 | 0.66133 | [6 empty] | 366 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.002342 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 367 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.002342 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 368 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.002342 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 369 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.002342 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 370 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.002342 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 371 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.002342 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 372 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.002342 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 373 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.002342 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 374 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.002342 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 375 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.002342 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 376 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.002342 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 377 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.002342 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 378 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.002342 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 379 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.002342 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 380 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.002342 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 | [6 empty] | 381 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | 0.002372 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.050962 | 0 | 0 |  |  |  |  | 0.050962 | 0 | [6 empty] | 382 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.002393 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | [6 empty] | 383 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.002393 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | [6 empty] | 384 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.002393 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | [6 empty] | 385 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.002393 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | [6 empty] | 386 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.002393 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 | [6 empty] | 387 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.0024 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 | [6 empty] | 388 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.0024 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 | [6 empty] | 389 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.0024 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 | [6 empty] | 390 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.0024 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0
48691 | GBY_73741085 | B | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972
48691 | GBY_73741085 | A | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972
48692 | GBY_81821075 | D | Houston | YES | 0.002413 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.051003 | 55 | 55 |  |  |  |  | 0.051003 | 2.8052
48692 | GBY_81821075 | C | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972
48693 | GBY_83841065 | F | Houston | YES | 0.002413 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.051003 | 54 | 54 |  |  |  |  | 0.051003 | 2.7542
48693 | GBY_83841065 | E | Houston | YES | 0.002413 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.051003 | 57 | 57 |  |  |  |  | 0.051003 | 2.9072
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.002415 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.051005 | 0 | 0 |  |  |  |  | 0.051005 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.002415 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.051005 | 0 | 0 |  |  |  |  | 0.051005 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.002418 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.051008 | 163.2 | 163.2 |  |  |  |  | 0.051008 | 8.3245
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.002418 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.051008 | 157.1 | 157.1 |  |  |  |  | 0.051008 | 8.0134
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.002418 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.051008 | 157.5 | 157.5 |  |  |  |  | 0.051008 | 8.0338
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.002418 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.051008 | 157 | 157 |  |  |  |  | 0.051008 | 8.0083
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.002418 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.051008 | 282 | 282 |  |  |  |  | 0.051008 | 14.3843
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.002423 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.051013 | 0 | 0 |  |  |  |  | 0.051013 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.002427 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.051017 | 0 | 0 |  |  |  |  | 0.051017 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.002427 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.051017 | 0 | 0 |  |  |  |  | 0.051017 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.002427 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.051017 | 165 | 165 |  |  |  |  | 0.051017 | 8.4178
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.002427 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.051017 | 176 | 176 |  |  |  |  | 0.051017 | 8.979
48855 | SRB_GT211035 | B1 | Houston | YES | 0.002427 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.051017 | 18 | 18 |  |  |  |  | 0.051017 | 0.91831
48855 | SRB_GT211035 | B2 | Houston | YES | 0.002427 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.051017 | 12 | 12 |  |  |  |  | 0.051017 | 0.61221
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.002428 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.002428 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.002428 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.002428 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.002428 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.002428 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.002428 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0
48845 | SOL_GT1 | 1 | Houston | YES | 0.002428 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.051018 | 16.2 | 16.2 |  |  |  |  | 0.051018 | 0.8265
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.002428 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.051018 | 213 | 213 |  |  |  |  | 0.051018 | 10.8669
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.002428 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.051018 | 228 | 228 |  |  |  |  | 0.051018 | 11.6322
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.002433 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0
48821 | SHELLG2 | 2 | Houston | YES | 0.002433 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.002433 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.002433 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.002441 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.051031 | 0 | 0 |  |  |  |  | 0.051031 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.002442 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.051032 | 42 | 42 |  |  |  |  | 0.051032 | 2.1434
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.002442 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.051032 | 42 | 42 |  |  |  |  | 0.051032 | 2.1434
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.002442 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.051032 | 39 | 39 |  |  |  |  | 0.051032 | 1.9903
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.002442 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.051032 | 39 | 39 |  |  |  |  | 0.051032 | 1.9903
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.002444 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.051034 | 0 | 0 |  |  |  |  | 0.051034 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.002444 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.051034 | 0 | 0 |  |  |  |  | 0.051034 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.002456 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.051046 | 107 | 107 |  |  |  |  | 0.051046 | 5.4619
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.002456 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.051046 | 108 | 108 |  |  |  |  | 0.051046 | 5.513
48875 | THW_3132 | A | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075
48875 | THW_3132 | B | Houston | YES | 0.002456 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.051046 | 53 | 53 |  |  |  |  | 0.051046 | 2.7054
48877 | THW_3334 | C | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075
48877 | THW_3334 | D | Houston | YES | 0.002456 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.051046 | 57 | 57 |  |  |  |  | 0.051046 | 2.9096
48879 | THW_4142 | E | Houston | YES | 0.002456 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.051046 | 56 | 56 |  |  |  |  | 0.051046 | 2.8586
48879 | THW_4142 | F | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075
48881 | THW_4344 | G | Houston | YES | 0.002456 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.051046 | 58 | 58 |  |  |  |  | 0.051046 | 2.9607
48881 | THW_4344 | H | Houston | YES | 0.002456 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.051046 | 58 | 58 |  |  |  |  | 0.051046 | 2.9607
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.002462 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.051052 | 746 | 746 |  |  |  |  | 0.051052 | 38.085
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.002468 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.051058 | 12 | 12 |  |  |  |  | 0.051058 | 0.6127
49803 | EXN_15GT | 1 | Houston | YES | 0.002468 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49804 | EXN_16GT | 2 | Houston | YES | 0.002468 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49805 | EXN_17GT | 3 | Houston | YES | 0.002468 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49826 | EXN938GT | 5 | Houston | YES | 0.002468 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49828 | EXN941GT | 10 | Houston | YES | 0.002468 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49829 | EXN942GT | 11 | Houston | YES | 0.002468 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49830 | EXN943GT | 12 | Houston | YES | 0.002468 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49831 | EXN944GT | 13 | Houston | YES | 0.002468 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49832 | EXN945GT | 9 | Houston | YES | 0.002468 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49837 | EXN_GT | 4 | Houston | YES | 0.002468 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
49838 | EXN_14GT | 14 | Houston | YES | 0.002468 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0
48651 | EP_1_2 | 1 | Houston | YES | 0.002473 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0
48651 | EP_1_2 | 2 | Houston | YES | 0.002473 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.002473 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.002474 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.051064 | 744 | 744 |  |  |  |  | 0.051064 | 37.9918
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.002474 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.002474 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.002474 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.002474 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.002474 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.002474 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.002474 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.002477 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.051067 | 0 | 0 |  |  |  |  | 0.051067 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.002488 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.051078 | 162.8 | 162.8 |  |  |  |  | 0.051078 | 8.3155
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.002488 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.051078 | 161.4 | 161.4 |  |  |  |  | 0.051078 | 8.244
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.002488 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.051078 | 158.9 | 158.9 |  |  |  |  | 0.051078 | 8.1163
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.002488 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.051078 | 269.2 | 269.2 |  |  |  |  | 0.051078 | 13.7503
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.002492 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.051082 | 398 | 398 |  |  |  |  | 0.051082 | 20.3307
48885 | THW_5152 | B | Houston | YES | 0.002496 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.051086 | 59 | 59 |  |  |  |  | 0.051086 | 3.0141
48885 | THW_5152 | A | Houston | YES | 0.002496 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.051086 | 58 | 58 |  |  |  |  | 0.051086 | 2.963
48886 | THW_5354 | D | Houston | YES | 0.002496 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.051086 | 58 | 58 |  |  |  |  | 0.051086 | 2.963
48886 | THW_5354 | C | Houston | YES | 0.002496 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.051086 | 57 | 57 |  |  |  |  | 0.051086 | 2.9119
48887 | THW_5556 | E | Houston | YES | 0.002496 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.051086 | 59 | 59 |  |  |  |  | 0.051086 | 3.0141
48887 | THW_5556 | F | Houston | YES | 0.002496 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.051086 | 57 | 57 |  |  |  |  | 0.051086 | 2.9119
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.002553 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.002553 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.002553 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.002553 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.002553 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.002865 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.051455 | 0 | 0 | 0 | 0 |  |  | 0.051455 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.002865 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.051455 | 0 | 0 | 0 | 0 |  |  | 0.051455 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.003066 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.051656 | 154.2 | 154.2 | 0.47278 | 154.2 |  |  | 0.051656 | 7.9654
48672 | FTR_GT2_5110 | 2 | North | YES | 0.003066 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.051656 | 159 | 159 | 0.48749 | 159 |  |  | 0.051656 | 8.2133
48673 | FTR_GT3_5085 | 3 | North | YES | 0.003066 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.051656 | 158 | 158 | 0.48443 | 158 |  |  | 0.051656 | 8.1617
48674 | FTR_CN4_5095 | 4 | North | YES | 0.003066 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.051656 | 380 | 380 | 1.1651 | 380 |  |  | 0.051656 | 19.6294
1877 | WLFHOLW_1G | 1 | North | YES | 0.003099 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.051689 | 217.3 | 217.3 | 0.67341 | 217.3 |  |  | 0.051689 | 11.2321
1878 | WLFHOLW_2G | 2 | North | YES | 0.003099 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.051689 | 215.7 | 215.7 | 0.66845 | 215.7 |  |  | 0.051689 | 11.1494
1879 | WLFHOLW_3G | 3 | North | YES | 0.003099 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.051689 | 272.4 | 272.4 | 0.84417 | 272.4 |  |  | 0.051689 | 14.0801
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.003164 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.051754 | 48 | 48 | 0.15187 | 48 |  |  | 0.051754 | 2.4842
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.003164 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.051754 | 46 | 46 | 0.14554 | 46 |  |  | 0.051754 | 2.3807
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.003164 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.051754 | 105 | 105 | 0.33222 | 105 |  |  | 0.051754 | 5.4342
32886 | BRYN_ATKINS3 | MB | North | YES | 0.003171 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.003171 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.003171 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.051761 | 17 | 17 | 0.053907 | 17 |  |  | 0.051761 | 0.87994
32890 | BRYN_ATKINS4 | MB | North | YES | 0.003171 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.003171 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | 0.003173 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.051763 | 0 | 463 | 1.4691 | 463 |  |  | 0.051763 | 23.9664
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.003174 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.051764 | 32 | 32 | 0.10157 | 32 |  |  | 0.051764 | 1.6565
3416 | LAKE_CRK1_G | 1 | North | YES | 0.003177 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.051767 | 75 | 75 | 0.23827 | 75 |  |  | 0.051767 | 3.8825
3417 | LAKE_CRK2_G | 2 | North | YES | 0.003177 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.051767 | 222 | 222 | 0.70529 | 222 |  |  | 0.051767 | 11.4923
3403 | THOUSE_1G | 1 | North | YES | 0.003296 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.051886 | 563 | 563 | 1.8556 | 563 |  |  | 0.051886 | 29.2119
3404 | THOUSE_2G | 2 | North | YES | 0.003296 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.051886 | 807 | 807 | 2.6599 | 807 |  |  | 0.051886 | 41.8722
238 | BOSQUESW505 | 1 | North | YES | 0.003321 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.051911 | 255 | 255 | 0.84686 | 255 |  |  | 0.051911 | 13.2374
239 | BOSQUESW502 | 1 | North | YES | 0.003321 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.051911 | 149 | 149 | 0.49483 | 149 |  |  | 0.051911 | 7.7348
247 | BOSQUESW501 | 2 | North | YES | 0.003321 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.051911 | 156 | 156 | 0.51808 | 156 |  |  | 0.051911 | 8.0982
251 | BOSQUESW803 | 2 | North | YES | 0.003372 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.051962 | 150 | 150 | 0.5058 | 150 |  |  | 0.051962 | 7.7943
253 | BOSQUESW804 | 2 | North | YES | 0.003372 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.051962 | 80 | 80 | 0.26976 | 80 |  |  | 0.051962 | 4.157
39960 | TNTNPONE_18 | 1 | North | YES | 0.003514 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.052104 | 0 | 152.3 | 0.53518 | 152.3 |  |  | 0.052104 | 7.9355
39970 | TNTNPONE_28 | 1 | North | YES | 0.003514 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.052104 | 0 | 153 | 0.53764 | 153 |  |  | 0.052104 | 7.9719
48721 | LEG_1___1 | 1 | North | YES | 0.003651 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.052241 | 0 | 827 | 3.0194 | 827 |  |  | 0.052241 | 43.2035
48722 | LEG_2___2 | 2 | North | YES | 0.003651 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.052241 | 0 | 819 | 2.9902 | 819 |  |  | 0.052241 | 42.7856
1643 | SLSTR1PP_1G | 1 | North | YES | 0.003654 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.052244 | 0 | 60 | 0.21924 | 60 |  |  | 0.052244 | 3.1347
244 | WHITNYDM01 | 1 | North | YES | 0.003812 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.052402 | 0 | 0 | 0 | 0 |  |  | 0.052402 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.003812 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.052402 | 0 | 0 | 0 | 0 |  |  | 0.052402 | 0
1889 | DECRDOVA_1G | 1 | North | YES | 0.003993 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.052583 | 779 | 779 | 3.1105 | 779 |  |  | 0.052583 | 40.9623
3381 | BBRN_1G | 1 | North | YES | 0.004017 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.052607 | 0 | 618 | 2.4825 | 618 |  |  | 0.052607 | 32.5113
3382 | BBRN_2G | 2 | North | YES | 0.004017 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.052607 | 0 | 589 | 2.366 | 589 |  |  | 0.052607 | 30.9857
13131 | CALFREST_1G | 1 | North | YES | 0.004077 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.052667 | 150.7 | 150.7 | 0.6144 | 150.7 |  |  | 0.052667 | 7.937
13132 | CALFREST_2G | 2 | North | YES | 0.004077 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.052667 | 151 | 151 | 0.61563 | 151 |  |  | 0.052667 | 7.9528
13133 | CALFREST_3G | 3 | North | YES | 0.004077 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.052667 | 177.4 | 177.4 | 0.72326 | 177.4 |  |  | 0.052667 | 9.3432
366 | JNSNCNTY802 | 1 | North | YES | 0.004093 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.052683 | 0 | 0 | 0 | 0 |  |  | 0.052683 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.004093 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.052683 | 0 | 0 | 0 | 0 |  |  | 0.052683 | 0
13134 | CALFREST_4G | 4 | North | YES | 0.004093 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.052683 | 151.5 | 151.5 | 0.62009 | 151.5 |  |  | 0.052683 | 7.9815
13135 | CALFREST_5G | 5 | North | YES | 0.004093 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.052683 | 152.3 | 152.3 | 0.62336 | 152.3 |  |  | 0.052683 | 8.0237
13136 | CALFREST_6G | 6 | North | YES | 0.004093 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.052683 | 177.5 | 177.5 | 0.72651 | 177.5 |  |  | 0.052683 | 9.3513
1937 | MDLTHELP_5G | 5 | North | YES | 0.004242 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.052832 | 224 | 224 | 0.95021 | 224 |  |  | 0.052832 | 11.8344
1938 | MDLTHELP_6G | 6 | North | YES | 0.004242 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.052832 | 226 | 226 | 0.95869 | 226 |  |  | 0.052832 | 11.9401
1943 | MDLTHELP_3G | 3 | North | YES | 0.004242 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.052832 | 212 | 212 | 0.8993 | 212 |  |  | 0.052832 | 11.2004
1944 | MDLTHELP_4G | 4 | North | YES | 0.004242 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.052832 | 211 | 211 | 0.89506 | 211 |  |  | 0.052832 | 11.1476
3126 | TRINIDAD_6G | 1 | North | YES | 0.004321 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.052911 | 224 | 224 | 0.9679 | 224 |  |  | 0.052911 | 11.8521
1941 | MDLTHELP_1G | 1 | North | YES | 0.004375 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.052965 | 216.4 | 216.4 | 0.94675 | 216.4 |  |  | 0.052965 | 11.4617
1942 | MDLTHELP_2G | 2 | North | YES | 0.004375 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.052965 | 216.1 | 216.1 | 0.94544 | 216.1 |  |  | 0.052965 | 11.4458
1892 | DECRDOVA_2G | A | North | YES | 0.004383 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.052973 | 70 | 70 | 0.30681 | 70 |  |  | 0.052973 | 3.7081
1893 | DECRDOVA_3G | B | North | YES | 0.004383 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.052973 | 69 | 69 | 0.30243 | 69 |  |  | 0.052973 | 3.6552
1894 | DECRDOVA_4G | C | North | YES | 0.004383 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.052973 | 69 | 69 | 0.30243 | 69 |  |  | 0.052973 | 3.6552
1895 | DECRDOVA_5G | D | North | YES | 0.004383 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.052973 | 68 | 68 | 0.29804 | 68 |  |  | 0.052973 | 3.6022
12322 | ENNSTRAC_1G | 1 | North | YES | 0.004392 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.052982 | 196 | 196 | 0.86083 | 196 |  |  | 0.052982 | 10.3845
12323 | ENNSTRAC_2G | 2 | North | YES | 0.004392 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.052982 | 116 | 116 | 0.50947 | 116 |  |  | 0.052982 | 6.1459
3107 | STRYKER_1G | 1 | North | YES | 0.004401 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.052991 | 182 | 182 | 0.80098 | 182 |  |  | 0.052991 | 9.6444
3108 | STRYKER_2G | 2 | North | YES | 0.004401 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.052991 | 484 | 484 | 2.1301 | 484 |  |  | 0.052991 | 25.6478
3309 | ASPN_G | 1 | North | YES | 0.004406 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.052996 | 50 | 50 | 0.2203 | 50 |  |  | 0.052996 | 2.6498
3348 | CHAMPION_1G | MB | North | YES | 0.00441 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.053 | 0 | 0 | 0 | 0 |  |  | 0.053 | 0
13116 | TGATEWAY_1G | 1 | North | YES | 0.004442 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.053032 | 151 | 151 | 0.67074 | 151 |  |  | 0.053032 | 8.0079
13117 | TGATEWAY_2G | 2 | North | YES | 0.004442 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.053032 | 130 | 130 | 0.57746 | 130 |  |  | 0.053032 | 6.8942
13118 | TGATEWAY_3G | 3 | North | YES | 0.004442 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.053032 | 148 | 148 | 0.65742 | 148 |  |  | 0.053032 | 7.8488
13119 | TGATEWAY_4G | 4 | North | YES | 0.004442 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.053032 | 399 | 399 | 1.7724 | 399 |  |  | 0.053032 | 21.1599
3097 | MARTLAKE_1G | 1 | North | YES | 0.004479 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 790 | 3.5384 | 790 |  |  | 0.053069 | 41.9247
3098 | MARTLAKE_2G | 2 | North | YES | 0.004479 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 795 | 3.5608 | 795 |  |  | 0.053069 | 42.19
3099 | MARTLAKE_3G | 3 | North | YES | 0.004479 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 804 | 3.6011 | 804 |  |  | 0.053069 | 42.6677
2413 | MTCK6_G | 6 | North | YES | 0.004678 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.053268 | 118 | 118 | 0.552 | 118 |  |  | 0.053268 | 6.2857
2414 | MTCK7_G | 7 | North | YES | 0.004678 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.053268 | 115 | 115 | 0.53797 | 115 |  |  | 0.053268 | 6.1258
2417 | MTCK8_G | 8 | North | YES | 0.004678 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.053268 | 556 | 556 | 2.601 | 556 |  |  | 0.053268 | 29.6171
12440 | PARKD_1SVC8 | 1 | North | YES | 0.004735 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.053325 | 0 | 0 | 0 | 0 |  |  | 0.053325 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.004735 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.053325 | 0 | 0 | 0 | 0 |  |  | 0.053325 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.004751 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.053341 | 161 | 161 | 0.76491 | 161 |  |  | 0.053341 | 8.5879
12412 | FPLEFR1B_G | 2 | North | YES | 0.004751 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.053341 | 164 | 164 | 0.77916 | 164 |  |  | 0.053341 | 8.748
12413 | FPLEFR1C_G | 3 | North | YES | 0.004751 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.053341 | 164 | 164 | 0.77916 | 164 |  |  | 0.053341 | 8.748
12414 | FPLEFR1S_G | 4 | North | YES | 0.004751 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.053341 | 414 | 414 | 1.9669 | 414 |  |  | 0.053341 | 22.0833
12421 | FPLEFR2A_G | 1 | North | YES | 0.004751 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.053341 | 162 | 162 | 0.76966 | 162 |  |  | 0.053341 | 8.6413
12422 | FPLEFR2B_G | 2 | North | YES | 0.004751 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.053341 | 161 | 161 | 0.76491 | 161 |  |  | 0.053341 | 8.5879
12423 | FPLEFR2C_G | 3 | North | YES | 0.004751 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.053341 | 163 | 163 | 0.77441 | 163 |  |  | 0.053341 | 8.6946
12424 | FPLEFR2S_G | 4 | North | YES | 0.004751 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.053341 | 415 | 415 | 1.9717 | 415 |  |  | 0.053341 | 22.1366
2451 | LKHB1_G | 1 | North | YES | 0.004769 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.053359 | 391 | 391 | 1.8647 | 391 |  |  | 0.053359 | 20.8635
2452 | LKHB2_G | 2 | North | YES | 0.004769 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.053359 | 516 | 516 | 2.4608 | 516 |  |  | 0.053359 | 27.5334
948 | STEAM1 | 1 | North | YES | 0.004863 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.053453 | 20 | 20 | 0.09726 | 20 |  |  | 0.053453 | 1.0691
949 | STEAM2 | 1 | North | YES | 0.004863 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.053453 | 26 | 26 | 0.12644 | 26 |  |  | 0.053453 | 1.3898
950 | STEAM3 | 1 | North | YES | 0.004863 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.053453 | 42 | 42 | 0.20425 | 42 |  |  | 0.053453 | 2.245
837 | NEWMAN_G5 | 1 | North | YES | 0.004866 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.053456 | 40 | 40 | 0.19464 | 40 |  |  | 0.053456 | 2.1382
842 | OLINGER_G1 | 1 | North | YES | 0.004881 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.053471 | 79 | 79 | 0.3856 | 79 |  |  | 0.053471 | 4.2242
843 | OLINGER_G2 | 1 | North | YES | 0.004881 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.053471 | 110 | 110 | 0.53691 | 110 |  |  | 0.053471 | 5.8818
844 | OLINGER_G3 | 1 | North | YES | 0.004881 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.053471 | 150 | 150 | 0.73215 | 150 |  |  | 0.053471 | 8.0207
845 | OLINGER_G4 | 1 | North | YES | 0.004881 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.053471 | 76 | 76 | 0.37096 | 76 |  |  | 0.053471 | 4.0638
1701 | MOSES_1G | 1 | North | YES | 0.004963 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 558 | 2.7694 | 558 |  |  | 0.053553 | 29.8827
1702 | MOSES_2G | 2 | North | YES | 0.004963 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 579 | 2.8736 | 579 |  |  | 0.053553 | 31.0073
1703 | MOSES_3G | 3 | North | YES | 0.004963 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 808 | 4.0101 | 808 |  |  | 0.053553 | 43.271
5925 | DCEAST | EQ | North | YES | 0.004963 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.053553 | 0 | 0 | 0 | 0 |  |  | 0.053553 | 0
1675 | PEC_1G | 1 | North | YES | 0.005012 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0
1676 | PEC_2G | 2 | North | YES | 0.005012 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0
1677 | PEC_3G | 3 | North | YES | 0.005012 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.005012 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.053602 | 160 | 160 | 0.80192 | 160 |  |  | 0.053602 | 8.5764
1679 | LAMARPWR_2G | 2 | North | YES | 0.005012 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.053602 | 156 | 156 | 0.78187 | 156 |  |  | 0.053602 | 8.3619
1680 | LAMARPWR_3G | 3 | North | YES | 0.005012 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.053602 | 196 | 196 | 0.98235 | 196 |  |  | 0.053602 | 10.506
1681 | LAMARPWR_4G | 4 | North | YES | 0.005012 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.053602 | 156 | 156 | 0.78187 | 156 |  |  | 0.053602 | 8.3619
1682 | LAMARPWR_5G | 5 | North | YES | 0.005012 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.053602 | 157 | 157 | 0.78688 | 157 |  |  | 0.053602 | 8.4155
1683 | LAMARPWR_6G | 6 | North | YES | 0.005012 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.053602 | 198 | 198 | 0.99238 | 198 |  |  | 0.053602 | 10.6132
1948 | HANDLEY_4G | 4 | North | YES | 0.005031 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.053621 | 435 | 435 | 2.1885 | 435 |  |  | 0.053621 | 23.3252
1689 | VALLEY_3G | 3 | North | YES | 0.005034 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.053624 | 375 | 375 | 1.8878 | 375 |  |  | 0.053624 | 20.1091
11691 | KMICHICT1_G | 1 | North | YES | 0.005034 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.053624 | 144 | 144 | 0.7249 | 144 |  |  | 0.053624 | 7.7219
11692 | KMICHICT2_G | 2 | North | YES | 0.005034 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.053624 | 146 | 146 | 0.73496 | 146 |  |  | 0.053624 | 7.8291
11693 | KMICHIST3_G | 3 | North | YES | 0.005034 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.053624 | 312 | 312 | 1.5706 | 312 |  |  | 0.053624 | 16.7308
11694 | KMICHICT4_G | 4 | North | YES | 0.005034 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.053624 | 144 | 144 | 0.7249 | 144 |  |  | 0.053624 | 7.7219
11695 | KMICHICT5_G | 5 | North | YES | 0.005034 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.053624 | 148 | 148 | 0.74503 | 148 |  |  | 0.053624 | 7.9364
11696 | KMICHIST6_G | 6 | North | YES | 0.005034 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.053624 | 310 | 310 | 1.5605 | 310 |  |  | 0.053624 | 16.6235
1947 | HANDLEY_3G | 3 | North | YES | 0.005036 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.053626 | 395 | 395 | 1.9892 | 395 |  |  | 0.053626 | 21.1824
1949 | HANDLEY_5G | 5 | North | YES | 0.005036 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.053626 | 435 | 435 | 2.1907 | 435 |  |  | 0.053626 | 23.3274
2381 | NTHLK1_G | 1 | North | YES | 0.005044 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.053634 | 156 | 156 | 0.78686 | 156 |  |  | 0.053634 | 8.3669
2382 | NTHLK2_G | 2 | North | YES | 0.005044 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.053634 | 181 | 181 | 0.91296 | 181 |  |  | 0.053634 | 9.7078
2383 | NTHLK3_G | 3 | North | YES | 0.005044 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.053634 | 329 | 329 | 1.6595 | 329 |  |  | 0.053634 | 17.6457
1687 | VALLEY_1G | 1 | North | YES | 0.005154 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.053744 | 170 | 170 | 0.87618 | 170 |  |  | 0.053744 | 9.1365
1688 | VALLEY_2G | 2 | North | YES | 0.005154 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.053744 | 527 | 527 | 2.7162 | 527 |  |  | 0.053744 | 28.3232
2371 | COLLIN_1G | MB | North | YES | 0.005219 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.053809 | 0 | 0 | 0 | 0 |  |  | 0.053809 | 0
6948 | DENISNDM | 1 | North | YES | 0.005237 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.053827 | 0 | 0 | 0 | 0 |  |  | 0.053827 | 0
6948 | DENISNDM | 2 | North | YES | 0.005237 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.053827 | 0 | 0 | 0 | 0 |  |  | 0.053827 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.006131 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.054721 | 61 | 61 | 0.37399 | 61 |  |  | 0.054721 | 3.338
924 | SPENCER_G5 | 1 | North | YES | 0.006131 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.054721 | 66 | 66 | 0.40465 | 66 |  |  | 0.054721 | 3.6116
1861 | EAGLEMNT_1G | MB | North | YES | 0.006645 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.006645 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.006645 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0
1453 | WCPWRCO_1G | 1 | North | YES | 0.007071 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.055661 | 204 | 204 | 1.4425 | 204 |  |  | 0.055661 | 11.3549
1454 | WCPWRCO_2G | 2 | North | YES | 0.007071 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.055661 | 204 | 204 | 1.4425 | 204 |  |  | 0.055661 | 11.3549
1455 | WCPWRCO_3G | 3 | North | YES | 0.007071 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.055661 | 242 | 242 | 1.7112 | 242 |  |  | 0.055661 | 13.47
728 | WOLFRIDGE801 | 1 | North | YES | 0.00863 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.05722 | 0 | 112.5 | 0.97088 | 112.5 |  |  | 0.05722 | 6.4373
1432 | GRHAMSES_2G | 2 | North | YES | 0.01108 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.05967 | 366 | 366 | 4.0553 | 366 |  |  | 0.05967 | 21.8393
1437 | MESQUITW_1G | 1 | North | YES | 0.01108 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.05967 | 0 | 400 | 4.432 | 400 |  |  | 0.05967 | 23.8681
1438 | MESQUITW_2G | 1 | North | YES | 0.01108 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.05967 | 0 | 236 | 2.6149 | 236 |  |  | 0.05967 | 14.0822
1442 | COKFIELD_5 | 1 | North | YES | 0.01108 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.05967 | 0 | 165 | 1.8282 | 165 |  |  | 0.05967 | 9.8456
580 | JCKCNTY801 | 1 | North | YES | 0.011414 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.060004 | 288 | 288 | 3.2872 | 288 |  |  | 0.060004 | 17.2812
581 | JCKCNTY802 | 2 | North | YES | 0.011414 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.060004 | 147 | 147 | 1.6779 | 147 |  |  | 0.060004 | 8.8206
582 | JCKCNTY803 | 3 | North | YES | 0.011414 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.060004 | 147 | 147 | 1.6779 | 147 |  |  | 0.060004 | 8.8206
1479 | WFCOGEN_1G | 1 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.012797 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0
332 | RWMILLER01 | 1 | North | YES | 0.012978 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.061568 | 73 | 73 | 0.94739 | 73 |  |  | 0.061568 | 4.4945
333 | RWMILLER02 | 2 | North | YES | 0.012978 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.061568 | 119 | 119 | 1.5444 | 119 |  |  | 0.061568 | 7.3266
334 | RWMILLER03 | 3 | North | YES | 0.012978 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.061568 | 208 | 208 | 2.6994 | 208 |  |  | 0.061568 | 12.8062
335 | RWMILLER04 | 4 | North | YES | 0.012978 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.061568 | 102 | 102 | 1.3238 | 102 |  |  | 0.061568 | 6.28
336 | RWMILLER05 | 5 | North | YES | 0.012978 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.061568 | 101 | 101 | 1.3108 | 101 |  |  | 0.061568 | 6.2184
503 | NTHTEXAS01 | 1 | North | YES | 0.013714 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.062304 | 18 | 18 | 0.24685 | 18 |  |  | 0.062304 | 1.1215
504 | NTHTEXAS02 | 2 | North | YES | 0.013714 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.062304 | 18 | 18 | 0.24685 | 18 |  |  | 0.062304 | 1.1215
505 | NTHTEXAS03 | 3 | North | YES | 0.013714 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.062304 | 38 | 38 | 0.52113 | 38 |  |  | 0.062304 | 2.3676
344 | MRSSHPRD | 1 | North | YES | 0.023526 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.072116 | 0 | 0 | 0 | 0 |  |  | 0.072116 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.023526 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.072116 | 0 | 0 | 0 | 0 |  |  | 0.072116 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.039674 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.088264 | 0 | 120 | 4.7609 | 120 |  |  | 0.088264 | 10.5917
1433 | GRHAMSES_1G | 1 | North | YES | 0.069041 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.11763 | 242 | 242 | 16.7079 | 242 |  |  | 0.11763 | 28.4668
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Bound Gen
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | max of zone correlation | 0.029973 |  |  | Neg PTDF weight | Pos PTDF weight
6100 | OKLA7A | EQ | West | YES | -0.02434 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.029973 | 0 | 0 |  |  | 0 | 0 | -0.029973 | 0 |  |  |  |  | 0 | 0
6752 | OKLA0A | 1 | West | YES | -0.02434 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.029973 | 0 | 649.7 |  |  | 0 | 0 | -0.029973 | 0 |  |  |  |  | 0 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.013289 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 |  |  |  |  | 0 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.013289 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 |  |  | Weighted Shift Factors |  | 0 | 0
88253 | HAMILTON | F | South | YES | -0.013289 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.035301 | 0 | 0 |  |  |  |  | 0.035301 | 0 |  |  | North | 0.0056325 | 0 | 0
8262 | ELPS | 1 | South | YES | -0.009524 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.039066 | 0 | 0 |  |  |  |  | 0.039066 | 0 |  |  | West | -0.04859 | 0 | 0
11056 | ROSCOE_1G | 1 | West | YES | -0.038521 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.044154 | 0 | 209 |  |  | 0 | 0 | -0.044154 | 0 |  |  |  |  | 0 | 0
11057 | CHAMPION_1G | 1 | West | YES | -0.038521 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.044154 | 0 | 126.5 |  |  | 0 | 0 | -0.044154 | 0 | West |  |  |  | 0 | 0
11058 | PYRON_1G | 1 | West | YES | -0.038521 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.044154 | 0 | 249 |  |  | 0 | 0 | -0.044154 | 0 | Line Rating |  | 186 |  | 0 | 0
11059 | INADALE_1G | 1 | West | YES | -0.038521 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.044154 | 0 | 197 |  |  | 0 | 0 | -0.044154 | 0 | Impact Counter to Zone: |  | 0 |  | 0 | 0
60202 | FRNDDRCS | F | West | YES | -0.038909 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.044542 | 0 | 0 |  |  | 0 | 0 | -0.044542 | 0 |  |  | 0% |  | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.002087 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.046503 | 0 | 0 |  |  |  |  | 0.046503 | 0 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | North |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | Line Rating |  | 186 |  | 0 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 | Impact Counter to Zone: |  | 0 |  | 0 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  | 0% |  | 0 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.001717 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.046873 | 8.4 | 8.4 |  |  |  |  | 0.046873 | 0.39374 |  |  |  |  | 0 | 0
80265 | LARECU40A | 4 | South | YES | -0.001313 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.047277 | 100 | 100 |  |  |  |  | 0.047277 | 4.7277 |  |  |  |  | 0 | 0
80266 | LARECU50A | 5 | South | YES | -0.001313 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.047277 | 100 | 100 |  |  |  |  | 0.047277 | 4.7277 |  |  |  |  | 0 | 0
80012 | LAR | F | South | YES | -0.001312 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.047278 | 0 | 0 |  |  |  |  | 0.047278 | 0 |  |  |  |  | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.001264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 |  |  |  |  | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.001264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 |  |  |  |  | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.001264 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.047326 | 0 | 0 |  |  |  |  | 0.047326 | 0 |  |  |  |  | 0 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.001217 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.047373 | 423.3 | 423.3 |  |  |  |  | 0.047373 | 20.0531 |  |  |  |  | 0 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.001202 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.047388 | 23.9 | 23.9 |  |  |  |  | 0.047388 | 1.1326 |  |  |  |  | 0 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.001202 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.047388 | 24 | 24 |  |  |  |  | 0.047388 | 1.1373 |  |  |  |  | 0 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.001202 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.047388 | 24.3 | 24.3 |  |  |  |  | 0.047388 | 1.1515 |  |  |  |  | 0 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.001081 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.047509 | 0 | 0 |  |  |  |  | 0.047509 | 0 |  |  |  |  | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.001081 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.047509 | 0 | 0 |  |  |  |  | 0.047509 | 0 |  |  |  |  | 0 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.000655 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047935 | 0 | 0 |  |  |  |  | 0.047935 | 0 |  |  |  |  | 0 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.000655 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.047935 | 0 | 0 |  |  |  |  | 0.047935 | 0 |  |  |  |  | 0 | 0
88299 | ZAPATA | F | South | YES | -0.000513 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.048077 | 0 | 0 |  |  |  |  | 0.048077 | 0 |  |  |  |  | 0 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.042803 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.048436 | 0 | 112.5 |  |  | 0 | 0 | -0.048436 | 0 |  |  |  |  | 0 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.042803 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 149.5 |  |  | 0 | 0 | -0.048436 | 0 |  |  |  |  | 0 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.042803 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 186 |  |  | 0 | 0 | -0.048436 | 0 |  |  |  |  | 0 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.042803 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.048436 | 0 | 214.5 |  |  | 0 | 0 | -0.048436 | 0 |  |  |  |  | 0 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.04859 | 0 | 0 |  |  |  |  | 0.04859 | 0 |  |  |  |  | 0 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.04859 | 15 | 15 |  |  |  |  | 0.04859 | 0.72885 |  |  |  |  | 0 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | 2.9e-05 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 |  |  |  |  | 0 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 2.9e-05 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 |  |  |  |  | 0 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 2.9e-05 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.048619 | 0 | 0 |  |  |  |  | 0.048619 | 0 |  |  |  |  | 0 | 0
88508 | FALFURRI | F | South | YES | 0.000116 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.048706 | 0 | 0 |  |  |  |  | 0.048706 | 0 |  |  |  |  | 0 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | -0.043314 | 30 | 0 | 150 |  | 1.02 | Wind | -1 | 0.048947 | 0 | 150 |  |  | 0 | 0 | -0.048947 | 0 |  |  |  |  | 0 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | 0.000461 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.049051 | 43 | 43 |  |  |  |  | 0.049051 | 2.1092 |  |  |  |  | 0 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | 0.000461 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.049051 | 44 | 44 |  |  |  |  | 0.049051 | 2.1583 |  |  |  |  | 0 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | 0.000461 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.049051 | 44 | 44 |  |  |  |  | 0.049051 | 2.1583 |  |  |  |  | 0 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | 0.000461 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.049051 | 45 | 45 |  |  |  |  | 0.049051 | 2.2073 |  |  |  |  | 0 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | 0.000461 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.049051 | 58 | 58 |  |  |  |  | 0.049051 | 2.845 |  |  |  |  | 0 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | 0.000461 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.049051 | 89 | 89 |  |  |  |  | 0.049051 | 4.3656 |  |  |  |  | 0 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.000506 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 |  |  |  |  | 0 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.000506 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 |  |  |  |  | 0 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.000506 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.049096 | 0 | 0 |  |  |  |  | 0.049096 | 0 |  |  |  |  | 0 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.00055 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.04914 | 407 | 407 |  |  |  |  | 0.04914 | 20.0001 |  |  |  |  | 0 | 0
60000 | DSKY2 | 1 | West | YES | -0.043529 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.049162 | 0 | 76.5 |  |  | 0 | 0 | -0.049162 | 0 |  |  |  |  | 0 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.000577 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.049167 | 215 | 215 |  |  |  |  | 0.049167 | 10.571 |  |  |  |  | 0 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.000577 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.049167 | 216 | 216 |  |  |  |  | 0.049167 | 10.6201 |  |  |  |  | 0 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | 0.000579 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.049169 | 400 | 400 |  |  |  |  | 0.049169 | 19.6677 |  |  |  |  | 0 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | 0.000579 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.049169 | 418 | 418 |  |  |  |  | 0.049169 | 20.5527 |  |  |  |  | 0 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | 0.000595 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.049185 | 0 | 430 |  |  |  |  | 0.049185 | 21.1496 |  |  |  |  | 0 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | 0.000595 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.049185 | 0 | 430 |  |  |  |  | 0.049185 | 21.1496 |  |  |  |  | 0 | 0
8933 | FGNTS001 | 1 | South | YES | 0.000596 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.049186 | 146.5 | 146.5 |  |  |  |  | 0.049186 | 7.2058 |  |  |  |  | 0 | 0
8934 | FGNTS101 | 2 | South | YES | 0.000596 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.049186 | 147.9 | 147.9 |  |  |  |  | 0.049186 | 7.2746 |  |  |  |  | 0 | 0
8935 | FGNTS201 | 3 | South | YES | 0.000596 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.049186 | 173 | 173 |  |  |  |  | 0.049186 | 8.5092 |  |  |  |  | 0 | 0
88198 | BEEVILLE | F | South | YES | 0.000599 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.049189 | 0 | 0 |  |  |  |  | 0.049189 | 0 |  |  |  |  | 0 | 0
60018 | DSKY1 | 1 | West | YES | -0.043565 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.049198 | 0 | 84 |  |  | 0 | 0 | -0.049198 | 0 |  |  |  |  | 0 | 0
5903 | SANMIGUELGEN | 1 | South | YES | 0.000649 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.049239 | 0 | 396.3 |  |  |  |  | 0.049239 | 19.5135 |  |  |  |  | 0 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.000654 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.049244 | 61 | 61 |  |  |  |  | 0.049244 | 3.0039 |  |  |  |  | 0 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.000654 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.049244 | 95 | 95 |  |  |  |  | 0.049244 | 4.6782 |  |  |  |  | 0 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.000654 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.049244 | 151 | 151 |  |  |  |  | 0.049244 | 7.4359 |  |  |  |  | 0 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.000676 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.049266 | 155 | 155 |  |  |  |  | 0.049266 | 7.6363 |  |  |  |  | 0 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.000676 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.049266 | 155 | 155 |  |  |  |  | 0.049266 | 7.6363 |  |  |  |  | 0 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | 0.000676 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.049266 | 174 | 174 |  |  |  |  | 0.049266 | 8.5723 |  |  |  |  | 0 | 0
8982 | HECN2 | 2 | South | YES | 0.000691 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.049281 | 144.1 | 144.1 |  |  |  |  | 0.049281 | 7.1014 |  |  |  |  | 0 | 0
8981 | HECN1 | 1 | South | YES | 0.000691 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.049281 | 144.8 | 144.8 |  |  |  |  | 0.049281 | 7.1359 |  |  |  |  | 0 | 0
8983 | HECN3 | 3 | South | YES | 0.000691 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.049281 | 171.9 | 171.9 |  |  |  |  | 0.049281 | 8.4714 |  |  |  |  | 0 | 0
8936 | MVGN#1 | 1 | South | YES | 0.000692 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.049282 | 216.6 | 216.6 |  |  |  |  | 0.049282 | 10.6745 |  |  |  |  | 0 | 0
8937 | MVGN#2 | 2 | South | YES | 0.000692 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.049282 | 216.7 | 216.7 |  |  |  |  | 0.049282 | 10.6795 |  |  |  |  | 0 | 0
8938 | MVGN#3 | 3 | South | YES | 0.000692 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.049282 | 250.9 | 250.9 |  |  |  |  | 0.049282 | 12.3649 |  |  |  |  | 0 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | 0.000705 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.049295 | 0 | 562 |  |  |  |  | 0.049295 | 27.7039 |  |  |  |  | 0 | 0
80003 | MILHWYS | F | South | YES | 0.000732 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.049322 | 0 | 0 |  |  |  |  | 0.049322 | 0 |  |  |  |  | 0 | 0
5933 | SI_RAY6 | 6 | South | YES | 0.000732 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.049322 | 19.3 | 19.3 |  |  |  |  | 0.049322 | 0.95192 |  |  |  |  | 0 | 0
5932 | SI_RAY9 | 9 | South | YES | 0.000732 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.049322 | 38 | 38 |  |  |  |  | 0.049322 | 1.8742 |  |  |  |  | 0 | 0
5935 | SI_RAY10 | 10 | South | YES | 0.000732 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.049322 | 47 | 47 |  |  |  |  | 0.049322 | 2.3181 |  |  |  |  | 0 | 0
8517 | CELANEBI0A | 1 | South | YES | 0.000754 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.049344 | 0 | 0 |  |  |  |  | 0.049344 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 4 | South | YES | 0.000757 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 19 |  |  |  |  | 0.049347 | 0.9376 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 4 | South | YES | 0.000757 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 22 |  |  |  |  | 0.049347 | 1.0856 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 2 | South | YES | 0.000757 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 36 |  |  |  |  | 0.049347 | 1.7765 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 3 | South | YES | 0.000757 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 38 |  |  |  |  | 0.049347 | 1.8752 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 2 | South | YES | 0.000757 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 41 |  |  |  |  | 0.049347 | 2.0232 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 3 | South | YES | 0.000757 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 43 |  |  |  |  | 0.049347 | 2.1219 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 2 | South | YES | 0.000757 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 50 |  |  |  |  | 0.049347 | 2.4674 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 2 | South | YES | 0.000757 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 50 |  |  |  |  | 0.049347 | 2.4674 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 1 | South | YES | 0.000757 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 55 |  |  |  |  | 0.049347 | 2.7141 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 1 | South | YES | 0.000757 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 94 |  |  |  |  | 0.049347 | 4.6386 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 1 | South | YES | 0.000757 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 94 |  |  |  |  | 0.049347 | 4.6386 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 1 | South | YES | 0.000757 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.049347 | 0 | 148 |  |  |  |  | 0.049347 | 7.3034 |  |  |  |  | 0 | 0
8461 | KOCH_UP0A | 1 | South | YES | 0.000774 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.049364 | 0 | 0 |  |  |  |  | 0.049364 | 0 |  |  |  |  | 0 | 0
8506 | VAL #1 | 1 | South | YES | 0.00078 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 |  |  |  |  | 0 | 0
8507 | VAL #2 | 2 | South | YES | 0.00078 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 |  |  |  |  | 0 | 0
8511 | OXY_CC0A | 1 | South | YES | 0.00078 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.04937 | 0 | 0 |  |  |  |  | 0.04937 | 0 |  |  |  |  | 0 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.000788 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.049378 | 0 | 0 |  |  |  |  | 0.049378 | 0 |  |  |  |  | 0 | 0
8459 | B_DAVIS0B | MB | South | YES | 0.00079 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.04938 | 0 | 0 |  |  |  |  | 0.04938 | 0 |  |  |  |  | 0 | 0
8460 | B_DAVIS0A | MB | South | YES | 0.00079 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.04938 | 0 | 0 |  |  |  |  | 0.04938 | 0 |  |  |  |  | 0 | 0
80263 | B_DAVIS31A | 3 | South | YES | 0.00079 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.04938 | 180 | 180 |  |  |  |  | 0.04938 | 8.8884 |  |  |  |  | 0 | 0
80264 | B_DAVIS41A | 4 | South | YES | 0.00079 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.04938 | 180 | 180 |  |  |  |  | 0.04938 | 8.8884 |  |  |  |  | 0 | 0
8456 | COSW#1 | 1 | South | YES | 0.000793 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.049383 | 0 | 0 |  |  |  |  | 0.049383 | 0 |  |  |  |  | 0 | 0
8457 | COSW#2 | 2 | South | YES | 0.000793 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.049383 | 0 | 0 |  |  |  |  | 0.049383 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | MB | South | YES | 0.000796 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 |  |  |  |  | 0 | 0
8560 | CNOPGT1 | 1 | South | YES | 0.000796 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 |  |  |  |  | 0 | 0
8561 | CNOPGT2 | 2 | South | YES | 0.000796 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 |  |  |  |  | 0 | 0
8562 | CNOPST1 | 3 | South | YES | 0.000796 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.049386 | 0 | 0 |  |  |  |  | 0.049386 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | 7 | South | YES | 0.000796 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.049386 | 367 | 367 |  |  |  |  | 0.049386 | 18.1247 |  |  |  |  | 0 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.000816 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.049406 | 0 | 0 |  |  |  |  | 0.049406 | 0 |  |  |  |  | 0 | 0
8926 | LGE_GT10A | 1 | South | YES | 0.000843 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 |  |  |  |  | 0 | 0
8927 | LGE_GT20A | 2 | South | YES | 0.000843 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 |  |  |  |  | 0 | 0
8928 | LGE_STG0A | 3 | South | YES | 0.000843 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 |  |  |  |  | 0 | 0
8930 | ICPGN10A | 1 | South | YES | 0.000843 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 |  |  |  |  | 0 | 0
8931 | ICPGN20A | 2 | South | YES | 0.000843 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 |  |  |  |  | 0 | 0
8932 | ICPGN30A | 3 | South | YES | 0.000843 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 |  |  |  |  | 0 | 0
80223 | REYSHR G | 1 | South | YES | 0.000843 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.049433 | 0 | 0 |  |  |  |  | 0.049433 | 0 |  |  |  |  | 0 | 0
8161 | COLETO0A | 1 | South | YES | 0.000851 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.049441 | 0 | 633 |  |  |  |  | 0.049441 | 31.2963 |  |  |  |  | 0 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.000868 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.049458 | 138 | 138 |  |  |  |  | 0.049458 | 6.8252 |  |  |  |  | 0 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.000868 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.049458 | 146 | 146 |  |  |  |  | 0.049458 | 7.2209 |  |  |  |  | 0 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.000868 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.049458 | 147 | 147 |  |  |  |  | 0.049458 | 7.2704 |  |  |  |  | 0 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.000868 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.049458 | 149 | 149 |  |  |  |  | 0.049458 | 7.3693 |  |  |  |  | 0 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.000868 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.049458 | 182 | 182 |  |  |  |  | 0.049458 | 9.0014 |  |  |  |  | 0 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.000868 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.049458 | 203 | 203 |  |  |  |  | 0.049458 | 10.04 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.000882 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.000882 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.000882 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.049472 | 0 | 0 |  |  |  |  | 0.049472 | 0 |  |  |  |  | 0 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.000914 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.049504 | 148 | 148 |  |  |  |  | 0.049504 | 7.3266 |  |  |  |  | 0 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.000914 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.049504 | 148 | 148 |  |  |  |  | 0.049504 | 7.3266 |  |  |  |  | 0 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.000914 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.049504 | 154 | 154 |  |  |  |  | 0.049504 | 7.6237 |  |  |  |  | 0 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.000914 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.049504 | 293 | 293 |  |  |  |  | 0.049504 | 14.5047 |  |  |  |  | 0 | 0
60017 | ORNNWP1 | 1 | West | YES | -0.043874 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.049507 | 0 | 80 |  |  | 0 | 0 | -0.049507 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.000944 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.049534 | 0 | 0 |  |  |  |  | 0.049534 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.000944 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.049534 | 0 | 0 |  |  |  |  | 0.049534 | 0 |  |  |  |  | 0 | 0
8189 | CUECPL2A | 1 | South | YES | 0.000953 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.049543 | 0 | 0 |  |  |  |  | 0.049543 | 0 |  |  |  |  | 0 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.00096 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.04955 | 223.9 | 223.9 |  |  |  |  | 0.04955 | 11.0943 |  |  |  |  | 0 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.00096 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.04955 | 224.6 | 224.6 |  |  |  |  | 0.04955 | 11.129 |  |  |  |  | 0 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.00096 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.04955 | 225 | 225 |  |  |  |  | 0.04955 | 11.1488 |  |  |  |  | 0 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.00096 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.04955 | 226.7 | 226.7 |  |  |  |  | 0.04955 | 11.233 |  |  |  |  | 0 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | 0.000967 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.049557 | 11 | 11 |  |  |  |  | 0.049557 | 0.54513 |  |  |  |  | 0 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | 0.000967 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.049557 | 11 | 11 |  |  |  |  | 0.049557 | 0.54513 |  |  |  |  | 0 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | 0.000967 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.049557 | 22 | 22 |  |  |  |  | 0.049557 | 1.0903 |  |  |  |  | 0 | 0
5509 | RAYBURNCC10 | 1 | South | YES | 0.001006 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.049596 | 37.3 | 37.3 |  |  |  |  | 0.049596 | 1.8499 |  |  |  |  | 0 | 0
5511 | RAYBURNCC7 | 1 | South | YES | 0.001006 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.049596 | 47.5 | 47.5 |  |  |  |  | 0.049596 | 2.3558 |  |  |  |  | 0 | 0
5508 | RAYBURNCC9 | 1 | South | YES | 0.001006 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.049596 | 47.7 | 47.7 |  |  |  |  | 0.049596 | 2.3657 |  |  |  |  | 0 | 0
5512 | RAYBURNCC8 | 1 | South | YES | 0.001006 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.049596 | 49.3 | 49.3 |  |  |  |  | 0.049596 | 2.4451 |  |  |  |  | 0 | 0
8173 | VICEC51A | 5 | South | YES | 0.001014 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.049604 | 144 | 144 |  |  |  |  | 0.049604 | 7.143 |  |  |  |  | 0 | 0
8174 | VICEC61A | 6 | South | YES | 0.001014 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.049604 | 188 | 188 |  |  |  |  | 0.049604 | 9.3256 |  |  |  |  | 0 | 0
8066 | DUP1V#1 | 1 | South | YES | 0.001033 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.049623 | 0 | 0 |  |  |  |  | 0.049623 | 0 |  |  |  |  | 0 | 0
80224 | VISTRONG1 | 1 | South | YES | 0.001057 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.049647 | 0 | 0 |  |  |  |  | 0.049647 | 0 |  |  |  |  | 0 | 0
80225 | VISTRONG2 | 2 | South | YES | 0.001057 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.049647 | 0 | 0 |  |  |  |  | 0.049647 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.00106 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.04965 | 0 | 0 |  |  |  |  | 0.04965 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.00106 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.04965 | 0 | 0 |  |  |  |  | 0.04965 | 0 |  |  |  |  | 0 | 0
80227 | AIRCO G | 1 | South | YES | 0.001061 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.049651 | 0 | 0 |  |  |  |  | 0.049651 | 0 |  |  |  |  | 0 | 0
8147 | UCAR #2 | 10 | South | YES | 0.001077 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 |  |  |  |  | 0 | 0
8148 | UCAR #1 | 2 | South | YES | 0.001077 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 9 | South | YES | 0.001077 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 8 | South | YES | 0.001077 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 |  |  |  |  | 0 | 0
80138 | CSDR7 | 7 | South | YES | 0.001077 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 6 | South | YES | 0.001077 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 5 | South | YES | 0.001077 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 |  |  |  |  | 0 | 0
80140 | CSDR11 | 11 | South | YES | 0.001077 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.049667 | 0 | 0 |  |  |  |  | 0.049667 | 0 |  |  |  |  | 0 | 0
9017 | SANDH_G2 | 2 | South | YES | 0.001118 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.049708 | 46 | 46 |  |  |  |  | 0.049708 | 2.2866 |  |  |  |  | 0 | 0
9018 | SANDH_G3 | 3 | South | YES | 0.001118 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.049708 | 46 | 46 |  |  |  |  | 0.049708 | 2.2866 |  |  |  |  | 0 | 0
9019 | SANDH_G4 | 4 | South | YES | 0.001118 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.049708 | 47 | 47 |  |  |  |  | 0.049708 | 2.3363 |  |  |  |  | 0 | 0
9016 | SANDH_G1 | 1 | South | YES | 0.001118 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.049708 | 49 | 49 |  |  |  |  | 0.049708 | 2.4357 |  |  |  |  | 0 | 0
9021 | SANDHG5C | 5C | South | YES | 0.001118 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.049708 | 148 | 148 |  |  |  |  | 0.049708 | 7.3568 |  |  |  |  | 0 | 0
9020 | SANDHG5A | 5A | South | YES | 0.001118 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.049708 | 155 | 155 |  |  |  |  | 0.049708 | 7.7048 |  |  |  |  | 0 | 0
9000 | DECKR_G1 | 1 | South | YES | 0.00112 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.04971 | 321 | 321 |  |  |  |  | 0.04971 | 15.957 |  |  |  |  | 0 | 0
9001 | DECKR_G2 | 2 | South | YES | 0.00112 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.04971 | 426 | 426 |  |  |  |  | 0.04971 | 21.1766 |  |  |  |  | 0 | 0
80226 | ALCOA G | 1 | South | YES | 0.001152 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.049742 | 0 | 0 |  |  |  |  | 0.049742 | 0 |  |  |  |  | 0 | 0
9002 | DECKR_G3 | 3 | South | YES | 0.001161 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.049751 | 42 | 42 |  |  |  |  | 0.049751 | 2.0896 |  |  |  |  | 0 | 0
9003 | DECKR_G4 | 4 | South | YES | 0.001161 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.049751 | 44 | 44 |  |  |  |  | 0.049751 | 2.1891 |  |  |  |  | 0 | 0
9004 | DECKR_G5 | 5 | South | YES | 0.001161 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.049751 | 44 | 44 |  |  |  |  | 0.049751 | 2.1891 |  |  |  |  | 0 | 0
9005 | DECKR_G6 | 6 | South | YES | 0.001161 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.049751 | 47 | 47 |  |  |  |  | 0.049751 | 2.3383 |  |  |  |  | 0 | 0
8134 | FOR #1 | 1 | South | YES | 0.001172 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
8138 | FOR #2 | 2 | South | YES | 0.001172 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
8153 | FOR #3 | 3 | South | YES | 0.001172 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
8154 | FOR #4 | 4 | South | YES | 0.001172 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
8155 | FOR #5 | 5 | South | YES | 0.001172 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
8156 | FOR #6 | 6 | South | YES | 0.001172 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
8157 | FOR #7 | 7 | South | YES | 0.001172 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
80051 | FOR #8 | 8 | South | YES | 0.001172 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
80052 | FOR #9 | 9 | South | YES | 0.001172 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
80053 | FOR #10 | 10 | South | YES | 0.001172 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.049762 | 0 | 0 |  |  |  |  | 0.049762 | 0 |  |  |  |  | 0 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.001262 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.049852 | 132 | 132 |  |  |  |  | 0.049852 | 6.5805 |  |  |  |  | 0 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.001262 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.049852 | 139 | 139 |  |  |  |  | 0.049852 | 6.9295 |  |  |  |  | 0 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.001262 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.049852 | 329 | 329 |  |  |  |  | 0.049852 | 16.4014 |  |  |  |  | 0 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.001364 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.049954 | 149.5 | 149.5 |  |  |  |  | 0.049954 | 7.4682 |  |  |  |  | 0 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.001364 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.049954 | 152.5 | 152.5 |  |  |  |  | 0.049954 | 7.618 |  |  |  |  | 0 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.001364 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.049954 | 232.6 | 232.6 |  |  |  |  | 0.049954 | 11.6194 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.001373 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.049963 | 50 | 50 |  |  |  |  | 0.049963 | 2.4982 |  |  |  |  | 0 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.001467 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.050057 | 158 | 158 |  |  |  |  | 0.050057 | 7.909 |  |  |  |  | 0 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.001467 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.050057 | 160 | 160 |  |  |  |  | 0.050057 | 8.0092 |  |  |  |  | 0 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.001467 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.050057 | 175 | 175 |  |  |  |  | 0.050057 | 8.76 |  |  |  |  | 0 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.001468 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 436 |  |  |  |  | 0.050058 | 21.8254 |  |  |  |  | 0 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.001468 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 598 |  |  |  |  | 0.050058 | 29.9348 |  |  |  |  | 0 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.001468 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.050058 | 0 | 606 |  |  |  |  | 0.050058 | 30.3353 |  |  |  |  | 0 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.001827 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.050417 | 0 | 580 |  |  |  |  | 0.050417 | 29.242 |  |  |  |  | 0 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | -0.044788 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.050421 | 0 | 150 |  |  | 0 | 0 | -0.050421 | 0 |  |  |  |  | 0 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | 0.001843 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.050433 | 0 | 0 |  |  |  |  | 0.050433 | 0 |  |  |  |  | 0 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | 0.001843 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.050433 | 0 | 0 |  |  |  |  | 0.050433 | 0 |  |  |  |  | 0 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.044816 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.050449 | 0 | 80 |  |  | 0 | 0 | -0.050449 | 0 |  |  |  |  | 0 | 0
60016 | WOODWRD11A | 1 | West | YES | -0.044823 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.050456 | 0 | 80 |  |  | 0 | 0 | -0.050456 | 0 |  |  |  |  | 0 | 0
48731 | CBE_GT1 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 |  |  |  |  | 0 | 0
48732 | CBE_GT2 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 |  |  |  |  | 0 | 0
48734 | CBE_GT3 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 |  |  |  |  | 0 | 0
48735 | CBE_GT4 | 1 | Houston | YES | 0.001871 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.050461 | 76 | 76 |  |  |  |  | 0.050461 | 3.8351 |  |  |  |  | 0 | 0
48733 | CBE_ST12 | 1 | Houston | YES | 0.001871 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.050461 | 105 | 105 |  |  |  |  | 0.050461 | 5.2984 |  |  |  |  | 0 | 0
48736 | CBE_ST34 | 1 | Houston | YES | 0.001871 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.050461 | 105 | 105 |  |  |  |  | 0.050461 | 5.2984 |  |  |  |  | 0 | 0
6016 | SWMESA | 1 | West | YES | -0.04485 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.050483 | 0 | 75 |  |  | 0 | 0 | -0.050483 | 0 |  |  |  |  | 0 | 0
60003 | KING_NE1A | 1 | West | YES | -0.04485 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050483 | 0 | 80 |  |  | 0 | 0 | -0.050483 | 0 |  |  |  |  | 0 | 0
60005 | KING_SE1A | 1 | West | YES | -0.04485 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.050483 | 0 | 40 |  |  | 0 | 0 | -0.050483 | 0 |  |  |  |  | 0 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.001897 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.050487 | 0 | 0 |  |  |  |  | 0.050487 | 0 |  |  |  |  | 0 | 0
60201 | RIO DRCS | F | West | YES | -0.044909 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.050542 | 0 | 0 |  |  | 0 | 0 | -0.050542 | 0 |  |  |  |  | 0 | 0
60007 | KING_SW1A | 1 | West | YES | -0.045015 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050648 | 0 | 80 |  |  | 0 | 0 | -0.050648 | 0 |  |  |  |  | 0 | 0
60019 | KING_NW1A | 1 | West | YES | -0.045015 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.050648 | 0 | 80 |  |  | 0 | 0 | -0.050648 | 0 |  |  |  |  | 0 | 0
49851 | DOW17000 | 37 | Houston | YES | 0.002065 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49858 | DOW38100 | 31 | Houston | YES | 0.002065 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49859 | DOW38200 | 33 | Houston | YES | 0.002065 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49860 | DOW38300 | 32 | Houston | YES | 0.002065 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49862 | DOW39100 | 36 | Houston | YES | 0.002065 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49863 | DOW39200 | 35 | Houston | YES | 0.002065 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49865 | DOW41000 | 41 | Houston | YES | 0.002065 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49866 | DOW42000 | 42 | Houston | YES | 0.002065 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49869 | DOW49000 | 45 | Houston | YES | 0.002065 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49870 | DOW61000 | 61 | Houston | YES | 0.002065 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49871 | DOW62000 | 62 | Houston | YES | 0.002065 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49872 | DOW63000 | 63 | Houston | YES | 0.002065 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49873 | DOW64000 | 64 | Houston | YES | 0.002065 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49876 | DOW65000 | 65 | Houston | YES | 0.002065 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49877 | DOW66000 | 66 | Houston | YES | 0.002065 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49878 | DOW67000 | 67 | Houston | YES | 0.002065 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49882 | DOW81000 | 81 | Houston | YES | 0.002065 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49884 | DOW82000 | 82 | Houston | YES | 0.002065 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49885 | DOW83000 | 83 | Houston | YES | 0.002065 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
49886 | DOW84000 | 84 | Houston | YES | 0.002065 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.050655 | 0 | 0 |  |  |  |  | 0.050655 | 0 |  |  |  |  | 0 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.002098 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.050688 | 0 | 581 |  |  |  |  | 0.050688 | 29.4499 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.002105 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.050695 | 0 | 0 |  |  |  |  | 0.050695 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.002105 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.050695 | 0 | 0 |  |  |  |  | 0.050695 | 0 |  |  |  |  | 0 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.002139 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 |  |  |  |  | 0 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.002139 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 |  |  |  |  | 0 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.002139 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 |  |  |  |  | 0 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.002139 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.050729 | 0 | 0 |  |  |  |  | 0.050729 | 0 |  |  |  |  | 0 | 0
48730 | MNS_GT | 1 | Houston | YES | 0.002251 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.050841 | 0 | 0 |  |  |  |  | 0.050841 | 0 |  |  |  |  | 0 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.002259 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 564 |  |  |  |  | 0.050849 | 28.679 |  |  |  |  | 0 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.002259 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 603 |  |  |  |  | 0.050849 | 30.6621 |  |  |  |  | 0 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.002259 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.050849 | 0 | 651 |  |  |  |  | 0.050849 | 33.1028 |  |  |  |  | 0 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.00226 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.05085 | 166.4 | 166.4 |  |  |  |  | 0.05085 | 8.4615 |  |  |  |  | 0 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.00226 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.05085 | 167.7 | 167.7 |  |  |  |  | 0.05085 | 8.5276 |  |  |  |  | 0 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.00226 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.05085 | 252.4 | 252.4 |  |  |  |  | 0.05085 | 12.8346 |  |  |  |  | 0 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.002268 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.050858 | 0 | 0 |  |  |  |  | 0.050858 | 0 |  |  |  |  | 0 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.002281 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.050871 | 13 | 13 |  |  |  |  | 0.050871 | 0.66133 |  |  |  |  | 0 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.002281 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.050871 | 166 | 166 |  |  |  |  | 0.050871 | 8.4446 |  |  |  |  | 0 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.002281 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.050871 | 166 | 166 |  |  |  |  | 0.050871 | 8.4446 |  |  |  |  | 0 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.002281 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.050871 | 248 | 248 |  |  |  |  | 0.050871 | 12.6161 |  |  |  |  | 0 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.002281 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.050871 | 546 | 546 |  |  |  |  | 0.050871 | 27.7757 |  |  |  |  | 0 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.002281 | 618.1 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.050871 | 0 | 654 |  |  |  |  | 0.050871 | 33.2698 |  |  |  |  | 0 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.002342 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.002342 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.002342 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.002342 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.002342 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.002342 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.002342 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.002342 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.002342 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.002342 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.002342 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.002342 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.002342 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.002342 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.002342 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.050932 | 0 | 0 |  |  |  |  | 0.050932 | 0 |  |  |  |  | 0 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | 0.002372 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.050962 | 0 | 0 |  |  |  |  | 0.050962 | 0 |  |  |  |  | 0 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.002393 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 |  |  |  |  | 0 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.002393 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 |  |  |  |  | 0 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.002393 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 |  |  |  |  | 0 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.002393 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 |  |  |  |  | 0 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.002393 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.050983 | 0 | 0 |  |  |  |  | 0.050983 | 0 |  |  |  |  | 0 | 0
60058 | BUFF_GAP1A | 1 | West | YES | -0.045356 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.050989 | 0 | 120 |  |  | 0 | 0 | -0.050989 | 0 |  |  |  |  | 0 | 0
60060 | CIRELLO | 1 | West | YES | -0.045356 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.050989 | 0 | 233 |  |  | 0 | 0 | -0.050989 | 0 |  |  |  |  | 0 | 0
60063 | BUFF_GAP1B | 1 | West | YES | -0.045356 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.050989 | 0 | 170.2 |  |  | 0 | 0 | -0.050989 | 0 |  |  |  |  | 0 | 0
60066 | H_HOLLOW1A | 1 | West | YES | -0.045356 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.050989 | 0 | 222 |  |  | 0 | 0 | -0.050989 | 0 |  |  |  |  | 0 | 0
60068 | HHOLLOW21A | 1 | West | YES | -0.045356 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 184 |  |  | 0 | 0 | -0.050989 | 0 |  |  |  |  | 0 | 0
60070 | HHOLLOW31A | 1 | West | YES | -0.045356 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 224 |  |  | 0 | 0 | -0.050989 | 0 |  |  |  |  | 0 | 0
60072 | HHOLLOW41A | 1 | West | YES | -0.045356 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.050989 | 0 | 115 |  |  | 0 | 0 | -0.050989 | 0 |  |  |  |  | 0 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.0024 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 |  |  |  |  | 0 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.0024 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 |  |  |  |  | 0 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.0024 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 |  |  |  |  | 0 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.0024 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.05099 | 0 | 0 |  |  |  |  | 0.05099 | 0 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | B | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | A | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | C | Houston | YES | 0.002413 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.051003 | 47 | 47 |  |  |  |  | 0.051003 | 2.3972 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | F | Houston | YES | 0.002413 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.051003 | 54 | 54 |  |  |  |  | 0.051003 | 2.7542 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | D | Houston | YES | 0.002413 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.051003 | 55 | 55 |  |  |  |  | 0.051003 | 2.8052 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | E | Houston | YES | 0.002413 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.051003 | 57 | 57 |  |  |  |  | 0.051003 | 2.9072 |  |  |  |  | 0 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.002415 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.051005 | 0 | 0 |  |  |  |  | 0.051005 | 0 |  |  |  |  | 0 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.002415 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.051005 | 0 | 0 |  |  |  |  | 0.051005 | 0 |  |  |  |  | 0 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.002418 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.051008 | 157 | 157 |  |  |  |  | 0.051008 | 8.0083 |  |  |  |  | 0 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.002418 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.051008 | 157.1 | 157.1 |  |  |  |  | 0.051008 | 8.0134 |  |  |  |  | 0 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.002418 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.051008 | 157.5 | 157.5 |  |  |  |  | 0.051008 | 8.0338 |  |  |  |  | 0 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.002418 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.051008 | 163.2 | 163.2 |  |  |  |  | 0.051008 | 8.3245 |  |  |  |  | 0 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.002418 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.051008 | 282 | 282 |  |  |  |  | 0.051008 | 14.3843 |  |  |  |  | 0 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.002423 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.051013 | 0 | 0 |  |  |  |  | 0.051013 | 0 |  |  |  |  | 0 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.002427 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.051017 | 0 | 0 |  |  |  |  | 0.051017 | 0 |  |  |  |  | 0 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.002427 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.051017 | 0 | 0 |  |  |  |  | 0.051017 | 0 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | 0.002427 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.051017 | 12 | 12 |  |  |  |  | 0.051017 | 0.61221 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | 0.002427 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.051017 | 18 | 18 |  |  |  |  | 0.051017 | 0.91831 |  |  |  |  | 0 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.002427 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.051017 | 165 | 165 |  |  |  |  | 0.051017 | 8.4178 |  |  |  |  | 0 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.002427 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.051017 | 176 | 176 |  |  |  |  | 0.051017 | 8.979 |  |  |  |  | 0 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.002428 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 |  |  |  |  | 0 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.002428 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 |  |  |  |  | 0 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.002428 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 |  |  |  |  | 0 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.002428 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 |  |  |  |  | 0 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.002428 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 |  |  |  |  | 0 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.002428 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 |  |  |  |  | 0 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.002428 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.051018 | 0 | 0 |  |  |  |  | 0.051018 | 0 |  |  |  |  | 0 | 0
48845 | SOL_GT1 | 1 | Houston | YES | 0.002428 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.051018 | 16.2 | 16.2 |  |  |  |  | 0.051018 | 0.8265 |  |  |  |  | 0 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.002428 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.051018 | 213 | 213 |  |  |  |  | 0.051018 | 10.8669 |  |  |  |  | 0 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.002428 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.051018 | 228 | 228 |  |  |  |  | 0.051018 | 11.6322 |  |  |  |  | 0 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.002433 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0 |  |  |  |  | 0 | 0
48821 | SHELLG2 | 2 | Houston | YES | 0.002433 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.002433 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.002433 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.051023 | 0 | 0 |  |  |  |  | 0.051023 | 0 |  |  |  |  | 0 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.002441 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.051031 | 0 | 0 |  |  |  |  | 0.051031 | 0 |  |  |  |  | 0 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.002442 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.051032 | 39 | 39 |  |  |  |  | 0.051032 | 1.9903 |  |  |  |  | 0 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.002442 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.051032 | 39 | 39 |  |  |  |  | 0.051032 | 1.9903 |  |  |  |  | 0 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.002442 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.051032 | 42 | 42 |  |  |  |  | 0.051032 | 2.1434 |  |  |  |  | 0 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.002442 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.051032 | 42 | 42 |  |  |  |  | 0.051032 | 2.1434 |  |  |  |  | 0 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.002444 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.051034 | 0 | 0 |  |  |  |  | 0.051034 | 0 |  |  |  |  | 0 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.002444 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.051034 | 0 | 0 |  |  |  |  | 0.051034 | 0 |  |  |  |  | 0 | 0
48875 | THW_3132 | B | Houston | YES | 0.002456 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.051046 | 53 | 53 |  |  |  |  | 0.051046 | 2.7054 |  |  |  |  | 0 | 0
48875 | THW_3132 | A | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075 |  |  |  |  | 0 | 0
48877 | THW_3334 | C | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075 |  |  |  |  | 0 | 0
48879 | THW_4142 | F | Houston | YES | 0.002456 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.051046 | 55 | 55 |  |  |  |  | 0.051046 | 2.8075 |  |  |  |  | 0 | 0
48879 | THW_4142 | E | Houston | YES | 0.002456 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.051046 | 56 | 56 |  |  |  |  | 0.051046 | 2.8586 |  |  |  |  | 0 | 0
48877 | THW_3334 | D | Houston | YES | 0.002456 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.051046 | 57 | 57 |  |  |  |  | 0.051046 | 2.9096 |  |  |  |  | 0 | 0
48881 | THW_4344 | G | Houston | YES | 0.002456 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.051046 | 58 | 58 |  |  |  |  | 0.051046 | 2.9607 |  |  |  |  | 0 | 0
48881 | THW_4344 | H | Houston | YES | 0.002456 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.051046 | 58 | 58 |  |  |  |  | 0.051046 | 2.9607 |  |  |  |  | 0 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.002456 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.051046 | 107 | 107 |  |  |  |  | 0.051046 | 5.4619 |  |  |  |  | 0 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.002456 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.051046 | 108 | 108 |  |  |  |  | 0.051046 | 5.513 |  |  |  |  | 0 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.002462 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.051052 | 746 | 746 |  |  |  |  | 0.051052 | 38.085 |  |  |  |  | 0 | 0
49803 | EXN_15GT | 1 | Houston | YES | 0.002468 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49804 | EXN_16GT | 2 | Houston | YES | 0.002468 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49805 | EXN_17GT | 3 | Houston | YES | 0.002468 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49826 | EXN938GT | 5 | Houston | YES | 0.002468 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49828 | EXN941GT | 10 | Houston | YES | 0.002468 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49829 | EXN942GT | 11 | Houston | YES | 0.002468 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49830 | EXN943GT | 12 | Houston | YES | 0.002468 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49831 | EXN944GT | 13 | Houston | YES | 0.002468 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49832 | EXN945GT | 9 | Houston | YES | 0.002468 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49837 | EXN_GT | 4 | Houston | YES | 0.002468 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
49838 | EXN_14GT | 14 | Houston | YES | 0.002468 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.051058 | 0 | 0 |  |  |  |  | 0.051058 | 0 |  |  |  |  | 0 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.002468 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.051058 | 12 | 12 |  |  |  |  | 0.051058 | 0.6127 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 1 | Houston | YES | 0.002473 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 2 | Houston | YES | 0.002473 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0 |  |  |  |  | 0 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.002473 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.051063 | 0 | 0 |  |  |  |  | 0.051063 | 0 |  |  |  |  | 0 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.002474 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 |  |  |  |  | 0 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.002474 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 |  |  |  |  | 0 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.002474 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 |  |  |  |  | 0 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.002474 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 |  |  |  |  | 0 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.002474 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 |  |  |  |  | 0 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.002474 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 |  |  |  |  | 0 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.002474 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.051064 | 0 | 0 |  |  |  |  | 0.051064 | 0 |  |  |  |  | 0 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.002474 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.051064 | 744 | 744 |  |  |  |  | 0.051064 | 37.9918 |  |  |  |  | 0 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.002477 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.051067 | 0 | 0 |  |  |  |  | 0.051067 | 0 |  |  |  |  | 0 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837 |  |  |  |  | 0 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837 |  |  |  |  | 0 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.002478 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.051068 | 172 | 172 |  |  |  |  | 0.051068 | 8.7837 |  |  |  |  | 0 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.002488 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.051078 | 158.9 | 158.9 |  |  |  |  | 0.051078 | 8.1163 |  |  |  |  | 0 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.002488 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.051078 | 161.4 | 161.4 |  |  |  |  | 0.051078 | 8.244 |  |  |  |  | 0 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.002488 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.051078 | 162.8 | 162.8 |  |  |  |  | 0.051078 | 8.3155 |  |  |  |  | 0 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.002488 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.051078 | 269.2 | 269.2 |  |  |  |  | 0.051078 | 13.7503 |  |  |  |  | 0 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.002492 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.051082 | 398 | 398 |  |  |  |  | 0.051082 | 20.3307 |  |  |  |  | 0 | 0
48886 | THW_5354 | C | Houston | YES | 0.002496 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.051086 | 57 | 57 |  |  |  |  | 0.051086 | 2.9119 |  |  |  |  | 0 | 0
48887 | THW_5556 | F | Houston | YES | 0.002496 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.051086 | 57 | 57 |  |  |  |  | 0.051086 | 2.9119 |  |  |  |  | 0 | 0
48885 | THW_5152 | A | Houston | YES | 0.002496 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.051086 | 58 | 58 |  |  |  |  | 0.051086 | 2.963 |  |  |  |  | 0 | 0
48886 | THW_5354 | D | Houston | YES | 0.002496 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.051086 | 58 | 58 |  |  |  |  | 0.051086 | 2.963 |  |  |  |  | 0 | 0
48885 | THW_5152 | B | Houston | YES | 0.002496 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.051086 | 59 | 59 |  |  |  |  | 0.051086 | 3.0141 |  |  |  |  | 0 | 0
48887 | THW_5556 | E | Houston | YES | 0.002496 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.051086 | 59 | 59 |  |  |  |  | 0.051086 | 3.0141 |  |  |  |  | 0 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.002553 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 |  |  |  |  | 0 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.002553 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 |  |  |  |  | 0 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.002553 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 |  |  |  |  | 0 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.002553 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 |  |  |  |  | 0 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.002553 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.051143 | 0 | 0 |  |  |  |  | 0.051143 | 0 |  |  |  |  | 0 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.002865 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.051455 | 0 | 0 | 0 | 0 |  |  | 0.051455 | 0 |  |  |  |  | 0 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.002865 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.051455 | 0 | 0 | 0 | 0 |  |  | 0.051455 | 0 |  |  |  |  | 0 | 0
1417 | SWETWATR_2G | 2 | West | YES | -0.045937 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.05157 | 72 | 72 |  |  | -3.3075 | 72 | -0.05157 | -3.713 |  |  |  |  | 0 | 0
1418 | SWETWATR_3G | 3 | West | YES | -0.045937 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.05157 | 68 | 68 |  |  | -3.1237 | 68 | -0.05157 | -3.5067 |  |  |  |  | 0 | 0
1419 | SWETWATR_4G | 4 | West | YES | -0.045937 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.05157 | 61 | 61 |  |  | -2.8022 | 61 | -0.05157 | -3.1457 |  |  |  |  | 0 | 0
1416 | SWETWATR_1G | 1 | West | YES | -0.045937 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.05157 | 30 | 30 |  |  | -1.3781 | 30 | -0.05157 | -1.5471 |  |  |  |  | 0 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.003066 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.051656 | 154.2 | 154.2 | 0.47278 | 154.2 |  |  | 0.051656 | 7.9654 |  |  |  |  | 0 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | 0.003066 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.051656 | 158 | 158 | 0.48443 | 158 |  |  | 0.051656 | 8.1617 |  |  |  |  | 0 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | 0.003066 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.051656 | 159 | 159 | 0.48749 | 159 |  |  | 0.051656 | 8.2133 |  |  |  |  | 0 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | 0.003066 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.051656 | 380 | 380 | 1.1651 | 380 |  |  | 0.051656 | 19.6294 |  |  |  |  | 0 | 0
1878 | WLFHOLW_2G | 2 | North | YES | 0.003099 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.051689 | 215.7 | 215.7 | 0.66845 | 215.7 |  |  | 0.051689 | 11.1494 |  |  |  |  | 0 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.003099 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.051689 | 217.3 | 217.3 | 0.67341 | 217.3 |  |  | 0.051689 | 11.2321 |  |  |  |  | 0 | 0
1879 | WLFHOLW_3G | 3 | North | YES | 0.003099 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.051689 | 272.4 | 272.4 | 0.84417 | 272.4 |  |  | 0.051689 | 14.0801 |  |  |  |  | 0 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.003164 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.051754 | 46 | 46 | 0.14554 | 46 |  |  | 0.051754 | 2.3807 |  |  |  |  | 0 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.003164 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.051754 | 48 | 48 | 0.15187 | 48 |  |  | 0.051754 | 2.4842 |  |  |  |  | 0 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.003164 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.051754 | 105 | 105 | 0.33222 | 105 |  |  | 0.051754 | 5.4342 |  |  |  |  | 0 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | 0.003171 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0 |  |  |  |  | 0 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.003171 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0 |  |  |  |  | 0 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | 0.003171 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0 |  |  |  |  | 0 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.003171 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.051761 | 0 | 0 | 0 | 0 |  |  | 0.051761 | 0 |  |  |  |  | 0 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.003171 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.051761 | 17 | 17 | 0.053907 | 17 |  |  | 0.051761 | 0.87994 |  |  |  |  | 0 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | 0.003173 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.051763 | 0 | 463 | 1.4691 | 463 |  |  | 0.051763 | 23.9664 |  |  |  |  | 0 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.003174 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.051764 | 32 | 32 | 0.10157 | 32 |  |  | 0.051764 | 1.6565 |  |  |  |  | 0 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | 0.003177 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.051767 | 75 | 75 | 0.23827 | 75 |  |  | 0.051767 | 3.8825 |  |  |  |  | 0 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | 0.003177 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.051767 | 222 | 222 | 0.70529 | 222 |  |  | 0.051767 | 11.4923 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 1 | West | YES | -0.046157 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.05179 | 0 | 150 |  |  | 0 | 0 | -0.05179 | 0 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 2 | West | YES | -0.046157 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.05179 | 0 | 220 |  |  | 0 | 0 | -0.05179 | 0 |  |  |  |  | 0 | 0
11065 | ELBOWCK_1G | 1 | West | YES | -0.046157 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.05179 | 0 | 121.9 |  |  | 0 | 0 | -0.05179 | 0 |  |  |  |  | 0 | 0
3403 | THOUSE_1G | 1 | North | YES | 0.003296 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.051886 | 563 | 563 | 1.8556 | 563 |  |  | 0.051886 | 29.2119 |  |  |  |  | 0 | 0
3404 | THOUSE_2G | 2 | North | YES | 0.003296 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.051886 | 807 | 807 | 2.6599 | 807 |  |  | 0.051886 | 41.8722 |  |  |  |  | 0 | 0
239 | BOSQUESW502 | 1 | North | YES | 0.003321 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.051911 | 149 | 149 | 0.49483 | 149 |  |  | 0.051911 | 7.7348 |  |  |  |  | 0 | 0
247 | BOSQUESW501 | 2 | North | YES | 0.003321 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.051911 | 156 | 156 | 0.51808 | 156 |  |  | 0.051911 | 8.0982 |  |  |  |  | 0 | 0
238 | BOSQUESW505 | 1 | North | YES | 0.003321 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.051911 | 255 | 255 | 0.84686 | 255 |  |  | 0.051911 | 13.2374 |  |  |  |  | 0 | 0
253 | BOSQUESW804 | 2 | North | YES | 0.003372 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.051962 | 80 | 80 | 0.26976 | 80 |  |  | 0.051962 | 4.157 |  |  |  |  | 0 | 0
251 | BOSQUESW803 | 2 | North | YES | 0.003372 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.051962 | 150 | 150 | 0.5058 | 150 |  |  | 0.051962 | 7.7943 |  |  |  |  | 0 | 0
1045 | CALENG1G_1G | 1 | West | YES | -0.046446 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0 |  |  |  |  | 0 | 0
1046 | CALENG2G_2G | 2 | West | YES | -0.046446 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0 |  |  |  |  | 0 | 0
1047 | CALENG3G_3G | 3 | West | YES | -0.046446 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.052079 | 0 | 0 |  |  | 0 | 0 | -0.052079 | 0 |  |  |  |  | 0 | 0
39960 | TNTNPONE_18 | 1 | North | YES | 0.003514 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.052104 | 0 | 152.3 | 0.53518 | 152.3 |  |  | 0.052104 | 7.9355 |  |  |  |  | 0 | 0
39970 | TNTNPONE_28 | 1 | North | YES | 0.003514 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.052104 | 0 | 153 | 0.53764 | 153 |  |  | 0.052104 | 7.9719 |  |  |  |  | 0 | 0
48722 | LEG_2___2 | 2 | North | YES | 0.003651 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.052241 | 0 | 819 | 2.9902 | 819 |  |  | 0.052241 | 42.7856 |  |  |  |  | 0 | 0
48721 | LEG_1___1 | 1 | North | YES | 0.003651 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.052241 | 0 | 827 | 3.0194 | 827 |  |  | 0.052241 | 43.2035 |  |  |  |  | 0 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.003654 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.052244 | 0 | 60 | 0.21924 | 60 |  |  | 0.052244 | 3.1347 |  |  |  |  | 0 | 0
244 | WHITNYDM01 | 1 | North | YES | 0.003812 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.052402 | 0 | 0 | 0 | 0 |  |  | 0.052402 | 0 |  |  |  |  | 0 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.003812 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.052402 | 0 | 0 | 0 | 0 |  |  | 0.052402 | 0 |  |  |  |  | 0 | 0
1889 | DECRDOVA_1G | 1 | North | YES | 0.003993 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.052583 | 779 | 779 | 3.1105 | 779 |  |  | 0.052583 | 40.9623 |  |  |  |  | 0 | 0
3382 | BBRN_2G | 2 | North | YES | 0.004017 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.052607 | 0 | 589 | 2.366 | 589 |  |  | 0.052607 | 30.9857 |  |  |  |  | 0 | 0
3381 | BBRN_1G | 1 | North | YES | 0.004017 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.052607 | 0 | 618 | 2.4825 | 618 |  |  | 0.052607 | 32.5113 |  |  |  |  | 0 | 0
11014 | NAV6ST | 1 | West | YES | -0.046978 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.052611 | 115 | 115 |  |  | -5.4025 | 115 | -0.052611 | -6.0502 |  |  |  |  | 0 | 0
11011 | NAV3ST | 1 | West | YES | -0.046978 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.052611 | 92.8 | 92.8 |  |  | -4.3596 | 92.8 | -0.052611 | -4.8823 |  |  |  |  | 0 | 0
11012 | NAV4CT | 1 | West | YES | -0.046978 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.052611 | 80 | 80 |  |  | -3.7582 | 80 | -0.052611 | -4.2088 |  |  |  |  | 0 | 0
11013 | NAV5CT | 1 | West | YES | -0.046978 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.052611 | 80 | 80 |  |  | -3.7582 | 80 | -0.052611 | -4.2088 |  |  |  |  | 0 | 0
11009 | NAV2CT | 1 | West | YES | -0.046978 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.052611 | 71.4 | 71.4 |  |  | -3.3542 | 71.4 | -0.052611 | -3.7564 |  |  |  |  | 0 | 0
11001 | NAV1CT | 1 | West | YES | -0.046978 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.052611 | 70.4 | 70.4 |  |  | -3.3073 | 70.4 | -0.052611 | -3.7038 |  |  |  |  | 0 | 0
11025 | TIEHVSG_2G | 1 | West | YES | -0.046987 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.05262 | 213.2 | 213.2 |  |  | -10.0176 | 213.2 | -0.05262 | -11.2185 |  |  |  |  | 0 | 0
11020 | TIEHVSG_1G | 1 | West | YES | -0.046987 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.05262 | 208.2 | 208.2 |  |  | -9.7827 | 208.2 | -0.05262 | -10.9554 |  |  |  |  | 0 | 0
11024 | TIEHVCG_4G | 1 | West | YES | -0.046987 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.05262 | 147 | 147 |  |  | -6.9071 | 147 | -0.05262 | -7.7351 |  |  |  |  | 0 | 0
11021 | TIEHVCG_1G | 1 | West | YES | -0.046987 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.05262 | 142.1 | 142.1 |  |  | -6.6769 | 142.1 | -0.05262 | -7.4772 |  |  |  |  | 0 | 0
11023 | TIEHVCG_3G | 1 | West | YES | -0.046987 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.05262 | 137.4 | 137.4 |  |  | -6.456 | 137.4 | -0.05262 | -7.2299 |  |  |  |  | 0 | 0
11022 | TIEHVCG_2G | 1 | West | YES | -0.046987 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.05262 | 132.4 | 132.4 |  |  | -6.2211 | 132.4 | -0.05262 | -6.9668 |  |  |  |  | 0 | 0
13131 | CALFREST_1G | 1 | North | YES | 0.004077 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.052667 | 150.7 | 150.7 | 0.6144 | 150.7 |  |  | 0.052667 | 7.937 |  |  |  |  | 0 | 0
13132 | CALFREST_2G | 2 | North | YES | 0.004077 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.052667 | 151 | 151 | 0.61563 | 151 |  |  | 0.052667 | 7.9528 |  |  |  |  | 0 | 0
13133 | CALFREST_3G | 3 | North | YES | 0.004077 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.052667 | 177.4 | 177.4 | 0.72326 | 177.4 |  |  | 0.052667 | 9.3432 |  |  |  |  | 0 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.004093 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.052683 | 0 | 0 | 0 | 0 |  |  | 0.052683 | 0 |  |  |  |  | 0 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.004093 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.052683 | 0 | 0 | 0 | 0 |  |  | 0.052683 | 0 |  |  |  |  | 0 | 0
13134 | CALFREST_4G | 4 | North | YES | 0.004093 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.052683 | 151.5 | 151.5 | 0.62009 | 151.5 |  |  | 0.052683 | 7.9815 |  |  |  |  | 0 | 0
13135 | CALFREST_5G | 5 | North | YES | 0.004093 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.052683 | 152.3 | 152.3 | 0.62336 | 152.3 |  |  | 0.052683 | 8.0237 |  |  |  |  | 0 | 0
13136 | CALFREST_6G | 6 | North | YES | 0.004093 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.052683 | 177.5 | 177.5 | 0.72651 | 177.5 |  |  | 0.052683 | 9.3513 |  |  |  |  | 0 | 0
1944 | MDLTHELP_4G | 4 | North | YES | 0.004242 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.052832 | 211 | 211 | 0.89506 | 211 |  |  | 0.052832 | 11.1476 |  |  |  |  | 0 | 0
1943 | MDLTHELP_3G | 3 | North | YES | 0.004242 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.052832 | 212 | 212 | 0.8993 | 212 |  |  | 0.052832 | 11.2004 |  |  |  |  | 0 | 0
1937 | MDLTHELP_5G | 5 | North | YES | 0.004242 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.052832 | 224 | 224 | 0.95021 | 224 |  |  | 0.052832 | 11.8344 |  |  |  |  | 0 | 0
1938 | MDLTHELP_6G | 6 | North | YES | 0.004242 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.052832 | 226 | 226 | 0.95869 | 226 |  |  | 0.052832 | 11.9401 |  |  |  |  | 0 | 0
3126 | TRINIDAD_6G | 1 | North | YES | 0.004321 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.052911 | 224 | 224 | 0.9679 | 224 |  |  | 0.052911 | 11.8521 |  |  |  |  | 0 | 0
1942 | MDLTHELP_2G | 2 | North | YES | 0.004375 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.052965 | 216.1 | 216.1 | 0.94544 | 216.1 |  |  | 0.052965 | 11.4458 |  |  |  |  | 0 | 0
1941 | MDLTHELP_1G | 1 | North | YES | 0.004375 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.052965 | 216.4 | 216.4 | 0.94675 | 216.4 |  |  | 0.052965 | 11.4617 |  |  |  |  | 0 | 0
1895 | DECRDOVA_5G | D | North | YES | 0.004383 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.052973 | 68 | 68 | 0.29804 | 68 |  |  | 0.052973 | 3.6022 |  |  |  |  | 0 | 0
1893 | DECRDOVA_3G | B | North | YES | 0.004383 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.052973 | 69 | 69 | 0.30243 | 69 |  |  | 0.052973 | 3.6552 |  |  |  |  | 0 | 0
1894 | DECRDOVA_4G | C | North | YES | 0.004383 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.052973 | 69 | 69 | 0.30243 | 69 |  |  | 0.052973 | 3.6552 |  |  |  |  | 0 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.004383 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.052973 | 70 | 70 | 0.30681 | 70 |  |  | 0.052973 | 3.7081 |  |  |  |  | 0 | 0
12323 | ENNSTRAC_2G | 2 | North | YES | 0.004392 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.052982 | 116 | 116 | 0.50947 | 116 |  |  | 0.052982 | 6.1459 |  |  |  |  | 0 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | 0.004392 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.052982 | 196 | 196 | 0.86083 | 196 |  |  | 0.052982 | 10.3845 |  |  |  |  | 0 | 0
3107 | STRYKER_1G | 1 | North | YES | 0.004401 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.052991 | 182 | 182 | 0.80098 | 182 |  |  | 0.052991 | 9.6444 |  |  |  |  | 0 | 0
3108 | STRYKER_2G | 2 | North | YES | 0.004401 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.052991 | 484 | 484 | 2.1301 | 484 |  |  | 0.052991 | 25.6478 |  |  |  |  | 0 | 0
3309 | ASPN_G | 1 | North | YES | 0.004406 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.052996 | 50 | 50 | 0.2203 | 50 |  |  | 0.052996 | 2.6498 |  |  |  |  | 0 | 0
3348 | CHAMPION_1G | MB | North | YES | 0.00441 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.053 | 0 | 0 | 0 | 0 |  |  | 0.053 | 0 |  |  |  |  | 0 | 0
13117 | TGATEWAY_2G | 2 | North | YES | 0.004442 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.053032 | 130 | 130 | 0.57746 | 130 |  |  | 0.053032 | 6.8942 |  |  |  |  | 0 | 0
13118 | TGATEWAY_3G | 3 | North | YES | 0.004442 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.053032 | 148 | 148 | 0.65742 | 148 |  |  | 0.053032 | 7.8488 |  |  |  |  | 0 | 0
13116 | TGATEWAY_1G | 1 | North | YES | 0.004442 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.053032 | 151 | 151 | 0.67074 | 151 |  |  | 0.053032 | 8.0079 |  |  |  |  | 0 | 0
13119 | TGATEWAY_4G | 4 | North | YES | 0.004442 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.053032 | 399 | 399 | 1.7724 | 399 |  |  | 0.053032 | 21.1599 |  |  |  |  | 0 | 0
3097 | MARTLAKE_1G | 1 | North | YES | 0.004479 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 790 | 3.5384 | 790 |  |  | 0.053069 | 41.9247 |  |  |  |  | 0 | 0
3098 | MARTLAKE_2G | 2 | North | YES | 0.004479 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 795 | 3.5608 | 795 |  |  | 0.053069 | 42.19 |  |  |  |  | 0 | 0
3099 | MARTLAKE_3G | 3 | North | YES | 0.004479 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.053069 | 0 | 804 | 3.6011 | 804 |  |  | 0.053069 | 42.6677 |  |  |  |  | 0 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | -0.047437 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 37.5 |  |  | 0 | 0 | -0.05307 | 0 |  |  |  |  | 0 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | -0.047437 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 107.5 |  |  | 0 | 0 | -0.05307 | 0 |  |  |  |  | 0 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | -0.047437 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.05307 | 0 | 135 |  |  | 0 | 0 | -0.05307 | 0 |  |  |  |  | 0 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | -0.047437 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 119 |  |  | 0 | 0 | -0.05307 | 0 |  |  |  |  | 0 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | -0.047437 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 105 |  |  | 0 | 0 | -0.05307 | 0 |  |  |  |  | 0 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | -0.047437 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.05307 | 0 | 80.5 |  |  | 0 | 0 | -0.05307 | 0 |  |  |  |  | 0 | 0
2414 | MTCK7_G | 7 | North | YES | 0.004678 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.053268 | 115 | 115 | 0.53797 | 115 |  |  | 0.053268 | 6.1258 |  |  |  |  | 0 | 0
2413 | MTCK6_G | 6 | North | YES | 0.004678 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.053268 | 118 | 118 | 0.552 | 118 |  |  | 0.053268 | 6.2857 |  |  |  |  | 0 | 0
2417 | MTCK8_G | 8 | North | YES | 0.004678 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.053268 | 556 | 556 | 2.601 | 556 |  |  | 0.053268 | 29.6171 |  |  |  |  | 0 | 0
12440 | PARKD_1SVC8 | 1 | North | YES | 0.004735 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.053325 | 0 | 0 | 0 | 0 |  |  | 0.053325 | 0 |  |  |  |  | 0 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.004735 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.053325 | 0 | 0 | 0 | 0 |  |  | 0.053325 | 0 |  |  |  |  | 0 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.004751 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.053341 | 161 | 161 | 0.76491 | 161 |  |  | 0.053341 | 8.5879 |  |  |  |  | 0 | 0
12422 | FPLEFR2B_G | 2 | North | YES | 0.004751 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.053341 | 161 | 161 | 0.76491 | 161 |  |  | 0.053341 | 8.5879 |  |  |  |  | 0 | 0
12421 | FPLEFR2A_G | 1 | North | YES | 0.004751 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.053341 | 162 | 162 | 0.76966 | 162 |  |  | 0.053341 | 8.6413 |  |  |  |  | 0 | 0
12423 | FPLEFR2C_G | 3 | North | YES | 0.004751 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.053341 | 163 | 163 | 0.77441 | 163 |  |  | 0.053341 | 8.6946 |  |  |  |  | 0 | 0
12412 | FPLEFR1B_G | 2 | North | YES | 0.004751 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.053341 | 164 | 164 | 0.77916 | 164 |  |  | 0.053341 | 8.748 |  |  |  |  | 0 | 0
12413 | FPLEFR1C_G | 3 | North | YES | 0.004751 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.053341 | 164 | 164 | 0.77916 | 164 |  |  | 0.053341 | 8.748 |  |  |  |  | 0 | 0
12414 | FPLEFR1S_G | 4 | North | YES | 0.004751 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.053341 | 414 | 414 | 1.9669 | 414 |  |  | 0.053341 | 22.0833 |  |  |  |  | 0 | 0
12424 | FPLEFR2S_G | 4 | North | YES | 0.004751 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.053341 | 415 | 415 | 1.9717 | 415 |  |  | 0.053341 | 22.1366 |  |  |  |  | 0 | 0
2451 | LKHB1_G | 1 | North | YES | 0.004769 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.053359 | 391 | 391 | 1.8647 | 391 |  |  | 0.053359 | 20.8635 |  |  |  |  | 0 | 0
2452 | LKHB2_G | 2 | North | YES | 0.004769 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.053359 | 516 | 516 | 2.4608 | 516 |  |  | 0.053359 | 27.5334 |  |  |  |  | 0 | 0
948 | STEAM1 | 1 | North | YES | 0.004863 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.053453 | 20 | 20 | 0.09726 | 20 |  |  | 0.053453 | 1.0691 |  |  |  |  | 0 | 0
949 | STEAM2 | 1 | North | YES | 0.004863 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.053453 | 26 | 26 | 0.12644 | 26 |  |  | 0.053453 | 1.3898 |  |  |  |  | 0 | 0
950 | STEAM3 | 1 | North | YES | 0.004863 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.053453 | 42 | 42 | 0.20425 | 42 |  |  | 0.053453 | 2.245 |  |  |  |  | 0 | 0
837 | NEWMAN_G5 | 1 | North | YES | 0.004866 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.053456 | 40 | 40 | 0.19464 | 40 |  |  | 0.053456 | 2.1382 |  |  |  |  | 0 | 0
845 | OLINGER_G4 | 1 | North | YES | 0.004881 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.053471 | 76 | 76 | 0.37096 | 76 |  |  | 0.053471 | 4.0638 |  |  |  |  | 0 | 0
842 | OLINGER_G1 | 1 | North | YES | 0.004881 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.053471 | 79 | 79 | 0.3856 | 79 |  |  | 0.053471 | 4.2242 |  |  |  |  | 0 | 0
843 | OLINGER_G2 | 1 | North | YES | 0.004881 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.053471 | 110 | 110 | 0.53691 | 110 |  |  | 0.053471 | 5.8818 |  |  |  |  | 0 | 0
844 | OLINGER_G3 | 1 | North | YES | 0.004881 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.053471 | 150 | 150 | 0.73215 | 150 |  |  | 0.053471 | 8.0207 |  |  |  |  | 0 | 0
1008 | PB6GEN_7G | 6 | West | YES | -0.047875 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.053508 | 515 | 515 |  |  | -24.6556 | 515 | -0.053508 | -27.5564 |  |  |  |  | 0 | 0
1007 | PB5GEN_6G | 5 | West | YES | -0.047875 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.053508 | 114 | 114 |  |  | -5.4577 | 114 | -0.053508 | -6.0999 |  |  |  |  | 0 | 0
1005 | PBCTDGE_4G | D | West | YES | -0.047875 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.053508 | 68 | 68 |  |  | -3.2555 | 68 | -0.053508 | -3.6385 |  |  |  |  | 0 | 0
1004 | PBCTCGE_3G | C | West | YES | -0.047875 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.053508 | 67 | 67 |  |  | -3.2076 | 67 | -0.053508 | -3.585 |  |  |  |  | 0 | 0
1006 | PBCTEGE_5G | E | West | YES | -0.047875 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.053508 | 67 | 67 |  |  | -3.2076 | 67 | -0.053508 | -3.585 |  |  |  |  | 0 | 0
1002 | PBCTAGE_1G | A | West | YES | -0.047875 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.053508 | 66 | 66 |  |  | -3.1597 | 66 | -0.053508 | -3.5315 |  |  |  |  | 0 | 0
1003 | PBCTBGE_2G | B | West | YES | -0.047875 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.053508 | 66 | 66 |  |  | -3.1597 | 66 | -0.053508 | -3.5315 |  |  |  |  | 0 | 0
5925 | DCEAST | EQ | North | YES | 0.004963 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.053553 | 0 | 0 | 0 | 0 |  |  | 0.053553 | 0 |  |  |  |  | 0 | 0
1701 | MOSES_1G | 1 | North | YES | 0.004963 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 558 | 2.7694 | 558 |  |  | 0.053553 | 29.8827 |  |  |  |  | 0 | 0
1702 | MOSES_2G | 2 | North | YES | 0.004963 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 579 | 2.8736 | 579 |  |  | 0.053553 | 31.0073 |  |  |  |  | 0 | 0
1703 | MOSES_3G | 3 | North | YES | 0.004963 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.053553 | 0 | 808 | 4.0101 | 808 |  |  | 0.053553 | 43.271 |  |  |  |  | 0 | 0
1675 | PEC_1G | 1 | North | YES | 0.005012 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0 |  |  |  |  | 0 | 0
1676 | PEC_2G | 2 | North | YES | 0.005012 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0 |  |  |  |  | 0 | 0
1677 | PEC_3G | 3 | North | YES | 0.005012 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.053602 | 0 | 0 | 0 | 0 |  |  | 0.053602 | 0 |  |  |  |  | 0 | 0
1679 | LAMARPWR_2G | 2 | North | YES | 0.005012 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.053602 | 156 | 156 | 0.78187 | 156 |  |  | 0.053602 | 8.3619 |  |  |  |  | 0 | 0
1681 | LAMARPWR_4G | 4 | North | YES | 0.005012 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.053602 | 156 | 156 | 0.78187 | 156 |  |  | 0.053602 | 8.3619 |  |  |  |  | 0 | 0
1682 | LAMARPWR_5G | 5 | North | YES | 0.005012 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.053602 | 157 | 157 | 0.78688 | 157 |  |  | 0.053602 | 8.4155 |  |  |  |  | 0 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.005012 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.053602 | 160 | 160 | 0.80192 | 160 |  |  | 0.053602 | 8.5764 |  |  |  |  | 0 | 0
1680 | LAMARPWR_3G | 3 | North | YES | 0.005012 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.053602 | 196 | 196 | 0.98235 | 196 |  |  | 0.053602 | 10.506 |  |  |  |  | 0 | 0
1683 | LAMARPWR_6G | 6 | North | YES | 0.005012 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.053602 | 198 | 198 | 0.99238 | 198 |  |  | 0.053602 | 10.6132 |  |  |  |  | 0 | 0
1948 | HANDLEY_4G | 4 | North | YES | 0.005031 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.053621 | 435 | 435 | 2.1885 | 435 |  |  | 0.053621 | 23.3252 |  |  |  |  | 0 | 0
11691 | KMICHICT1_G | 1 | North | YES | 0.005034 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.053624 | 144 | 144 | 0.7249 | 144 |  |  | 0.053624 | 7.7219 |  |  |  |  | 0 | 0
11694 | KMICHICT4_G | 4 | North | YES | 0.005034 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.053624 | 144 | 144 | 0.7249 | 144 |  |  | 0.053624 | 7.7219 |  |  |  |  | 0 | 0
11692 | KMICHICT2_G | 2 | North | YES | 0.005034 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.053624 | 146 | 146 | 0.73496 | 146 |  |  | 0.053624 | 7.8291 |  |  |  |  | 0 | 0
11695 | KMICHICT5_G | 5 | North | YES | 0.005034 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.053624 | 148 | 148 | 0.74503 | 148 |  |  | 0.053624 | 7.9364 |  |  |  |  | 0 | 0
11696 | KMICHIST6_G | 6 | North | YES | 0.005034 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.053624 | 310 | 310 | 1.5605 | 310 |  |  | 0.053624 | 16.6235 |  |  |  |  | 0 | 0
11693 | KMICHIST3_G | 3 | North | YES | 0.005034 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.053624 | 312 | 312 | 1.5706 | 312 |  |  | 0.053624 | 16.7308 |  |  |  |  | 0 | 0
1689 | VALLEY_3G | 3 | North | YES | 0.005034 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.053624 | 375 | 375 | 1.8878 | 375 |  |  | 0.053624 | 20.1091 |  |  |  |  | 0 | 0
1947 | HANDLEY_3G | 3 | North | YES | 0.005036 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.053626 | 395 | 395 | 1.9892 | 395 |  |  | 0.053626 | 21.1824 |  |  |  |  | 0 | 0
1949 | HANDLEY_5G | 5 | North | YES | 0.005036 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.053626 | 435 | 435 | 2.1907 | 435 |  |  | 0.053626 | 23.3274 |  |  |  |  | 0 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.005044 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.053634 | 156 | 156 | 0.78686 | 156 |  |  | 0.053634 | 8.3669 |  |  |  |  | 0 | 0
2382 | NTHLK2_G | 2 | North | YES | 0.005044 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.053634 | 181 | 181 | 0.91296 | 181 |  |  | 0.053634 | 9.7078 |  |  |  |  | 0 | 0
2383 | NTHLK3_G | 3 | North | YES | 0.005044 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.053634 | 329 | 329 | 1.6595 | 329 |  |  | 0.053634 | 17.6457 |  |  |  |  | 0 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.005154 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.053744 | 170 | 170 | 0.87618 | 170 |  |  | 0.053744 | 9.1365 |  |  |  |  | 0 | 0
1688 | VALLEY_2G | 2 | North | YES | 0.005154 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.053744 | 527 | 527 | 2.7162 | 527 |  |  | 0.053744 | 28.3232 |  |  |  |  | 0 | 0
2371 | COLLIN_1G | MB | North | YES | 0.005219 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.053809 | 0 | 0 | 0 | 0 |  |  | 0.053809 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 1 | North | YES | 0.005237 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.053827 | 0 | 0 | 0 | 0 |  |  | 0.053827 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 2 | North | YES | 0.005237 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.053827 | 0 | 0 | 0 | 0 |  |  | 0.053827 | 0 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.048204 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.053837 | 0 | 35 |  |  | 0 | 0 | -0.053837 | 0 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.048204 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.053837 | 0 | 30 |  |  | 0 | 0 | -0.053837 | 0 |  |  |  |  | 0 | 0
11147 | NOTREES_1G | 1 | West | YES | -0.048921 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.054554 | 0 | 149 |  |  | 0 | 0 | -0.054554 | 0 |  |  |  |  | 0 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.006131 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.054721 | 61 | 61 | 0.37399 | 61 |  |  | 0.054721 | 3.338 |  |  |  |  | 0 | 0
924 | SPENCER_G5 | 1 | North | YES | 0.006131 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.054721 | 66 | 66 | 0.40465 | 66 |  |  | 0.054721 | 3.6116 |  |  |  |  | 0 | 0
1861 | EAGLEMNT_1G | MB | North | YES | 0.006645 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0 |  |  |  |  | 0 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.006645 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0 |  |  |  |  | 0 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.006645 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.055235 | 0 | 0 | 0 | 0 |  |  | 0.055235 | 0 |  |  |  |  | 0 | 0
1453 | WCPWRCO_1G | 1 | North | YES | 0.007071 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.055661 | 204 | 204 | 1.4425 | 204 |  |  | 0.055661 | 11.3549 |  |  |  |  | 0 | 0
1454 | WCPWRCO_2G | 2 | North | YES | 0.007071 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.055661 | 204 | 204 | 1.4425 | 204 |  |  | 0.055661 | 11.3549 |  |  |  |  | 0 | 0
1455 | WCPWRCO_3G | 3 | North | YES | 0.007071 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.055661 | 242 | 242 | 1.7112 | 242 |  |  | 0.055661 | 13.47 |  |  |  |  | 0 | 0
1326 | STANTONW_8 | 1 | West | YES | -0.051389 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.057022 | 0 | 100.5 |  |  | 0 | 0 | -0.057022 | 0 |  |  |  |  | 0 | 0
728 | WOLFRIDGE801 | 1 | North | YES | 0.00863 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.05722 | 0 | 112.5 | 0.97088 | 112.5 |  |  | 0.05722 | 6.4373 |  |  |  |  | 0 | 0
1328 | OCOTILLO_1G | 1 | West | YES | -0.053498 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.059131 | 0 | 58 |  |  | 0 | 0 | -0.059131 | 0 |  |  |  |  | 0 | 0
1349 | WESTXWIN_1G | 1 | West | YES | -0.053676 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.059309 | 0 | 6.6 |  |  | 0 | 0 | -0.059309 | 0 |  |  |  |  | 0 | 0
1350 | NWPWRG1_1G | 1 | West | YES | -0.053676 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.059309 | 0 | 34.3 |  |  | 0 | 0 | -0.059309 | 0 |  |  |  |  | 0 | 0
1442 | COKFIELD_5 | 1 | North | YES | 0.01108 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.05967 | 0 | 165 | 1.8282 | 165 |  |  | 0.05967 | 9.8456 |  |  |  |  | 0 | 0
1438 | MESQUITW_2G | 1 | North | YES | 0.01108 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.05967 | 0 | 236 | 2.6149 | 236 |  |  | 0.05967 | 14.0822 |  |  |  |  | 0 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.01108 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.05967 | 366 | 366 | 4.0553 | 366 |  |  | 0.05967 | 21.8393 |  |  |  |  | 0 | 0
1437 | MESQUITW_1G | 1 | North | YES | 0.01108 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.05967 | 0 | 400 | 4.432 | 400 |  |  | 0.05967 | 23.8681 |  |  |  |  | 0 | 0
1333 | MCDDONAL_8 | 1 | West | YES | -0.054171 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.059804 | 0 | 214.2 |  |  | 0 | 0 | -0.059804 | 0 |  |  |  |  | 0 | 0
581 | JCKCNTY802 | 2 | North | YES | 0.011414 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.060004 | 147 | 147 | 1.6779 | 147 |  |  | 0.060004 | 8.8206 |  |  |  |  | 0 | 0
582 | JCKCNTY803 | 3 | North | YES | 0.011414 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.060004 | 147 | 147 | 1.6779 | 147 |  |  | 0.060004 | 8.8206 |  |  |  |  | 0 | 0
580 | JCKCNTY801 | 1 | North | YES | 0.011414 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.060004 | 288 | 288 | 3.2872 | 288 |  |  | 0.060004 | 17.2812 |  |  |  |  | 0 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.055296 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.060929 | 137 | 137 |  |  | -7.5756 | 137 | -0.060929 | -8.3472 |  |  |  |  | 0 | 0
1040 | MRGNBG_2G | B | West | YES | -0.055296 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.060929 | 71 | 71 |  |  | -3.926 | 71 | -0.060929 | -4.3259 |  |  |  |  | 0 | 0
1041 | MRGNCG_3G | C | West | YES | -0.055296 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.060929 | 70 | 70 |  |  | -3.8707 | 70 | -0.060929 | -4.265 |  |  |  |  | 0 | 0
1043 | MRGNEG_5G | E | West | YES | -0.055296 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.060929 | 70 | 70 |  |  | -3.8707 | 70 | -0.060929 | -4.265 |  |  |  |  | 0 | 0
1039 | MRGNAG_1G | A | West | YES | -0.055296 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.060929 | 69 | 69 |  |  | -3.8154 | 69 | -0.060929 | -4.2041 |  |  |  |  | 0 | 0
1042 | MRGNDG_4G | D | West | YES | -0.055296 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.060929 | 68 | 68 |  |  | -3.7601 | 68 | -0.060929 | -4.1431 |  |  |  |  | 0 | 0
1044 | MRGNFG_6G | F | West | YES | -0.055296 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.060929 | 66 | 66 |  |  | -3.6495 | 66 | -0.060929 | -4.0213 |  |  |  |  | 0 | 0
1320 | BSP 1 | 1 | West | YES | -0.055685 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.061318 | 0 | 0 |  |  | 0 | 0 | -0.061318 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.012797 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.012797 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.061387 | 0 | 0 | 0 | 0 |  |  | 0.061387 | 0 |  |  |  |  | 0 | 0
332 | RWMILLER01 | 1 | North | YES | 0.012978 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.061568 | 73 | 73 | 0.94739 | 73 |  |  | 0.061568 | 4.4945 |  |  |  |  | 0 | 0
336 | RWMILLER05 | 5 | North | YES | 0.012978 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.061568 | 101 | 101 | 1.3108 | 101 |  |  | 0.061568 | 6.2184 |  |  |  |  | 0 | 0
335 | RWMILLER04 | 4 | North | YES | 0.012978 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.061568 | 102 | 102 | 1.3238 | 102 |  |  | 0.061568 | 6.28 |  |  |  |  | 0 | 0
333 | RWMILLER02 | 2 | North | YES | 0.012978 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.061568 | 119 | 119 | 1.5444 | 119 |  |  | 0.061568 | 7.3266 |  |  |  |  | 0 | 0
334 | RWMILLER03 | 3 | North | YES | 0.012978 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.061568 | 208 | 208 | 2.6994 | 208 |  |  | 0.061568 | 12.8062 |  |  |  |  | 0 | 0
503 | NTHTEXAS01 | 1 | North | YES | 0.013714 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.062304 | 18 | 18 | 0.24685 | 18 |  |  | 0.062304 | 1.1215 |  |  |  |  | 0 | 0
504 | NTHTEXAS02 | 2 | North | YES | 0.013714 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.062304 | 18 | 18 | 0.24685 | 18 |  |  | 0.062304 | 1.1215 |  |  |  |  | 0 | 0
505 | NTHTEXAS03 | 3 | North | YES | 0.013714 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.062304 | 38 | 38 | 0.52113 | 38 |  |  | 0.062304 | 2.3676 |  |  |  |  | 0 | 0
1327 | WILDHRSE_1G | 1 | West | YES | -0.05766 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.063293 | 0 | 120 |  |  | 0 | 0 | -0.063293 | 0 |  |  |  |  | 0 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.059128 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.064761 | 0 | 120 |  |  | 0 | 0 | -0.064761 | 0 |  |  |  |  | 0 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.063919 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.069552 | 0 | 225 |  |  | 0 | 0 | -0.069552 | 0 |  |  |  |  | 0 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.064627 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.07026 | 0 | 180 |  |  | 0 | 0 | -0.07026 | 0 |  |  |  |  | 0 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.064627 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.07026 | 0 | 180 |  |  | 0 | 0 | -0.07026 | 0 |  |  |  |  | 0 | 0
344 | MRSSHPRD | 1 | North | YES | 0.023526 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.072116 | 0 | 0 | 0 | 0 |  |  | 0.072116 | 0 |  |  |  |  | 0 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.023526 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.072116 | 0 | 0 | 0 | 0 |  |  | 0.072116 | 0 |  |  |  |  | 0 | 0
6637 | SNYDERW1A | 1 | West | YES | -0.068953 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.074586 | 0 | 63 |  |  | 0 | 0 | -0.074586 | 0 |  |  |  |  | 0 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.072453 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.078086 | 0 | 141 |  |  | 0 | 0 | -0.078086 | 0 |  |  |  |  | 0 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.072453 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.078086 | 0 | 120 |  |  | 0 | 0 | -0.078086 | 0 |  |  |  |  | 0 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.072731 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.078364 | 0 | 99 |  |  | 0 | 0 | -0.078364 | 0 |  |  |  |  | 0 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.072731 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.078364 | 0 | 61 |  |  | 0 | 0 | -0.078364 | 0 |  |  |  |  | 0 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.072731 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0 |  |  |  |  | 0 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.072731 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0 |  |  |  |  | 0 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.072731 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.078364 | 0 | 0 |  |  | 0 | 0 | -0.078364 | 0 |  |  |  |  | 0 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.079616 | 22.8 | 0 | 114 |  | 1.04 | Wind | -1 | 0.085249 | 0 | 114 |  |  | 0 | 0 | -0.085249 | 0 |  |  |  |  | 0 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.081016 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.086649 | 0 | 150 |  |  | 0 | 0 | -0.086649 | 0 |  |  |  |  | 0 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.081016 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.086649 | 0 | 101 |  |  | 0 | 0 | -0.086649 | 0 |  |  |  |  | 0 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.039674 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.088264 | 0 | 120 | 4.7609 | 120 |  |  | 0.088264 | 10.5917 |  |  |  |  | 0 | 0
36998 | RDCNYNG1 | 1 | West | YES | -0.082833 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.088466 | 0 | 84 |  |  | 0 | 0 | -0.088466 | 0 |  |  |  |  | 0 | 0
6407 | TURKTRAK1A | 1 | West | YES | -0.091498 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.097131 | 0 | 169.5 |  |  | 0 | 0 | -0.097131 | 0 |  |  |  |  | 0 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.069041 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.11763 | 242 | 242 | 16.7079 | 242 |  |  | 0.11763 | 28.4668 |  |  |  |  | 0 | 0
6144 | MCADOO1A | 1 | West | YES | -0.12715 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.13278 | 0 | 150 |  |  | 0 | 0 | -0.13278 | 0 |  |  |  |  | 0 | 0
60081 | WHRLWIND1A | 1 | West | YES | -0.14207 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.1477 | 0 | 60 |  |  | 0 | 0 | -0.1477 | 0 |  |  |  |  | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0

## Zones
Houston | 1
North | 1
South | 1
West | -1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | West | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1073 | SCURRYCW_2G | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3126 | TRINIDAD_6G | GST
3309 | ASPN_G | Bio
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5920 | WELSHDC1 | DCTie
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6096 | NORTHDC7 | DCTie
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NBEC7 | GST
8442 | NBEC7 | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11056 | ROSCOE_1G | Wind
11057 | CHAMPION_1G | Wind
11058 | PYRON_1G | Wind
11059 | INADALE_1G | Wind
11065 | ELBOWCK_1G | Wind
11147 | NOTREES_1G | Wind
11309 | BULLCREK_2G | Wind
11310 | BULLCREK_1G | Wind
11320 | COYOTE_1G | Wind
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
48940 | WARVUE_GT1 | Cogen
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
71061 | L_SWEETW1_5N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
76095 | L_CAPRSI1_1N | Wind
76096 | L_CAPRSI1_2N | Wind
76097 | L_CAPRGE1_1N | Wind
80003 | MILHWYS | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80263 | B_DAVIS31A | CC
80264 | B_DAVIS41A | CC
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
86104 | CID-138 | DCTie
86105 | CID-230 | DCTie
86106 | CUF-230 | DCTie
86107 | CUF-138 | DCTie
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR