## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  | Summary of Key Data points | Value
File Description: Cont_ LonCrek2_5 to CokField_5 OL_ Murry to Paint
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K27 |  | Number of units | 645
|  |  | Dec PTDF cutoff point | 543
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  | Dec PTDF cutoff unit | MESQUITW_2G
|  |  | Dec 10% unit | HANDLEY_3G
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  | Dec max cumltv zone impact - cumltv zone share | 0.023973
|  |  | Dec max cumltv zone impact - cumltv zone share pt | 128
Step 5 | Enter Dennis' file name into cell K27 |  | Dec max cumltv zone impact - cumltv zone share unit | TNTNPONE_28
|  |  | North Zonal weighted AWGSF | 0.0036354
Step 6 | click the step one button |  | West Zonal weighted AWGSF | -0.032493
|  |  | Inc PTDF cutoff point | 102
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  | Inc PTDF cutoff unit | OKLA0A
| X6:X30, or to the end of the selected list. |  | Inc 10% unit | MRGNCG_3G
|  |  | Inc max cumltv zone impact - cumltv zone share | 0.033252
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  | Inc max cumltv zone impact - cumltv zone share pt | 28
| of the formulas in columns L:V (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  | Inc max cumltv zone impact - cumltv zone share unit | MRGNFG_6G
| If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct leng |  | North Zonal weighted AWGSF | 0.0036354
| It is only necessary to match the Distributed Slack - Dec worksheet. |  | West Zonal weighted AWGSF | -0.032493
|  |  | Min of zone correlation | 0.012101
Step 9 | Click the step 2 button |  | Bounary gen in West Zone | 0
| The last file saved will still be open, yopu will need to close this file. |  | Bounary gen in soucre zone as % of line | 0%
| This sheet willno longer be open. |  | Bounary gen in North Zone | 0
|  |  | Bounary gen in soucre zone as % of line | 0
|  |  | OL element line rating | 155
|  |  | North Zonal weighted AWGSF | 0.0036354
|  | NW_043009automation.xls | West Zonal weighted AWGSF | -0.032493
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ LonCrek2_5 to CokField_5 OL_ Murry to Paint |  | i_PTDF_DEC_pt | 543 |  | TNTNPONE_28 | Unit at max
1433 | GRHAMSES_1G | 1 | North | YES | 0.067419 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.099912 | 242 | 242 | 16.3154 | 242 |  |  | 0.099912 | 24.1787 | 0.0040352 | 0.011523 |  |  | i_10pctunit | 45 |  | 128 | # units @ max
1600 | BARTNWND_1G | 1 | North | YES | 0.038401 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.070894 | 0 | 120 | 4.6081 | 120 |  |  | 0.070894 | 8.5073 | 0.0060361 | 0.015578 |  |  | # units | 645 |  | 0.023973 | delta max
344 | MRSSHPRD | 1 | North | YES | 0.022736 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.055229 | 0 | 0 | 0 | 0 |  |  | 0.055229 | 0 | 0.0060361 | 0.015578 | [5 empty] | Delta
345 | MRSSHPRD01 | 2 | North | YES | 0.022736 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.055229 | 0 | 0 | 0 | 0 |  |  | 0.055229 | 0 | 0.0060361 | 0.015578 | Weighted Shift Factors |  |  |  | 1 | 0.007488
503 | NTHTEXAS01 | 1 | North | YES | 0.012564 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.045057 | 18 | 18 | 0.22615 | 18 |  |  | 0.045057 | 0.81103 | 0.0063362 | 0.015964 | North | 0.0036354 |  |  | 2 | 0.0095415
504 | NTHTEXAS02 | 2 | North | YES | 0.012564 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.045057 | 18 | 18 | 0.22615 | 18 |  |  | 0.045057 | 0.81103 | 0.0066363 | 0.016351 | West | -0.032493 |  |  | 3 | 0.0095415
505 | NTHTEXAS03 | 3 | North | YES | 0.012564 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.045057 | 38 | 38 | 0.47743 | 38 |  |  | 0.045057 | 1.7122 | 0.00727 | 0.017167 |  |  |  |  | 4 | 0.0095415
332 | RWMILLER01 | 1 | North | YES | 0.012387 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.04488 | 73 | 73 | 0.90425 | 73 |  |  | 0.04488 | 3.2762 | 0.0084872 | 0.018728 |  |  |  |  | 5 | 0.0096279
333 | RWMILLER02 | 2 | North | YES | 0.012387 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.04488 | 119 | 119 | 1.4741 | 119 |  |  | 0.04488 | 5.3407 | 0.010471 | 0.021273 |  |  |  |  | 6 | 0.0097143
334 | RWMILLER03 | 3 | North | YES | 0.012387 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.04488 | 208 | 208 | 2.5765 | 208 |  |  | 0.04488 | 9.335 | 0.01394 | 0.025722 |  |  |  |  | 7 | 0.0098967
335 | RWMILLER04 | 4 | North | YES | 0.012387 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.04488 | 102 | 102 | 1.2635 | 102 |  |  | 0.04488 | 4.5778 | 0.01564 | 0.027904 |  |  |  |  | 8 | 0.010241
336 | RWMILLER05 | 5 | North | YES | 0.012387 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.04488 | 101 | 101 | 1.2511 | 101 |  |  | 0.04488 | 4.5329 | 0.017325 | 0.030064 |  |  |  |  | 9 | 0.010802
1479 | WFCOGEN_1G | 1 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0 | 0.017325 | 0.030064 |  |  |  |  | 10 | 0.011783
1479 | WFCOGEN_1G | 2 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0 | 0.017325 | 0.030064 |  |  |  |  | 11 | 0.012263
1482 | WFCOGEN_2G | 2 | North | YES | 0.01168 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0 | 0.017325 | 0.030064 |  |  |  |  | 12 | 0.01274
1482 | WFCOGEN_2G | 1 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0 | 0.017325 | 0.030064 |  |  |  |  | 13 | 0.01274
580 | JCKCNTY801 | 1 | North | YES | 0.00999 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.042483 | 288 | 288 | 2.8771 | 288 |  |  | 0.042483 | 12.2351 | 0.022127 | 0.035895 |  |  |  |  | 14 | 0.01274
581 | JCKCNTY802 | 2 | North | YES | 0.00999 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.042483 | 147 | 147 | 1.4685 | 147 |  |  | 0.042483 | 6.245 | 0.024578 | 0.038872 |  |  |  |  | 15 | 0.01274
582 | JCKCNTY803 | 3 | North | YES | 0.00999 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.042483 | 147 | 147 | 1.4685 | 147 |  |  | 0.042483 | 6.245 | 0.027029 | 0.041848 |  |  |  |  | 16 | 0.01274
728 | WOLFRIDGE801 | 1 | North | YES | 0.007076 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.039569 | 0 | 112.5 | 0.79605 | 112.5 |  |  | 0.039569 | 4.4515 | 0.028905 | 0.043969 |  |  |  |  | 17 | 0.013769
1432 | GRHAMSES_2G | 2 | North | YES | 0.005683 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.038176 | 366 | 366 | 2.08 | 366 |  |  | 0.038176 | 13.9724 | 0.035008 | 0.050628 |  |  |  |  | 18 | 0.014294
1442 | COKFIELD_5 | 1 | North | YES | 0.005683 | 16.5 | 0 | 165 | 0 | 1.029 | Wind | 1 | 0.038176 | 0 | 165 | 0.93769 | 165 |  |  | 0.038176 | 6.299 | 0.037759 | 0.05363 |  |  |  |  | 19 | 0.014819
1643 | SLSTR1PP_1G | 1 | North | YES | 0.005397 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.03789 | 0 | 60 | 0.32382 | 60 |  |  | 0.03789 | 2.2734 | 0.038759 | 0.054714 |  |  |  |  | 20 | 0.015065
1861 | EAGLEMNT_1G | MB | North | YES | 0.004873 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0 | 0.038759 | 0.054714 |  |  |  |  | 21 | 0.015621
1862 | EAGLEMNT_2G | MB | North | YES | 0.004873 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0 | 0.038759 | 0.054714 |  |  |  |  | 22 | 0.015872
1863 | EAGLEMNT_3G | MB | North | YES | 0.004873 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0 | 0.038759 | 0.054714 |  |  |  |  | 23 | 0.015955
1453 | WCPWRCO_1G | 1 | North | YES | 0.004266 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.036759 | 204 | 204 | 0.87026 | 204 |  |  | 0.036759 | 7.4988 | 0.042161 | 0.058288 |  |  |  |  | 24 | 0.015955
1454 | WCPWRCO_2G | 2 | North | YES | 0.004266 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.036759 | 204 | 204 | 0.87026 | 204 |  |  | 0.036759 | 7.4988 | 0.045562 | 0.061861 |  |  |  |  | 25 | 0.015955
1455 | WCPWRCO_3G | 3 | North | YES | 0.004266 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.036759 | 242 | 242 | 1.0324 | 242 |  |  | 0.036759 | 8.8957 | 0.049597 | 0.066101 |  |  |  |  | 26 | 0.015955
923 | SPENCER_G4 | 1 | North | YES | 0.004247 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.03674 | 61 | 61 | 0.25907 | 61 |  |  | 0.03674 | 2.2411 | 0.050615 | 0.067169 |  |  |  |  | 27 | 0.016127
924 | SPENCER_G5 | 1 | North | YES | 0.004247 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.03674 | 66 | 66 | 0.2803 | 66 |  |  | 0.03674 | 2.4248 | 0.051715 | 0.068325 |  |  |  |  | 28 | 0.016299
6948 | DENISNDM | 1 | North | YES | 0.003692 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.036185 | 0 | 0 | 0 | 0 |  |  | 0.036185 | 0 | 0.051715 | 0.068325 |  |  |  |  | 29 | 0.016503
6948 | DENISNDM | 2 | North | YES | 0.003692 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.036185 | 0 | 0 | 0 | 0 |  |  | 0.036185 | 0 | 0.051715 | 0.068325 |  |  |  |  | 30 | 0.016554
2371 | COLLIN_1G | MB | North | YES | 0.003631 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.036124 | 0 | 0 | 0 | 0 |  |  | 0.036124 | 0 | 0.051715 | 0.068325 |  |  |  |  | 31 | 0.01661
1687 | VALLEY_1G | 1 | North | YES | 0.003619 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.036112 | 170 | 170 | 0.61523 | 170 |  |  | 0.036112 | 6.139 | 0.05455 | 0.07125 |  |  |  |  | 32 | 0.01661
1688 | VALLEY_2G | 2 | North | YES | 0.003619 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.036112 | 527 | 527 | 1.9072 | 527 |  |  | 0.036112 | 19.031 | 0.063337 | 0.08032 |  |  |  |  | 33 | 0.01661
1689 | VALLEY_3G | 3 | North | YES | 0.003511 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.036004 | 375 | 375 | 1.3166 | 375 |  |  | 0.036004 | 13.5015 | 0.06959 | 0.086755 |  |  |  |  | 34 | 0.01661
11691 | KMICHICT1_G | 1 | North | YES | 0.003511 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036004 | 144 | 144 | 0.50558 | 144 |  |  | 0.036004 | 5.1846 | 0.071991 | 0.089226 |  |  |  |  | 35 | 0.016701
11692 | KMICHICT2_G | 2 | North | YES | 0.003511 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.036004 | 146 | 146 | 0.51261 | 146 |  |  | 0.036004 | 5.2566 | 0.074425 | 0.091731 |  |  |  |  | 36 | 0.016983
11693 | KMICHIST3_G | 3 | North | YES | 0.003511 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.036004 | 312 | 312 | 1.0954 | 312 |  |  | 0.036004 | 11.2332 | 0.079628 | 0.097085 |  |  |  |  | 37 | 0.017165
11694 | KMICHICT4_G | 4 | North | YES | 0.003511 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036004 | 144 | 144 | 0.50558 | 144 |  |  | 0.036004 | 5.1846 | 0.082029 | 0.099555 |  |  |  |  | 38 | 0.017235
11695 | KMICHICT5_G | 5 | North | YES | 0.003511 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.036004 | 148 | 148 | 0.51963 | 148 |  |  | 0.036004 | 5.3286 | 0.084497 | 0.10209 |  |  |  |  | 39 | 0.017306
11696 | KMICHIST6_G | 6 | North | YES | 0.003511 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.036004 | 310 | 310 | 1.0884 | 310 |  |  | 0.036004 | 11.1612 | 0.089666 | 0.10741 |  |  |  |  | 40 | 0.017457
1948 | HANDLEY_4G | 4 | North | YES | 0.00351 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.036003 | 435 | 435 | 1.5269 | 435 |  |  | 0.036003 | 15.6613 | 0.096919 | 0.11488 |  |  |  |  | 41 | 0.017527
1947 | HANDLEY_3G | 3 | North | YES | 0.003509 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.036002 | 395 | 395 | 1.3861 | 395 |  |  | 0.036002 | 14.2208 | 0.10351 | 0.12166 |  |  |  |  | 42 | 0.017598
1949 | HANDLEY_5G | 5 | North | YES | 0.003509 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.036002 | 435 | 435 | 1.5264 | 435 |  |  | 0.036002 | 15.6609 | 0.11076 | 0.12912 |  |  |  |  | 43 | 0.017749
2381 | NTHLK1_G | 1 | North | YES | 0.003508 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.036001 | 156 | 156 | 0.54725 | 156 |  |  | 0.036001 | 5.6161 | 0.11336 | 0.1318 |  |  |  |  | 44 | 0.017959
2382 | NTHLK2_G | 2 | North | YES | 0.003508 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.036001 | 181 | 181 | 0.63495 | 181 |  |  | 0.036001 | 6.5162 | 0.11638 | 0.1349 |  |  |  |  | 45 | 0.01815
2383 | NTHLK3_G | 3 | North | YES | 0.003508 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.036001 | 329 | 329 | 1.1541 | 329 |  |  | 0.036001 | 11.8443 | 0.12186 | 0.14055 |  |  |  |  | 46 | 0.018361
1675 | PEC_1G | 1 | North | YES | 0.003499 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0 | 0.12186 | 0.14055 |  |  |  |  | 47 | 0.018436
1676 | PEC_2G | 2 | North | YES | 0.003499 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0 | 0.12186 | 0.14055 |  |  |  |  | 48 | 0.018523
1677 | PEC_3G | 3 | North | YES | 0.003499 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0 | 0.12186 | 0.14055 |  |  |  |  | 49 | 0.018682
1678 | LAMARPWR_1G | 1 | North | YES | 0.003496 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.035989 | 160 | 160 | 0.55936 | 160 |  |  | 0.035989 | 5.7582 | 0.12453 | 0.14329 |  |  |  |  | 50 | 0.018682
1679 | LAMARPWR_2G | 2 | North | YES | 0.003496 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.035989 | 156 | 156 | 0.54538 | 156 |  |  | 0.035989 | 5.6143 | 0.12713 | 0.14597 |  |  |  |  | 51 | 0.018682
1680 | LAMARPWR_3G | 3 | North | YES | 0.003496 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.035989 | 196 | 196 | 0.68522 | 196 |  |  | 0.035989 | 7.0538 | 0.1304 | 0.14933 |  |  |  |  | 52 | 0.018682
1681 | LAMARPWR_4G | 4 | North | YES | 0.003496 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.035989 | 156 | 156 | 0.54538 | 156 |  |  | 0.035989 | 5.6143 | 0.133 | 0.152 |  |  |  |  | 53 | 0.018759
1682 | LAMARPWR_5G | 5 | North | YES | 0.003496 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.035989 | 157 | 157 | 0.54887 | 157 |  |  | 0.035989 | 5.6503 | 0.13562 | 0.1547 |  |  |  |  | 54 | 0.018833
1683 | LAMARPWR_6G | 6 | North | YES | 0.003496 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.035989 | 198 | 198 | 0.69221 | 198 |  |  | 0.035989 | 7.1258 | 0.13892 | 0.15809 |  |  |  |  | 55 | 0.018927
1701 | MOSES_1G | 1 | North | YES | 0.003456 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 558 | 1.9284 | 558 |  |  | 0.035949 | 20.0595 | 0.14823 | 0.16765 |  |  |  |  | 56 | 0.019001
1702 | MOSES_2G | 2 | North | YES | 0.003456 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 579 | 2.001 | 579 |  |  | 0.035949 | 20.8144 | 0.15788 | 0.17757 |  |  |  |  | 57 | 0.019076
1703 | MOSES_3G | 3 | North | YES | 0.003456 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 808 | 2.7924 | 808 |  |  | 0.035949 | 29.0468 | 0.17135 | 0.19142 |  |  |  |  | 58 | 0.019171
5925 | DCEAST | EQ | North | YES | 0.003456 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.035949 | 0 | 0 | 0 | 0 |  |  | 0.035949 | 0 | 0.17135 | 0.19142 |  |  |  |  | 59 | 0.019427
842 | OLINGER_G1 | 1 | North | YES | 0.003399 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.035892 | 79 | 79 | 0.26852 | 79 |  |  | 0.035892 | 2.8355 | 0.17267 | 0.19277 |  |  |  |  | 60 | 0.019692
843 | OLINGER_G2 | 1 | North | YES | 0.003399 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.035892 | 110 | 110 | 0.37389 | 110 |  |  | 0.035892 | 3.9481 | 0.1745 | 0.19465 |  |  |  |  | 61 | 0.020063
844 | OLINGER_G3 | 1 | North | YES | 0.003399 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.035892 | 150 | 150 | 0.50985 | 150 |  |  | 0.035892 | 5.3838 | 0.17701 | 0.19721 |  |  |  |  | 62 | 0.020063
845 | OLINGER_G4 | 1 | North | YES | 0.003399 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.035892 | 76 | 76 | 0.25832 | 76 |  |  | 0.035892 | 2.7278 | 0.17827 | 0.19851 |  |  |  |  | 63 | 0.020097
837 | NEWMAN_G5 | 1 | North | YES | 0.00339 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.035883 | 40 | 40 | 0.1356 | 40 |  |  | 0.035883 | 1.4353 | 0.17894 | 0.1992 |  |  |  |  | 64 | 0.020144
948 | STEAM1 | 1 | North | YES | 0.003387 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.03588 | 20 | 20 | 0.06774 | 20 |  |  | 0.03588 | 0.7176 | 0.17927 | 0.19954 |  |  |  |  | 65 | 0.020209
949 | STEAM2 | 1 | North | YES | 0.003387 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.03588 | 26 | 26 | 0.088062 | 26 |  |  | 0.03588 | 0.93288 | 0.17971 | 0.19998 |  |  |  |  | 66 | 0.020242
950 | STEAM3 | 1 | North | YES | 0.003387 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.03588 | 42 | 42 | 0.14225 | 42 |  |  | 0.03588 | 1.507 | 0.18041 | 0.2007 |  |  |  |  | 67 | 0.020259
1892 | DECRDOVA_2G | A | North | YES | 0.003377 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.03587 | 70 | 70 | 0.23639 | 70 |  |  | 0.03587 | 2.5109 | 0.18157 | 0.2019 |  |  |  |  | 68 | 0.020267
1893 | DECRDOVA_3G | B | North | YES | 0.003377 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.03587 | 69 | 69 | 0.23301 | 69 |  |  | 0.03587 | 2.475 | 0.18272 | 0.20308 |  |  |  |  | 69 | 0.020278
1894 | DECRDOVA_4G | C | North | YES | 0.003377 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.03587 | 69 | 69 | 0.23301 | 69 |  |  | 0.03587 | 2.475 | 0.18388 | 0.20426 |  |  |  |  | 70 | 0.020296
1895 | DECRDOVA_5G | D | North | YES | 0.003377 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.03587 | 68 | 68 | 0.22964 | 68 |  |  | 0.03587 | 2.4392 | 0.18501 | 0.20542 |  |  |  |  | 71 | 0.020326
2451 | LKHB1_G | 1 | North | YES | 0.003324 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.035817 | 391 | 391 | 1.2997 | 391 |  |  | 0.035817 | 14.0044 | 0.19153 | 0.2121 |  |  |  |  | 72 | 0.020355
2452 | LKHB2_G | 2 | North | YES | 0.003324 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.035817 | 516 | 516 | 1.7152 | 516 |  |  | 0.035817 | 18.4816 | 0.20013 | 0.2209 |  |  |  |  | 73 | 0.020384
12411 | FPLEFR1A_G | 1 | North | YES | 0.003313 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035806 | 161 | 161 | 0.53339 | 161 |  |  | 0.035806 | 5.7648 | 0.20282 | 0.22365 |  |  |  |  | 74 | 0.020412
12412 | FPLEFR1B_G | 2 | North | YES | 0.003313 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035806 | 164 | 164 | 0.54333 | 164 |  |  | 0.035806 | 5.8722 | 0.20555 | 0.22645 |  |  |  |  | 75 | 0.020567
12413 | FPLEFR1C_G | 3 | North | YES | 0.003313 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035806 | 164 | 164 | 0.54333 | 164 |  |  | 0.035806 | 5.8722 | 0.20829 | 0.22925 |  |  |  |  | 76 | 0.020771
12414 | FPLEFR1S_G | 4 | North | YES | 0.003313 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.035806 | 414 | 414 | 1.3716 | 414 |  |  | 0.035806 | 14.8237 | 0.21519 | 0.23631 |  |  |  |  | 77 | 0.020834
12421 | FPLEFR2A_G | 1 | North | YES | 0.003313 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.035806 | 162 | 162 | 0.53671 | 162 |  |  | 0.035806 | 5.8006 | 0.21789 | 0.23908 |  |  |  |  | 78 | 0.020898
12422 | FPLEFR2B_G | 2 | North | YES | 0.003313 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035806 | 161 | 161 | 0.53339 | 161 |  |  | 0.035806 | 5.7648 | 0.22057 | 0.24182 |  |  |  |  | 79 | 0.020962
12423 | FPLEFR2C_G | 3 | North | YES | 0.003313 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.035806 | 163 | 163 | 0.54002 | 163 |  |  | 0.035806 | 5.8364 | 0.22329 | 0.24461 |  |  |  |  | 80 | 0.021123
12424 | FPLEFR2S_G | 4 | North | YES | 0.003313 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.035806 | 415 | 415 | 1.3749 | 415 |  |  | 0.035806 | 14.8595 | 0.23021 | 0.25169 |  |  |  |  | 81 | 0.021187
12440 | PARKD_1SVC8 | 1 | North | YES | 0.003301 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035794 | 0 | 0 | 0 | 0 |  |  | 0.035794 | 0 | 0.23021 | 0.25169 |  |  |  |  | 82 | 0.02125
12449 | PARKD_2SVC8 | 1 | North | YES | 0.003301 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035794 | 0 | 0 | 0 | 0 |  |  | 0.035794 | 0 | 0.23021 | 0.25169 |  |  |  |  | 83 | 0.021313
2413 | MTCK6_G | 6 | North | YES | 0.003263 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.035756 | 118 | 118 | 0.38503 | 118 |  |  | 0.035756 | 4.2192 | 0.23218 | 0.2537 |  |  |  |  | 84 | 0.021475
2414 | MTCK7_G | 7 | North | YES | 0.003263 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.035756 | 115 | 115 | 0.37524 | 115 |  |  | 0.035756 | 4.1119 | 0.2341 | 0.25566 |  |  |  |  | 85 | 0.021475
2417 | MTCK8_G | 8 | North | YES | 0.003263 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.035756 | 556 | 556 | 1.8142 | 556 |  |  | 0.035756 | 19.8803 | 0.24337 | 0.26513 |  |  |  |  | 86 | 0.021475
3097 | MARTLAKE_1G | 1 | North | YES | 0.003135 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 790 | 2.4766 | 790 |  |  | 0.035628 | 28.1461 | 0.25654 | 0.27855 |  |  |  |  | 87 | 0.021518
3098 | MARTLAKE_2G | 2 | North | YES | 0.003135 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 795 | 2.4923 | 795 |  |  | 0.035628 | 28.3242 | 0.2698 | 0.29205 |  |  |  |  | 88 | 0.02156
3099 | MARTLAKE_3G | 3 | North | YES | 0.003135 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 804 | 2.5205 | 804 |  |  | 0.035628 | 28.6449 | 0.2832 | 0.3057 |  |  |  |  | 89 | 0.021764
13116 | TGATEWAY_1G | 1 | North | YES | 0.003111 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.035604 | 151 | 151 | 0.46976 | 151 |  |  | 0.035604 | 5.3762 | 0.28572 | 0.30826 |  |  |  |  | 90 | 0.022006
13117 | TGATEWAY_2G | 2 | North | YES | 0.003111 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.035604 | 130 | 130 | 0.40443 | 130 |  |  | 0.035604 | 4.6285 | 0.28789 | 0.31047 |  |  |  |  | 91 | 0.022248
13118 | TGATEWAY_3G | 3 | North | YES | 0.003111 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.035604 | 148 | 148 | 0.46043 | 148 |  |  | 0.035604 | 5.2694 | 0.29036 | 0.31298 |  |  |  |  | 92 | 0.022494
13119 | TGATEWAY_4G | 4 | North | YES | 0.003111 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.035604 | 399 | 399 | 1.2413 | 399 |  |  | 0.035604 | 14.206 | 0.29701 | 0.31975 |  |  |  |  | 93 | 0.022538
12322 | ENNSTRAC_1G | 1 | North | YES | 0.003103 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.035596 | 196 | 196 | 0.60819 | 196 |  |  | 0.035596 | 6.9768 | 0.30028 | 0.32307 |  |  |  |  | 94 | 0.022577
12323 | ENNSTRAC_2G | 2 | North | YES | 0.003103 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.035596 | 116 | 116 | 0.35995 | 116 |  |  | 0.035596 | 4.1291 | 0.30221 | 0.32504 |  |  |  |  | 95 | 0.02262
366 | JNSNCNTY802 | 1 | North | YES | 0.003092 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.035585 | 0 | 0 | 0 | 0 |  |  | 0.035585 | 0 | 0.30221 | 0.32504 |  |  |  |  | 96 | 0.022737
367 | JNSNCNTY802 | 2 | North | YES | 0.003092 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.035585 | 0 | 0 | 0 | 0 |  |  | 0.035585 | 0 | 0.30221 | 0.32504 |  |  |  |  | 97 | 0.022794
3348 | CHAMPION_1G | MB | North | YES | 0.00309 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.035583 | 0 | 0 | 0 | 0 |  |  | 0.035583 | 0 | 0.30221 | 0.32504 |  |  |  |  | 98 | 0.022828
3309 | ASPN_G | 1 | North | YES | 0.003088 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.035581 | 50 | 50 | 0.1544 | 50 |  |  | 0.035581 | 1.779 | 0.30305 | 0.32589 |  |  |  |  | 99 | 0.022828
3107 | STRYKER_1G | 1 | North | YES | 0.003085 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.035578 | 182 | 182 | 0.56147 | 182 |  |  | 0.035578 | 6.4752 | 0.30608 | 0.32897 |  |  |  |  | 100 | 0.022828
3108 | STRYKER_2G | 2 | North | YES | 0.003085 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.035578 | 484 | 484 | 1.4931 | 484 |  |  | 0.035578 | 17.2197 | 0.31415 | 0.33718 |  |  |  |  | 101 | 0.022828
3126 | TRINIDAD_6G | 1 | North | YES | 0.003054 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.035547 | 224 | 224 | 0.6841 | 224 |  |  | 0.035547 | 7.9625 | 0.31789 | 0.34098 |  |  |  |  | 102 | 0.022842
1941 | MDLTHELP_1G | 1 | North | YES | 0.00305 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.035543 | 216.4 | 216.4 | 0.66002 | 216.4 |  |  | 0.035543 | 7.6915 | 0.32149 | 0.34464 |  |  |  |  | 103 | 0.022893
1942 | MDLTHELP_2G | 2 | North | YES | 0.00305 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.035543 | 216.1 | 216.1 | 0.65911 | 216.1 |  |  | 0.035543 | 7.6808 | 0.3251 | 0.3483 |  |  |  |  | 104 | 0.02303
244 | WHITNYDM01 | 1 | North | YES | 0.003046 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.035539 | 0 | 0 | 0 | 0 |  |  | 0.035539 | 0 | 0.3251 | 0.3483 |  |  |  |  | 105 | 0.023089
245 | WHITNYDM02 | 2 | North | YES | 0.003046 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.035539 | 0 | 0 | 0 | 0 |  |  | 0.035539 | 0 | 0.3251 | 0.3483 |  |  |  |  | 106 | 0.023147
1937 | MDLTHELP_5G | 5 | North | YES | 0.00297 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.035463 | 224 | 224 | 0.66528 | 224 |  |  | 0.035463 | 7.9437 | 0.32883 | 0.35209 |  |  |  |  | 107 | 0.023204
1938 | MDLTHELP_6G | 6 | North | YES | 0.00297 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.035463 | 226 | 226 | 0.67122 | 226 |  |  | 0.035463 | 8.0146 | 0.3326 | 0.35591 |  |  |  |  | 108 | 0.023204
1943 | MDLTHELP_3G | 3 | North | YES | 0.00297 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.035463 | 212 | 212 | 0.62964 | 212 |  |  | 0.035463 | 7.5181 | 0.33614 | 0.35949 |  |  |  |  | 109 | 0.023204
1944 | MDLTHELP_4G | 4 | North | YES | 0.00297 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.035463 | 211 | 211 | 0.62667 | 211 |  |  | 0.035463 | 7.4827 | 0.33965 | 0.36306 |  |  |  |  | 110 | 0.023255
13134 | CALFREST_4G | 4 | North | YES | 0.002882 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.035375 | 151.5 | 151.5 | 0.43662 | 151.5 |  |  | 0.035375 | 5.3593 | 0.34218 | 0.36561 |  |  |  |  | 111 | 0.023306
13135 | CALFREST_5G | 5 | North | YES | 0.002882 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.035375 | 152.3 | 152.3 | 0.43893 | 152.3 |  |  | 0.035375 | 5.3876 | 0.34472 | 0.36818 |  |  |  |  | 112 | 0.023354
13136 | CALFREST_6G | 6 | North | YES | 0.002882 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.035375 | 177.5 | 177.5 | 0.51155 | 177.5 |  |  | 0.035375 | 6.2791 | 0.34768 | 0.37117 |  |  |  |  | 113 | 0.023402
13131 | CALFREST_1G | 1 | North | YES | 0.002871 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.035364 | 150.7 | 150.7 | 0.43266 | 150.7 |  |  | 0.035364 | 5.3293 | 0.35019 | 0.37371 |  |  |  |  | 114 | 0.02343
13132 | CALFREST_2G | 2 | North | YES | 0.002871 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.035364 | 151 | 151 | 0.43352 | 151 |  |  | 0.035364 | 5.34 | 0.35271 | 0.37626 |  |  |  |  | 115 | 0.023458
13133 | CALFREST_3G | 3 | North | YES | 0.002871 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.035364 | 177.4 | 177.4 | 0.50932 | 177.4 |  |  | 0.035364 | 6.2736 | 0.35567 | 0.37925 |  |  |  |  | 116 | 0.023491
3381 | BBRN_1G | 1 | North | YES | 0.002832 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.035325 | 0 | 618 | 1.7502 | 618 |  |  | 0.035325 | 21.8308 | 0.36597 | 0.38965 |  |  |  |  | 117 | 0.023518
3382 | BBRN_2G | 2 | North | YES | 0.002832 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.035325 | 0 | 589 | 1.668 | 589 |  |  | 0.035325 | 20.8064 | 0.37579 | 0.39957 |  |  |  |  | 118 | 0.023545
1889 | DECRDOVA_1G | 1 | North | YES | 0.002771 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.035264 | 779 | 779 | 2.1586 | 779 |  |  | 0.035264 | 27.4706 | 0.38878 | 0.41266 |  |  |  |  | 119 | 0.023577
251 | BOSQUESW803 | 2 | North | YES | 0.002639 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.035132 | 150 | 150 | 0.39585 | 150 |  |  | 0.035132 | 5.2698 | 0.39128 | 0.41517 |  |  |  |  | 120 | 0.023677
253 | BOSQUESW804 | 2 | North | YES | 0.002639 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.035132 | 80 | 80 | 0.21112 | 80 |  |  | 0.035132 | 2.8106 | 0.39262 | 0.41651 |  |  |  |  | 121 | 0.023772
48721 | LEG_1___1 | 1 | North | YES | 0.002597 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.03509 | 0 | 827 | 2.1477 | 827 |  |  | 0.03509 | 29.0194 | 0.40641 | 0.43034 |  |  |  |  | 122 | 0.023874
48722 | LEG_2___2 | 2 | North | YES | 0.002597 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.03509 | 0 | 819 | 2.1269 | 819 |  |  | 0.03509 | 28.7387 | 0.42006 | 0.44403 |  |  |  |  | 123 | 0.023885
39960 | TNTNPONE_18 | 1 | North | YES | 0.002507 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.035 | 0 | 152.3 | 0.38182 | 152.3 |  |  | 0.035 | 5.3305 | 0.4226 | 0.44658 |  |  |  |  | 124 | 0.02389
39970 | TNTNPONE_28 | 1 | North | YES | 0.002507 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.035 | 0 | 153 | 0.38357 | 153 |  |  | 0.035 | 5.355 | 0.42515 | 0.44913 |  |  |  |  | 125 | 0.023931
238 | BOSQUESW505 | 1 | North | YES | 0.00249 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.034983 | 255 | 255 | 0.63495 | 255 |  |  | 0.034983 | 8.9207 | 0.42941 | 0.45338 |  |  |  |  | 126 | 0.023971
239 | BOSQUESW502 | 1 | North | YES | 0.00249 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.034983 | 149 | 149 | 0.37101 | 149 |  |  | 0.034983 | 5.2125 | 0.43189 | 0.45586 |  |  |  |  | 127 | 0.023972
247 | BOSQUESW501 | 2 | North | YES | 0.00249 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.034983 | 156 | 156 | 0.38844 | 156 |  |  | 0.034983 | 5.4573 | 0.43449 | 0.45846 |  |  |  |  | 128 | 0.023973
3403 | THOUSE_1G | 1 | North | YES | 0.002398 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.034891 | 563 | 563 | 1.3501 | 563 |  |  | 0.034891 | 19.6436 | 0.44388 | 0.46783 |  |  |  |  | 129 | 0.023972
3404 | THOUSE_2G | 2 | North | YES | 0.002398 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.034891 | 807 | 807 | 1.9352 | 807 |  |  | 0.034891 | 28.157 | 0.45734 | 0.48124 |  |  |  |  | 130 | 0.023972
3416 | LAKE_CRK1_G | 1 | North | YES | 0.002329 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.034822 | 75 | 75 | 0.17467 | 75 |  |  | 0.034822 | 2.6116 | 0.45859 | 0.48249 |  |  |  |  | 131 | 0.023972
3417 | LAKE_CRK2_G | 2 | North | YES | 0.002329 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.034822 | 222 | 222 | 0.51704 | 222 |  |  | 0.034822 | 7.7305 | 0.46229 | 0.48617 |  |  |  |  | 132 | 0.023946
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.002285 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.034778 | 32 | 32 | 0.07312 | 32 |  |  | 0.034778 | 1.1129 | 0.46282 | 0.4867 |  |  |  |  | 133 | 0.023909
32886 | BRYN_ATKINS3 | MB | North | YES | 0.002284 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0 | 0.46282 | 0.4867 |  |  |  |  | 134 | 0.023903
32887 | BRYN_ATKINS6 | MB | North | YES | 0.002284 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0 | 0.46282 | 0.4867 |  |  |  |  | 135 | 0.023886
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.002284 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.034777 | 17 | 17 | 0.038828 | 17 |  |  | 0.034777 | 0.59121 | 0.4631 | 0.48699 |  |  |  |  | 136 | 0.023883
32890 | BRYN_ATKINS4 | MB | North | YES | 0.002284 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0 | 0.4631 | 0.48699 |  |  |  |  | 137 | 0.023883
32891 | BRYN_ATKINS5 | MB | North | YES | 0.002284 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0 | 0.4631 | 0.48699 |  |  |  |  | 138 | 0.023883
990 | GIBN_CREK_G1 | 1 | North | YES | 0.002282 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.034775 | 0 | 463 | 1.0566 | 463 |  |  | 0.034775 | 16.1008 | 0.47083 | 0.49466 |  |  |  |  | 139 | 0.023881
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.002279 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.034772 | 48 | 48 | 0.10939 | 48 |  |  | 0.034772 | 1.6691 | 0.47163 | 0.49545 |  |  |  |  | 140 | 0.023881
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.002279 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.034772 | 46 | 46 | 0.10483 | 46 |  |  | 0.034772 | 1.5995 | 0.47239 | 0.49622 |  |  |  |  | 141 | 0.023881
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.002279 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.034772 | 105 | 105 | 0.2393 | 105 |  |  | 0.034772 | 3.6511 | 0.47414 | 0.49796 |  |  |  |  | 142 | 0.023834
48671 | FTR_GT1_5105 | 1 | North | YES | 0.002212 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.034705 | 154.2 | 154.2 | 0.34109 | 154.2 |  |  | 0.034705 | 5.3515 | 0.47671 | 0.50051 |  |  |  |  | 143 | 0.023829
48672 | FTR_GT2_5110 | 2 | North | YES | 0.002212 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.034705 | 159 | 159 | 0.35171 | 159 |  |  | 0.034705 | 5.5181 | 0.47937 | 0.50314 |  |  |  |  | 144 | 0.023824
48673 | FTR_GT3_5085 | 3 | North | YES | 0.002212 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.034705 | 158 | 158 | 0.3495 | 158 |  |  | 0.034705 | 5.4834 | 0.482 | 0.50575 |  |  |  |  | 145 | 0.023814
48674 | FTR_CN4_5095 | 4 | North | YES | 0.002212 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.034705 | 380 | 380 | 0.84056 | 380 |  |  | 0.034705 | 13.1879 | 0.48834 | 0.51204 |  |  |  |  | 146 | 0.023793
1877 | WLFHOLW_1G | 1 | North | YES | 0.00218 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.034673 | 217.3 | 217.3 | 0.47371 | 217.3 |  |  | 0.034673 | 7.5344 | 0.49196 | 0.51563 |  |  |  |  | 147 | 0.023772
1878 | WLFHOLW_2G | 2 | North | YES | 0.00218 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.034673 | 215.7 | 215.7 | 0.47023 | 215.7 |  |  | 0.034673 | 7.479 | 0.49556 | 0.51919 |  |  |  |  | 148 | 0.02375
1879 | WLFHOLW_3G | 3 | North | YES | 0.00218 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.034673 | 272.4 | 272.4 | 0.59383 | 272.4 |  |  | 0.034673 | 9.4449 | 0.5001 | 0.52369 |  |  |  |  | 149 | 0.023699
1898 | COMCHEPK_1G | 1 | North | YES | 0.002026 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.034519 | 0 | 0 | 0 | 0 |  |  | 0.034519 | 0 | 0.5001 | 0.52369 |  |  |  |  | 150 | 0.023667
1899 | COMCHEPK_2G | 2 | North | YES | 0.002026 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.034519 | 0 | 0 | 0 | 0 |  |  | 0.034519 | 0 | 0.5001 | 0.52369 |  |  |  |  | 151 | 0.023634
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.001873 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 | 0.5001 | 0.52369 |  |  |  |  | 152 | 0.023594
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.001873 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 | 0.5001 | 0.52369 |  |  |  |  | 153 | 0.023594
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.001873 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 | 0.5001 | 0.52369 |  |  |  |  | 154 | 0.023594
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.001873 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 | 0.5001 | 0.52369 |  |  |  |  | 155 | 0.023594
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.001873 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 | 0.5001 | 0.52369 |  |  |  |  | 156 | 0.023594
48885 | THW_5152 | B | Houston | YES | 0.001836 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.034329 | 59 | 59 |  |  |  |  | 0.034329 | 2.0254 | 0.50108 | 0.52466 |  |  |  |  | 157 | 0.023594
48885 | THW_5152 | A | Houston | YES | 0.001836 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.034329 | 58 | 58 |  |  |  |  | 0.034329 | 1.9911 | 0.50205 | 0.52561 |  |  |  |  | 158 | 0.023594
48886 | THW_5354 | D | Houston | YES | 0.001836 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.034329 | 58 | 58 |  |  |  |  | 0.034329 | 1.9911 | 0.50302 | 0.52656 |  |  |  |  | 159 | 0.023594
48886 | THW_5354 | C | Houston | YES | 0.001836 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.034329 | 57 | 57 |  |  |  |  | 0.034329 | 1.9568 | 0.50397 | 0.52749 |  |  |  |  | 160 | 0.023575
48887 | THW_5556 | E | Houston | YES | 0.001836 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.034329 | 59 | 59 |  |  |  |  | 0.034329 | 2.0254 | 0.50495 | 0.52845 |  |  |  |  | 161 | 0.023557
48887 | THW_5556 | F | Houston | YES | 0.001836 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.034329 | 57 | 57 |  |  |  |  | 0.034329 | 1.9568 | 0.5059 | 0.52939 |  |  |  |  | 162 | 0.023539
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.001833 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.034326 | 398 | 398 |  |  |  |  | 0.034326 | 13.6617 | 0.51254 | 0.5359 |  |  |  |  | 163 | 0.023521
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.00183 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.034323 | 162.8 | 162.8 |  |  |  |  | 0.034323 | 5.5878 | 0.51525 | 0.53856 |  |  |  |  | 164 | 0.023502
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.00183 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.034323 | 161.4 | 161.4 |  |  |  |  | 0.034323 | 5.5397 | 0.51794 | 0.5412 |  |  |  |  | 165 | 0.023485
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.00183 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.034323 | 158.9 | 158.9 |  |  |  |  | 0.034323 | 5.4539 | 0.52059 | 0.5438 |  |  |  |  | 166 | 0.023359
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.00183 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.034323 | 269.2 | 269.2 |  |  |  |  | 0.034323 | 9.2397 | 0.52508 | 0.5482 |  |  |  |  | 167 | 0.023308
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025 | 0.52795 | 0.55102 |  |  |  |  | 168 | 0.023257
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025 | 0.53082 | 0.55383 |  |  |  |  | 169 | 0.023206
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025 | 0.53369 | 0.55664 |  |  |  |  | 170 | 0.023121
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.001823 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.034316 | 0 | 0 |  |  |  |  | 0.034316 | 0 | 0.53369 | 0.55664 |  |  |  |  | 171 | 0.023066
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.001821 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.034314 | 744 | 744 |  |  |  |  | 0.034314 | 25.5296 | 0.54609 | 0.56881 |  |  |  |  | 172 | 0.023011
48651 | EP_1_2 | 1 | Houston | YES | 0.001821 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 173 | 0.022956
48651 | EP_1_2 | 2 | Houston | YES | 0.001821 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 174 | 0.022956
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.001821 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 175 | 0.022718
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.001821 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 176 | 0.022718
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.001821 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 177 | 0.022718
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.001821 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 178 | 0.022718
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.001821 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 179 | 0.022718
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.001821 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 180 | 0.022718
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.001821 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 181 | 0.022718
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.001821 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 | 0.54609 | 0.56881 |  |  |  |  | 182 | 0.022718
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.001817 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.03431 | 12 | 12 |  |  |  |  | 0.03431 | 0.41172 | 0.54629 | 0.569 |  |  |  |  | 183 | 0.022718
49803 | EXN_15GT | 1 | Houston | YES | 0.001817 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 184 | 0.022718
49804 | EXN_16GT | 2 | Houston | YES | 0.001817 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 185 | 0.022718
49805 | EXN_17GT | 3 | Houston | YES | 0.001817 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 186 | 0.022714
49826 | EXN938GT | 5 | Houston | YES | 0.001817 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 187 | 0.022714
49828 | EXN941GT | 10 | Houston | YES | 0.001817 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 188 | 0.022714
49829 | EXN942GT | 11 | Houston | YES | 0.001817 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 189 | 0.022714
49830 | EXN943GT | 12 | Houston | YES | 0.001817 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 190 | 0.022714
49831 | EXN944GT | 13 | Houston | YES | 0.001817 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 191 | 0.022714
49832 | EXN945GT | 9 | Houston | YES | 0.001817 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 192 | 0.022714
49837 | EXN_GT | 4 | Houston | YES | 0.001817 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 193 | 0.022714
49838 | EXN_14GT | 14 | Houston | YES | 0.001817 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 | 0.54629 | 0.569 |  |  |  |  | 194 | 0.022714
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.001813 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.034306 | 746 | 746 |  |  |  |  | 0.034306 | 25.5922 | 0.55873 | 0.5812 |  |  |  |  | 195 | 0.022714
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.001809 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.034302 | 107 | 107 |  |  |  |  | 0.034302 | 3.6703 | 0.56051 | 0.58295 |  |  |  |  | 196 | 0.022714
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.001809 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.034302 | 108 | 108 |  |  |  |  | 0.034302 | 3.7046 | 0.56231 | 0.58472 |  |  |  |  | 197 | 0.022714
48875 | THW_3132 | A | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866 | 0.56323 | 0.58562 |  |  |  |  | 198 | 0.022472
48875 | THW_3132 | B | Houston | YES | 0.001809 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.034302 | 53 | 53 |  |  |  |  | 0.034302 | 1.818 | 0.56412 | 0.58648 |  |  |  |  | 199 | 0.022437
48877 | THW_3334 | C | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866 | 0.56503 | 0.58738 |  |  |  |  | 200 | 0.022401
48877 | THW_3334 | D | Houston | YES | 0.001809 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.034302 | 57 | 57 |  |  |  |  | 0.034302 | 1.9552 | 0.56598 | 0.58831 |  |  |  |  | 201 | 0.022383
48879 | THW_4142 | E | Houston | YES | 0.001809 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.034302 | 56 | 56 |  |  |  |  | 0.034302 | 1.9209 | 0.56692 | 0.58923 |  |  |  |  | 202 | 0.022366
48879 | THW_4142 | F | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866 | 0.56783 | 0.59013 |  |  |  |  | 203 | 0.022348
48881 | THW_4344 | G | Houston | YES | 0.001809 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.034302 | 58 | 58 |  |  |  |  | 0.034302 | 1.9895 | 0.5688 | 0.59108 |  |  |  |  | 204 | 0.02233
48881 | THW_4344 | H | Houston | YES | 0.001809 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.034302 | 58 | 58 |  |  |  |  | 0.034302 | 1.9895 | 0.56977 | 0.59202 |  |  |  |  | 205 | 0.022311
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.001801 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.034294 | 0 | 0 |  |  |  |  | 0.034294 | 0 | 0.56977 | 0.59202 |  |  |  |  | 206 | 0.022293
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.001801 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.034294 | 0 | 0 |  |  |  |  | 0.034294 | 0 | 0.56977 | 0.59202 |  |  |  |  | 207 | 0.022274
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.0018 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.034293 | 42 | 42 |  |  |  |  | 0.034293 | 1.4403 | 0.57047 | 0.59271 |  |  |  |  | 208 | 0.022255
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.0018 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.034293 | 42 | 42 |  |  |  |  | 0.034293 | 1.4403 | 0.57117 | 0.5934 |  |  |  |  | 209 | 0.022255
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.0018 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.034293 | 39 | 39 |  |  |  |  | 0.034293 | 1.3374 | 0.57182 | 0.59403 |  |  |  |  | 210 | 0.022255
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.0018 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.034293 | 39 | 39 |  |  |  |  | 0.034293 | 1.3374 | 0.57247 | 0.59467 |  |  |  |  | 211 | 0.022242
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.001799 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.034292 | 0 | 0 |  |  |  |  | 0.034292 | 0 | 0.57247 | 0.59467 |  |  |  |  | 212 | 0.022228
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.001794 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0 | 0.57247 | 0.59467 |  |  |  |  | 213 | 0.022215
48821 | SHELLG2 | 2 | Houston | YES | 0.001794 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0 | 0.57247 | 0.59467 |  |  |  |  | 214 | 0.022202
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.001794 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0 | 0.57247 | 0.59467 |  |  |  |  | 215 | 0.022202
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.001794 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0 | 0.57247 | 0.59467 |  |  |  |  | 216 | 0.022202
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.001791 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 | 0.57247 | 0.59467 |  |  |  |  | 217 | 0.022202
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.001791 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 | 0.57247 | 0.59467 |  |  |  |  | 218 | 0.022202
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.001791 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 | 0.57247 | 0.59467 |  |  |  |  | 219 | 0.022202
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.001791 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 | 0.57247 | 0.59467 |  |  |  |  | 220 | 0.022202
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.001791 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 | 0.57247 | 0.59467 |  |  |  |  | 221 | 0.022202
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.001791 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 | 0.57247 | 0.59467 |  |  |  |  | 222 | 0.022202
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.001791 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 | 0.57247 | 0.59467 |  |  |  |  | 223 | 0.022202
48845 | SOL_GT1 | 1 | Houston | YES | 0.001791 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.034284 | 16.2 | 16.2 |  |  |  |  | 0.034284 | 0.5554 | 0.57274 | 0.59494 |  |  |  |  | 224 | 0.022202
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.001791 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.034284 | 228 | 228 |  |  |  |  | 0.034284 | 7.8167 | 0.57654 | 0.59866 |  |  |  |  | 225 | 0.022202
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.00179 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.034283 | 0 | 0 |  |  |  |  | 0.034283 | 0 | 0.57654 | 0.59866 |  |  |  |  | 226 | 0.022202
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.00179 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.034283 | 0 | 0 |  |  |  |  | 0.034283 | 0 | 0.57654 | 0.59866 |  |  |  |  | 227 | 0.022196
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.00179 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.034283 | 165 | 165 |  |  |  |  | 0.034283 | 5.6567 | 0.57929 | 0.60136 |  |  |  |  | 228 | 0.02212
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.00179 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.034283 | 176 | 176 |  |  |  |  | 0.034283 | 6.0338 | 0.58223 | 0.60423 |  |  |  |  | 229 | 0.02212
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.00179 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.034283 | 213 | 213 |  |  |  |  | 0.034283 | 7.3023 | 0.58578 | 0.60771 |  |  |  |  | 230 | 0.02212
48855 | SRB_GT211035 | B1 | Houston | YES | 0.00179 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.034283 | 18 | 18 |  |  |  |  | 0.034283 | 0.61709 | 0.58608 | 0.60801 |  |  |  |  | 231 | 0.022065
48855 | SRB_GT211035 | B2 | Houston | YES | 0.00179 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.034283 | 12 | 12 |  |  |  |  | 0.034283 | 0.4114 | 0.58628 | 0.6082 |  |  |  |  | 232 | 0.022006
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.001787 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.03428 | 0 | 0 |  |  |  |  | 0.03428 | 0 | 0.58628 | 0.6082 |  |  |  |  | 233 | 0.021934
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.001784 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.034277 | 163.2 | 163.2 |  |  |  |  | 0.034277 | 5.594 | 0.589 | 0.61087 |  |  |  |  | 234 | 0.021928
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.001784 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.034277 | 157.1 | 157.1 |  |  |  |  | 0.034277 | 5.3849 | 0.59162 | 0.61344 |  |  |  |  | 235 | 0.021924
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.001784 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.034277 | 157.5 | 157.5 |  |  |  |  | 0.034277 | 5.3986 | 0.59425 | 0.61601 |  |  |  |  | 236 | 0.021924
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.001784 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.034277 | 157 | 157 |  |  |  |  | 0.034277 | 5.3815 | 0.59686 | 0.61857 |  |  |  |  | 237 | 0.021869
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.001784 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.034277 | 282 | 282 |  |  |  |  | 0.034277 | 9.6661 | 0.60157 | 0.62318 |  |  |  |  | 238 | 0.021816
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.001782 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.034275 | 0 | 0 |  |  |  |  | 0.034275 | 0 | 0.60157 | 0.62318 |  |  |  |  | 239 | 0.021762
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.001782 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.034275 | 0 | 0 |  |  |  |  | 0.034275 | 0 | 0.60157 | 0.62318 |  |  |  |  | 240 | 0.021709
48691 | GBY_73741085 | B | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108 | 0.60235 | 0.62395 |  |  |  |  | 241 | 0.021614
48691 | GBY_73741085 | A | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108 | 0.60313 | 0.62472 |  |  |  |  | 242 | 0.021614
48692 | GBY_81821075 | D | Houston | YES | 0.00178 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.034273 | 55 | 55 |  |  |  |  | 0.034273 | 1.885 | 0.60405 | 0.62561 |  |  |  |  | 243 | 0.021614
48692 | GBY_81821075 | C | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108 | 0.60483 | 0.62638 |  |  |  |  | 244 | 0.021598
48693 | GBY_83841065 | F | Houston | YES | 0.00178 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.034273 | 54 | 54 |  |  |  |  | 0.034273 | 1.8507 | 0.60573 | 0.62726 |  |  |  |  | 245 | 0.021582
48693 | GBY_83841065 | E | Houston | YES | 0.00178 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.034273 | 57 | 57 |  |  |  |  | 0.034273 | 1.9536 | 0.60669 | 0.62819 |  |  |  |  | 246 | 0.021563
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.001772 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 | 0.60669 | 0.62819 |  |  |  |  | 247 | 0.021547
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.001772 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 | 0.60669 | 0.62819 |  |  |  |  | 248 | 0.021529
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.001772 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 | 0.60669 | 0.62819 |  |  |  |  | 249 | 0.021509
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.001772 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 | 0.60669 | 0.62819 |  |  |  |  | 250 | 0.021509
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.001767 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | 0.60669 | 0.62819 |  |  |  |  | 251 | 0.021509
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.001767 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | 0.60669 | 0.62819 |  |  |  |  | 252 | 0.021509
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.001767 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | 0.60669 | 0.62819 |  |  |  |  | 253 | 0.021509
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.001767 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | 0.60669 | 0.62819 |  |  |  |  | 254 | 0.021509
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.001767 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | 0.60669 | 0.62819 |  |  |  |  | 255 | 0.021509
48772 | PHR_GN2_2 | MB | Houston | YES | 0.001753 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.034246 | 0 | 0 |  |  |  |  | 0.034246 | 0 | 0.60669 | 0.62819 |  |  |  |  | 256 | 0.021509
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.001734 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 257 | 0.021509
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.001734 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 258 | 0.021509
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.001734 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 259 | 0.021509
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.001734 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 260 | 0.021509
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.001734 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 261 | 0.021509
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.001734 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 262 | 0.021509
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.001734 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 263 | 0.021509
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.001734 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 264 | 0.021509
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.001734 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 265 | 0.021509
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.001734 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 266 | 0.021509
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.001734 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 267 | 0.021509
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.001734 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 268 | 0.021509
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.001734 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 269 | 0.021509
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.001734 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 270 | 0.021509
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.001734 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | 0.60669 | 0.62819 |  |  |  |  | 271 | 0.021509
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.001693 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.034186 | 166 | 166 |  |  |  |  | 0.034186 | 5.6749 | 0.60945 | 0.6309 |  |  |  |  | 272 | 0.021509
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.001693 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.034186 | 166 | 166 |  |  |  |  | 0.034186 | 5.6749 | 0.61222 | 0.6336 |  |  |  |  | 273 | 0.021509
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.001693 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.034186 | 248 | 248 |  |  |  |  | 0.034186 | 8.4781 | 0.61636 | 0.63764 |  |  |  |  | 274 | 0.021509
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.001693 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.034186 | 546 | 546 |  |  |  |  | 0.034186 | 18.6655 | 0.62546 | 0.64654 |  |  |  |  | 275 | 0.021446
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.001693 | 585.3 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.034186 | 0 | 654 |  |  |  |  | 0.034186 | 22.3576 | 0.63637 | 0.65719 |  |  |  |  | 276 | 0.021383
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.001693 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.034186 | 13 | 13 |  |  |  |  | 0.034186 | 0.44442 | 0.63658 | 0.65741 |  |  |  |  | 277 | 0.021288
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.001685 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.034178 | 0 | 0 |  |  |  |  | 0.034178 | 0 | 0.63658 | 0.65741 |  |  |  |  | 278 | 0.02108
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.001679 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.034172 | 167.7 | 167.7 |  |  |  |  | 0.034172 | 5.7306 | 0.63938 | 0.66014 |  |  |  |  | 279 | 0.02083
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.001679 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.034172 | 166.4 | 166.4 |  |  |  |  | 0.034172 | 5.6862 | 0.64215 | 0.66285 |  |  |  |  | 280 | 0.020825
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.001679 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.034172 | 252.4 | 252.4 |  |  |  |  | 0.034172 | 8.625 | 0.64636 | 0.66696 |  |  |  |  | 281 | 0.020825
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.001679 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 651 |  |  |  |  | 0.034172 | 22.2459 | 0.65722 | 0.67756 |  |  |  |  | 282 | 0.02076
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.001679 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 564 |  |  |  |  | 0.034172 | 19.273 | 0.66662 | 0.68675 |  |  |  |  | 283 | 0.020695
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.001679 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 603 |  |  |  |  | 0.034172 | 20.6057 | 0.67668 | 0.69657 |  |  |  |  | 284 | 0.020597
48730 | MNS_GT | 1 | Houston | YES | 0.001674 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.034167 | 0 | 0 |  |  |  |  | 0.034167 | 0 | 0.67668 | 0.69657 |  |  |  |  | 285 | 0.020344
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.0016 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 | 0.67668 | 0.69657 |  |  |  |  | 286 | 0.020125
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.0016 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 | 0.67668 | 0.69657 |  |  |  |  | 287 | 0.019891
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.0016 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 | 0.67668 | 0.69657 |  |  |  |  | 288 | 0.019891
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.0016 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 | 0.67668 | 0.69657 |  |  |  |  | 289 | 0.019891
13432 | SANDOW_5G | 5 | South | YES | 0.001588 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.034081 | 0 | 581 |  |  |  |  | 0.034081 | 19.801 | 0.68636 | 0.706 |  |  |  |  | 290 | 0.019891
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.001577 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.03407 | 0 | 0 |  |  |  |  | 0.03407 | 0 | 0.68636 | 0.706 |  |  |  |  | 291 | 0.019891
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.001577 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.03407 | 0 | 0 |  |  |  |  | 0.03407 | 0 | 0.68636 | 0.706 |  |  |  |  | 292 | 0.019891
49851 | DOW17000 | 37 | Houston | YES | 0.001551 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 293 | 0.01964
49858 | DOW38100 | 31 | Houston | YES | 0.001551 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 294 | 0.01964
49859 | DOW38200 | 33 | Houston | YES | 0.001551 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 295 | 0.01964
49860 | DOW38300 | 32 | Houston | YES | 0.001551 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 296 | 0.01964
49862 | DOW39100 | 36 | Houston | YES | 0.001551 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 297 | 0.01964
49863 | DOW39200 | 35 | Houston | YES | 0.001551 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 298 | 0.01964
49865 | DOW41000 | 41 | Houston | YES | 0.001551 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 299 | 0.01964
49866 | DOW42000 | 42 | Houston | YES | 0.001551 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 300 | 0.01964
49869 | DOW49000 | 45 | Houston | YES | 0.001551 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 301 | 0.01964
49870 | DOW61000 | 61 | Houston | YES | 0.001551 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 302 | 0.01964
49871 | DOW62000 | 62 | Houston | YES | 0.001551 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 303 | 0.01964
49872 | DOW63000 | 63 | Houston | YES | 0.001551 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 304 | 0.01964
49873 | DOW64000 | 64 | Houston | YES | 0.001551 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 305 | 0.01964
49876 | DOW65000 | 65 | Houston | YES | 0.001551 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 306 | 0.01964
49877 | DOW66000 | 66 | Houston | YES | 0.001551 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 307 | 0.01964
49878 | DOW67000 | 67 | Houston | YES | 0.001551 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 308 | 0.01964
49882 | DOW81000 | 81 | Houston | YES | 0.001551 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 309 | 0.01964
49884 | DOW82000 | 82 | Houston | YES | 0.001551 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 310 | 0.01964
49885 | DOW83000 | 83 | Houston | YES | 0.001551 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 311 | 0.01964
49886 | DOW84000 | 84 | Houston | YES | 0.001551 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | 0.68636 | 0.706 |  |  |  |  | 312 | 0.01964
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.00144 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.033933 | 0 | 0 |  |  |  |  | 0.033933 | 0 | 0.68636 | 0.706 |  |  |  |  | 313 | 0.01964
48731 | CBE_GT1 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 | 0.68763 | 0.70723 |  |  |  |  | 314 | 0.01964
48732 | CBE_GT2 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 | 0.6889 | 0.70846 |  |  |  |  | 315 | 0.01964
48733 | CBE_ST12 | 1 | Houston | YES | 0.001422 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.033915 | 105 | 105 |  |  |  |  | 0.033915 | 3.5611 | 0.69065 | 0.71016 |  |  |  |  | 316 | 0.01964
48734 | CBE_GT3 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 | 0.69192 | 0.71139 |  |  |  |  | 317 | 0.019601
48735 | CBE_GT4 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 | 0.69318 | 0.71261 |  |  |  |  | 318 | 0.019562
48736 | CBE_ST34 | 1 | Houston | YES | 0.001422 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.033915 | 105 | 105 |  |  |  |  | 0.033915 | 3.5611 | 0.69493 | 0.71431 |  |  |  |  | 319 | 0.019509
3432 | SANDOW_4G | 4 | South | YES | 0.00141 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.033903 | 0 | 580 |  |  |  |  | 0.033903 | 19.6637 | 0.7046 | 0.72368 |  |  |  |  | 320 | 0.01947
5911 | STP_GN1___1 | 1 | Houston | YES | 0.001404 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.033897 | 0 | 0 |  |  |  |  | 0.033897 | 0 | 0.7046 | 0.72368 |  |  |  |  | 321 | 0.019431
5912 | STP_GN2___2 | 2 | Houston | YES | 0.001404 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.033897 | 0 | 0 |  |  |  |  | 0.033897 | 0 | 0.7046 | 0.72368 |  |  |  |  | 322 | 0.019377
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.001162 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.033655 | 158 | 158 |  |  |  |  | 0.033655 | 5.3175 | 0.70724 | 0.72622 |  |  |  |  | 323 | 0.019078
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.001162 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.033655 | 160 | 160 |  |  |  |  | 0.033655 | 5.3848 | 0.70991 | 0.72878 |  |  |  |  | 324 | 0.019078
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.001162 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.033655 | 175 | 175 |  |  |  |  | 0.033655 | 5.8896 | 0.71282 | 0.73159 |  |  |  |  | 325 | 0.019078
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.001162 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.033655 | 0 | 606 |  |  |  |  | 0.033655 | 20.3949 | 0.72293 | 0.74131 |  |  |  |  | 326 | 0.018977
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.001162 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.033655 | 0 | 598 |  |  |  |  | 0.033655 | 20.1257 | 0.7329 | 0.7509 |  |  |  |  | 327 | 0.018876
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.001161 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.033654 | 0 | 436 |  |  |  |  | 0.033654 | 14.6731 | 0.74017 | 0.75789 |  |  |  |  | 328 | 0.018765
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 | 0.741 | 0.75869 |  |  |  |  | 329 | 0.01838
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 | 0.74184 | 0.75949 |  |  |  |  | 330 | 0.018
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 | 0.74267 | 0.7603 |  |  |  |  | 331 | 0.017723
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 | 0.74351 | 0.7611 |  |  |  |  | 332 | 0.01769
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.001094 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.033587 | 152.5 | 152.5 |  |  |  |  | 0.033587 | 5.122 | 0.74605 | 0.76354 |  |  |  |  | 333 | 0.017657
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.001094 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.033587 | 149.5 | 149.5 |  |  |  |  | 0.033587 | 5.0213 | 0.74854 | 0.76593 |  |  |  |  | 334 | 0.017624
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.001094 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.033587 | 232.6 | 232.6 |  |  |  |  | 0.033587 | 7.8123 | 0.75242 | 0.76965 |  |  |  |  | 335 | 0.01759
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.001025 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.033518 | 132 | 132 |  |  |  |  | 0.033518 | 4.4244 | 0.75462 | 0.77176 |  |  |  |  | 336 | 0.017489
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.001025 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.033518 | 139 | 139 |  |  |  |  | 0.033518 | 4.659 | 0.75694 | 0.77398 |  |  |  |  | 337 | 0.017389
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.001025 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.033518 | 329 | 329 |  |  |  |  | 0.033518 | 11.0274 | 0.76242 | 0.77924 |  |  |  |  | 338 | 0.017234
8134 | FOR #1 | 1 | South | YES | 0.000958 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76242 | 0.77924 |  |  |  |  | 339 | 0.017141
8138 | FOR #2 | 2 | South | YES | 0.000958 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76242 | 0.77924 |  |  |  |  | 340 | 0.017044
8153 | FOR #3 | 3 | South | YES | 0.000958 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76242 | 0.77924 |  |  |  |  | 341 | 0.016814
8154 | FOR #4 | 4 | South | YES | 0.000958 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76242 | 0.77924 |  |  |  |  | 342 | 0.016814
8155 | FOR #5 | 5 | South | YES | 0.000958 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76242 | 0.77924 |  |  |  |  | 343 | 0.016814
8156 | FOR #6 | 6 | South | YES | 0.000958 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76242 | 0.77924 |  |  |  |  | 344 | 0.016814
8157 | FOR #7 | 7 | South | YES | 0.000958 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76242 | 0.77924 |  |  |  |  | 345 | 0.016814
9002 | DECKR_G3 | 3 | South | YES | 0.000958 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.033451 | 42 | 42 |  |  |  |  | 0.033451 | 1.4049 | 0.76312 | 0.77991 |  |  |  |  | 346 | 0.016814
9003 | DECKR_G4 | 4 | South | YES | 0.000958 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.033451 | 44 | 44 |  |  |  |  | 0.033451 | 1.4718 | 0.76386 | 0.78061 |  |  |  |  | 347 | 0.016814
9004 | DECKR_G5 | 5 | South | YES | 0.000958 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.033451 | 44 | 44 |  |  |  |  | 0.033451 | 1.4718 | 0.76459 | 0.78131 |  |  |  |  | 348 | 0.016814
9005 | DECKR_G6 | 6 | South | YES | 0.000958 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.033451 | 47 | 47 |  |  |  |  | 0.033451 | 1.5722 | 0.76538 | 0.78206 |  |  |  |  | 349 | 0.016783
80051 | FOR #8 | 8 | South | YES | 0.000958 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76538 | 0.78206 |  |  |  |  | 350 | 0.016751
80052 | FOR #9 | 9 | South | YES | 0.000958 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76538 | 0.78206 |  |  |  |  | 351 | 0.016718
80053 | FOR #10 | 10 | South | YES | 0.000958 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | 0.76538 | 0.78206 |  |  |  |  | 352 | 0.016684
80226 | ALCOA G | 1 | South | YES | 0.000945 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.033438 | 0 | 0 |  |  |  |  | 0.033438 | 0 | 0.76538 | 0.78206 |  |  |  |  | 353 | 0.016684
9000 | DECKR_G1 | 1 | South | YES | 0.000931 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.033424 | 321 | 321 |  |  |  |  | 0.033424 | 10.7291 | 0.77073 | 0.78717 |  |  |  |  | 354 | 0.016684
9001 | DECKR_G2 | 2 | South | YES | 0.000931 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.033424 | 426 | 426 |  |  |  |  | 0.033424 | 14.2386 | 0.77783 | 0.79396 |  |  |  |  | 355 | 0.016684
9016 | SANDH_G1 | 1 | South | YES | 0.00093 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.033423 | 49 | 49 |  |  |  |  | 0.033423 | 1.6377 | 0.77865 | 0.79474 |  |  |  |  | 356 | 0.016684
9017 | SANDH_G2 | 2 | South | YES | 0.00093 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.033423 | 46 | 46 |  |  |  |  | 0.033423 | 1.5375 | 0.77942 | 0.79547 |  |  |  |  | 357 | 0.016445
9018 | SANDH_G3 | 3 | South | YES | 0.00093 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.033423 | 46 | 46 |  |  |  |  | 0.033423 | 1.5375 | 0.78018 | 0.7962 |  |  |  |  | 358 | 0.016128
9019 | SANDH_G4 | 4 | South | YES | 0.00093 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.033423 | 47 | 47 |  |  |  |  | 0.033423 | 1.5709 | 0.78097 | 0.79695 |  |  |  |  | 359 | 0.016091
9020 | SANDHG5A | 5A | South | YES | 0.00093 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.033423 | 155 | 155 |  |  |  |  | 0.033423 | 5.1806 | 0.78355 | 0.79942 |  |  |  |  | 360 | 0.016057
9021 | SANDHG5C | 5C | South | YES | 0.00093 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.033423 | 148 | 148 |  |  |  |  | 0.033423 | 4.9466 | 0.78602 | 0.80178 |  |  |  |  | 361 | 0.016022
8147 | UCAR #2 | 10 | South | YES | 0.000895 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | 0.78602 | 0.80178 |  |  |  |  | 362 | 0.015987
8148 | UCAR #1 | 2 | South | YES | 0.000895 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | 0.78602 | 0.80178 |  |  |  |  | 363 | 0.015872
80137 | CSDR89 | 9 | South | YES | 0.000895 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | 0.78602 | 0.80178 |  |  |  |  | 364 | 0.015762
80137 | CSDR89 | 8 | South | YES | 0.000895 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | 0.78602 | 0.80178 |  |  |  |  | 365 | 0.015762
80138 | CSDR7 | 7 | South | YES | 0.000895 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | 0.78602 | 0.80178 |  |  |  |  | 366 | 0.015762
80139 | CSDR56 | 6 | South | YES | 0.000895 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | 0.78602 | 0.80178 |  |  |  |  | 367 | 0.015762
80139 | CSDR56 | 5 | South | YES | 0.000895 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | 0.78602 | 0.80178 |  |  |  |  | 368 | 0.015762
80140 | CSDR11 | 11 | South | YES | 0.000895 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | 0.78602 | 0.80178 |  |  |  |  | 369 | 0.015762
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.000891 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.033384 | 0 | 0 |  |  |  |  | 0.033384 | 0 | 0.78602 | 0.80178 |  |  |  |  | 370 | 0.015762
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.000891 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.033384 | 0 | 0 |  |  |  |  | 0.033384 | 0 | 0.78602 | 0.80178 |  |  |  |  | 371 | 0.015762
80227 | AIRCO G | 1 | South | YES | 0.000884 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.033377 | 0 | 0 |  |  |  |  | 0.033377 | 0 | 0.78602 | 0.80178 |  |  |  |  | 372 | 0.015762
80224 | VISTRONG1 | 1 | South | YES | 0.000882 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.033375 | 0 | 0 |  |  |  |  | 0.033375 | 0 | 0.78602 | 0.80178 |  |  |  |  | 373 | 0.015762
80225 | VISTRONG2 | 2 | South | YES | 0.000882 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.033375 | 0 | 0 |  |  |  |  | 0.033375 | 0 | 0.78602 | 0.80178 |  |  |  |  | 374 | 0.015762
8066 | DUP1V#1 | 1 | South | YES | 0.000866 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.033359 | 0 | 0 |  |  |  |  | 0.033359 | 0 | 0.78602 | 0.80178 |  |  |  |  | 375 | 0.015762
8173 | VICEC51A | 5 | South | YES | 0.000854 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.033347 | 144 | 144 |  |  |  |  | 0.033347 | 4.802 | 0.78842 | 0.80407 |  |  |  |  | 376 | 0.015762
8174 | VICEC61A | 6 | South | YES | 0.000854 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.033347 | 188 | 188 |  |  |  |  | 0.033347 | 6.2692 | 0.79155 | 0.80706 |  |  |  |  | 377 | 0.015762
5508 | RAYBURNCC9 | 1 | South | YES | 0.000848 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.033341 | 47.7 | 47.7 |  |  |  |  | 0.033341 | 1.5904 | 0.79235 | 0.80781 |  |  |  |  | 378 | 0.015762
5509 | RAYBURNCC10 | 1 | South | YES | 0.000848 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.033341 | 37.3 | 37.3 |  |  |  |  | 0.033341 | 1.2436 | 0.79297 | 0.80841 |  |  |  |  | 379 | 0.015649
5511 | RAYBURNCC7 | 1 | South | YES | 0.000848 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.033341 | 47.5 | 47.5 |  |  |  |  | 0.033341 | 1.5837 | 0.79376 | 0.80916 |  |  |  |  | 380 | 0.015502
5512 | RAYBURNCC8 | 1 | South | YES | 0.000848 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.033341 | 49.3 | 49.3 |  |  |  |  | 0.033341 | 1.6437 | 0.79459 | 0.80994 |  |  |  |  | 381 | 0.015465
5503 | RAYBURNGEN3 | 1 | South | YES | 0.000821 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.033314 | 22 | 22 |  |  |  |  | 0.033314 | 0.73291 | 0.79495 | 0.81029 |  |  |  |  | 382 | 0.015435
5505 | RAYBURNGEN1 | 1 | South | YES | 0.000821 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.033314 | 11 | 11 |  |  |  |  | 0.033314 | 0.36645 | 0.79514 | 0.81047 |  |  |  |  | 383 | 0.015398
5506 | RAYBURNGEN2 | 1 | South | YES | 0.000821 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.033314 | 11 | 11 |  |  |  |  | 0.033314 | 0.36645 | 0.79532 | 0.81064 |  |  |  |  | 384 | 0.015359
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.000821 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.033314 | 223.9 | 223.9 |  |  |  |  | 0.033314 | 7.459 | 0.79905 | 0.8142 |  |  |  |  | 385 | 0.015342
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.000821 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.033314 | 225 | 225 |  |  |  |  | 0.033314 | 7.4956 | 0.8028 | 0.81777 |  |  |  |  | 386 | 0.015333
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.000821 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.033314 | 224.6 | 224.6 |  |  |  |  | 0.033314 | 7.4823 | 0.80655 | 0.82134 |  |  |  |  | 387 | 0.015324
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.000821 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.033314 | 226.7 | 226.7 |  |  |  |  | 0.033314 | 7.5523 | 0.81033 | 0.82494 |  |  |  |  | 388 | 0.015146
8189 | CUECPL2A | 1 | South | YES | 0.000815 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.033308 | 0 | 0 |  |  |  |  | 0.033308 | 0 | 0.81033 | 0.82494 |  |  |  |  | 389 | 0.014966
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.00081 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.033303 | 0 | 0 |  |  |  |  | 0.033303 | 0 | 0.81033 | 0.82494 |  |  |  |  | 390 | 0.014787
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.00081 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.033303 | 0 | 0 |  |  |  |  | 0.033303 | 0 | 0.81033 | 0.82494
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.00079 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.033283 | 148 | 148 |  |  |  |  | 0.033283 | 4.9259 | 0.8128 | 0.82728
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.00079 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.033283 | 148 | 148 |  |  |  |  | 0.033283 | 4.9259 | 0.81526 | 0.82963
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.00079 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.033283 | 154 | 154 |  |  |  |  | 0.033283 | 5.1256 | 0.81783 | 0.83207
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.00079 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.033283 | 293 | 293 |  |  |  |  | 0.033283 | 9.7519 | 0.82272 | 0.83672
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.000769 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 | 0.82272 | 0.83672
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.000769 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 | 0.82272 | 0.83672
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.000769 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 | 0.82272 | 0.83672
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.000759 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.033252 | 147 | 147 |  |  |  |  | 0.033252 | 4.888 | 0.82517 | 0.83905
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.000759 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.033252 | 138 | 138 |  |  |  |  | 0.033252 | 4.5888 | 0.82747 | 0.84124
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.000759 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.033252 | 146 | 146 |  |  |  |  | 0.033252 | 4.8548 | 0.8299 | 0.84355
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.000759 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.033252 | 149 | 149 |  |  |  |  | 0.033252 | 4.9545 | 0.83239 | 0.84591
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.000759 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.033252 | 182 | 182 |  |  |  |  | 0.033252 | 6.0519 | 0.83542 | 0.8488
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.000759 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.033252 | 203 | 203 |  |  |  |  | 0.033252 | 6.7501 | 0.83881 | 0.85201
8161 | COLETO0A | 1 | South | YES | 0.000745 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.033238 | 0 | 633 |  |  |  |  | 0.033238 | 21.0396 | 0.84936 | 0.86204
8926 | LGE_GT10A | 1 | South | YES | 0.000739 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | 0.84936 | 0.86204
8927 | LGE_GT20A | 2 | South | YES | 0.000739 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | 0.84936 | 0.86204
8928 | LGE_STG0A | 3 | South | YES | 0.000739 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | 0.84936 | 0.86204
8930 | ICPGN10A | 1 | South | YES | 0.000739 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | 0.84936 | 0.86204
8931 | ICPGN20A | 2 | South | YES | 0.000739 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | 0.84936 | 0.86204
8932 | ICPGN30A | 3 | South | YES | 0.000739 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | 0.84936 | 0.86204
80223 | REYSHR G | 1 | South | YES | 0.000739 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | 0.84936 | 0.86204
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.000724 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.033217 | 0 | 0 |  |  |  |  | 0.033217 | 0 | 0.84936 | 0.86204
8442 | NBEC7 | 7 | South | YES | 0.000708 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.033201 | 367 | 367 |  |  |  |  | 0.033201 | 12.1848 | 0.85548 | 0.86785
8442 | NBEC7 | MB | South | YES | 0.000708 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.033201 | 0 | 0 |  |  |  |  | 0.033201 | 0 | 0.85548 | 0.86785
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.000707 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 | 0.85548 | 0.86785
8560 | CNOPGT1 | 1 | South | YES | 0.000707 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 | 0.85548 | 0.86785
8561 | CNOPGT2 | 2 | South | YES | 0.000707 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 | 0.85548 | 0.86785
8562 | CNOPST1 | 3 | South | YES | 0.000707 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 | 0.85548 | 0.86785
8456 | COSW#1 | 1 | South | YES | 0.000706 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.033199 | 0 | 0 |  |  |  |  | 0.033199 | 0 | 0.85548 | 0.86785
8457 | COSW#2 | 2 | South | YES | 0.000706 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.033199 | 0 | 0 |  |  |  |  | 0.033199 | 0 | 0.85548 | 0.86785
8459 | B_DAVIS0B | MB | South | YES | 0.000704 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.033197 | 0 | 0 |  |  |  |  | 0.033197 | 0 | 0.85548 | 0.86785
8460 | B_DAVIS0A | MB | South | YES | 0.000704 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.033197 | 0 | 0 |  |  |  |  | 0.033197 | 0 | 0.85548 | 0.86785
80263 | B_DAVIS31A | 3 | South | YES | 0.000704 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.033197 | 180 | 180 |  |  |  |  | 0.033197 | 5.9755 | 0.85848 | 0.8707
80264 | B_DAVIS41A | 4 | South | YES | 0.000704 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.033197 | 180 | 180 |  |  |  |  | 0.033197 | 5.9755 | 0.86149 | 0.87354
8506 | VAL #1 | 1 | South | YES | 0.000697 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 | 0.86149 | 0.87354
8507 | VAL #2 | 2 | South | YES | 0.000697 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 | 0.86149 | 0.87354
8511 | OXY_CC0A | 1 | South | YES | 0.000697 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 | 0.86149 | 0.87354
8461 | KOCH_UP0A | 1 | South | YES | 0.000693 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.033186 | 0 | 0 |  |  |  |  | 0.033186 | 0 | 0.86149 | 0.87354
80080 | GWINDT11A | 3 | South | YES | 0.000682 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 38 |  |  |  |  | 0.033175 | 1.2606 | 0.86212 | 0.87414
80080 | GWINDT11A | 4 | South | YES | 0.000682 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 19 |  |  |  |  | 0.033175 | 0.63032 | 0.86244 | 0.87444
80080 | GWINDT11A | 2 | South | YES | 0.000682 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 41 |  |  |  |  | 0.033175 | 1.3602 | 0.86312 | 0.87509
80080 | GWINDT11A | 1 | South | YES | 0.000682 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 94 |  |  |  |  | 0.033175 | 3.1184 | 0.86469 | 0.87658
80081 | GWINDT21A | 4 | South | YES | 0.000682 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 22 |  |  |  |  | 0.033175 | 0.72985 | 0.86505 | 0.87693
80081 | GWINDT21A | 1 | South | YES | 0.000682 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 94 |  |  |  |  | 0.033175 | 3.1184 | 0.86662 | 0.87841
80081 | GWINDT21A | 3 | South | YES | 0.000682 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 43 |  |  |  |  | 0.033175 | 1.4265 | 0.86734 | 0.87909
80081 | GWINDT21A | 2 | South | YES | 0.000682 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 36 |  |  |  |  | 0.033175 | 1.1943 | 0.86794 | 0.87966
80180 | PNSCALT11A | 2 | South | YES | 0.000682 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 50 |  |  |  |  | 0.033175 | 1.6587 | 0.86877 | 0.88045
80180 | PNSCALT11A | 1 | South | YES | 0.000682 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 148 |  |  |  |  | 0.033175 | 4.9099 | 0.87124 | 0.88279
80181 | PNSCALT21A | 2 | South | YES | 0.000682 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 50 |  |  |  |  | 0.033175 | 1.6587 | 0.87207 | 0.88358
80181 | PNSCALT21A | 1 | South | YES | 0.000682 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 55 |  |  |  |  | 0.033175 | 1.8246 | 0.87299 | 0.88445
8517 | CELANEBI0A | 1 | South | YES | 0.000679 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.033172 | 0 | 0 |  |  |  |  | 0.033172 | 0 | 0.87299 | 0.88445
5932 | SI_RAY9 | 9 | South | YES | 0.000665 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.033158 | 38 | 38 |  |  |  |  | 0.033158 | 1.26 | 0.87362 | 0.88505
5933 | SI_RAY6 | 6 | South | YES | 0.000665 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.033158 | 19.3 | 19.3 |  |  |  |  | 0.033158 | 0.63995 | 0.87395 | 0.88536
5935 | SI_RAY10 | 10 | South | YES | 0.000665 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.033158 | 47 | 47 |  |  |  |  | 0.033158 | 1.5584 | 0.87473 | 0.8861
80003 | MILHWYS | F | South | YES | 0.000665 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.033158 | 0 | 0 |  |  |  |  | 0.033158 | 0 | 0.87473 | 0.8861
5401 | CALAVER_JKS1 | 1 | South | YES | 0.000649 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.033142 | 0 | 562 |  |  |  |  | 0.033142 | 18.6258 | 0.8841 | 0.89498
8936 | MVGN#1 | 1 | South | YES | 0.000638 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.033131 | 216.6 | 216.6 |  |  |  |  | 0.033131 | 7.1762 | 0.88771 | 0.8984
8937 | MVGN#2 | 2 | South | YES | 0.000638 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.033131 | 216.7 | 216.7 |  |  |  |  | 0.033131 | 7.1795 | 0.89133 | 0.90182
8938 | MVGN#3 | 3 | South | YES | 0.000638 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.033131 | 250.9 | 250.9 |  |  |  |  | 0.033131 | 8.3126 | 0.89551 | 0.90578
8981 | HECN1 | 1 | South | YES | 0.000638 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.033131 | 144.8 | 144.8 |  |  |  |  | 0.033131 | 4.7974 | 0.89792 | 0.90807
8982 | HECN2 | 2 | South | YES | 0.000638 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.033131 | 144.1 | 144.1 |  |  |  |  | 0.033131 | 4.7742 | 0.90033 | 0.91034
8983 | HECN3 | 3 | South | YES | 0.000638 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.033131 | 171.9 | 171.9 |  |  |  |  | 0.033131 | 5.6952 | 0.90319 | 0.91306
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.00063 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.033123 | 155 | 155 |  |  |  |  | 0.033123 | 5.1341 | 0.90578 | 0.9155
5477 | BRA_AVR1_ST | 1 | South | YES | 0.00063 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.033123 | 174 | 174 |  |  |  |  | 0.033123 | 5.7634 | 0.90868 | 0.91825
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.00063 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.033123 | 155 | 155 |  |  |  |  | 0.033123 | 5.1341 | 0.91126 | 0.9207
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.000615 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.033108 | 61 | 61 |  |  |  |  | 0.033108 | 2.0196 | 0.91228 | 0.92166
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.000615 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.033108 | 95 | 95 |  |  |  |  | 0.033108 | 3.1453 | 0.91386 | 0.92316
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.000615 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.033108 | 151 | 151 |  |  |  |  | 0.033108 | 4.9993 | 0.91638 | 0.92554
5903 | SANMIGUELGEN | 1 | South | YES | 0.000611 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.033104 | 0 | 396.3 |  |  |  |  | 0.033104 | 13.1191 | 0.92299 | 0.93179
88198 | BEEVILLE | F | South | YES | 0.000577 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.03307 | 0 | 0 |  |  |  |  | 0.03307 | 0 | 0.92299 | 0.93179
5111 | CALAVER_JTD1 | 1 | South | YES | 0.000576 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.033069 | 0 | 430 |  |  |  |  | 0.033069 | 14.2197 | 0.93016 | 0.93857
5112 | CALAVER_JTD2 | 2 | South | YES | 0.000576 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.033069 | 0 | 430 |  |  |  |  | 0.033069 | 14.2197 | 0.93733 | 0.94535
8933 | FGNTS001 | 1 | South | YES | 0.000574 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.033067 | 146.5 | 146.5 |  |  |  |  | 0.033067 | 4.8443 | 0.93977 | 0.94766
8934 | FGNTS101 | 2 | South | YES | 0.000574 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.033067 | 147.9 | 147.9 |  |  |  |  | 0.033067 | 4.8906 | 0.94224 | 0.94999
8935 | FGNTS201 | 3 | South | YES | 0.000574 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.033067 | 173 | 173 |  |  |  |  | 0.033067 | 5.7206 | 0.94512 | 0.95271
5396 | CALAVER_OWS1 | 1 | South | YES | 0.000565 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.033058 | 418 | 418 |  |  |  |  | 0.033058 | 13.8182 | 0.95209 | 0.9593
5397 | CALAVER_OWS2 | 2 | South | YES | 0.000565 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.033058 | 400 | 400 |  |  |  |  | 0.033058 | 13.2232 | 0.95876 | 0.9656
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.000564 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.033057 | 215 | 215 |  |  |  |  | 0.033057 | 7.1072 | 0.96235 | 0.96899
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.000564 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.033057 | 216 | 216 |  |  |  |  | 0.033057 | 7.1403 | 0.96595 | 0.97239
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.000546 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.033039 | 407 | 407 |  |  |  |  | 0.033039 | 13.4469 | 0.97274 | 0.9788
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.000517 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 | 0.97274 | 0.9788
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.000517 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 | 0.97274 | 0.9788
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.000517 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 | 0.97274 | 0.9788
5264 | LEON_LCP3G3 | 3 | South | YES | 0.000486 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.032979 | 58 | 58 |  |  |  |  | 0.032979 | 1.9128 | 0.9737 | 0.97971
5265 | LEON_LCP4G4 | 4 | South | YES | 0.000486 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.032979 | 89 | 89 |  |  |  |  | 0.032979 | 2.9351 | 0.97519 | 0.98111
5266 | LEON_LCPCT1 | 1 | South | YES | 0.000486 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.032979 | 44 | 44 |  |  |  |  | 0.032979 | 1.4511 | 0.97592 | 0.9818
5267 | LEON_LCPCT2 | 2 | South | YES | 0.000486 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.032979 | 44 | 44 |  |  |  |  | 0.032979 | 1.4511 | 0.97665 | 0.98249
5268 | LEON_LCPCT3 | 3 | South | YES | 0.000486 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.032979 | 43 | 43 |  |  |  |  | 0.032979 | 1.4181 | 0.97737 | 0.98317
5269 | LEON_LCPCT4 | 4 | South | YES | 0.000486 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.032979 | 45 | 45 |  |  |  |  | 0.032979 | 1.4841 | 0.97812 | 0.98388
88508 | FALFURRI | F | South | YES | 0.000253 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.032746 | 0 | 0 |  |  |  |  | 0.032746 | 0 | 0.97812 | 0.98388
5728 | FALCONHYDRO2 | 2 | South | YES | 0.000195 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 | 0.97812 | 0.98388
5729 | FALCONHYDRO3 | 3 | South | YES | 0.000195 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 | 0.97812 | 0.98388
8048 | FALCONHYDRO1 | 1 | South | YES | 0.000195 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 | 0.97812 | 0.98388
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.032493 | 15 | 15 |  |  |  |  | 0.032493 | 0.48739 | 0.97837 | 0.98411
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | 0.97837 | 0.98411
88299 | ZAPATA | F | South | YES | -0.000168 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.032325 | 0 | 0 |  |  |  |  | 0.032325 | 0 | 0.97837 | 0.98411
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.000264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.032229 | 0 | 0 |  |  |  |  | 0.032229 | 0 | 0.97837 | 0.98411
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.000264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.032229 | 0 | 0 |  |  |  |  | 0.032229 | 0 | 0.97837 | 0.98411
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.000551 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.031942 | 0 | 0 |  |  |  |  | 0.031942 | 0 | 0.97837 | 0.98411
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.000551 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.031942 | 0 | 0 |  |  |  |  | 0.031942 | 0 | 0.97837 | 0.98411
5890 | PEARSALLGEN1 | 1 | South | YES | -0.000627 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.031866 | 24 | 24 |  |  |  |  | 0.031866 | 0.76478 | 0.97877 | 0.98447
5891 | PEARSALLGEN2 | 1 | South | YES | -0.000627 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.031866 | 24.3 | 24.3 |  |  |  |  | 0.031866 | 0.77434 | 0.97918 | 0.98484
5892 | PEARSALLGEN3 | 1 | South | YES | -0.000627 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.031866 | 23.9 | 23.9 |  |  |  |  | 0.031866 | 0.7616 | 0.97958 | 0.9852
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.000641 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.031852 | 423.3 | 423.3 |  |  |  |  | 0.031852 | 13.4829 | 0.98663 | 0.99163
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.00068 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 | 0.98663 | 0.99163
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.00068 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 | 0.98663 | 0.99163
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.00068 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 | 0.98663 | 0.99163
80012 | LAR | F | South | YES | -0.000702 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.031791 | 0 | 0 |  |  |  |  | 0.031791 | 0 | 0.98663 | 0.99163
80265 | LARECU40A | 4 | South | YES | -0.000703 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.03179 | 100 | 100 |  |  |  |  | 0.03179 | 3.179 | 0.9883 | 0.99315
80266 | LARECU50A | 5 | South | YES | -0.000703 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.03179 | 100 | 100 |  |  |  |  | 0.03179 | 3.179 | 0.98997 | 0.99466
58909 | PEARSALLSCG1 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99011 | 0.99479
58909 | PEARSALLSCG1 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99025 | 0.99491
58909 | PEARSALLSCG1 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99039 | 0.99504
58909 | PEARSALLSCG1 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99053 | 0.99517
58909 | PEARSALLSCG1 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99067 | 0.99529
58909 | PEARSALLSCG1 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99081 | 0.99542
58919 | PEARSALLSCG2 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99095 | 0.99554
58919 | PEARSALLSCG2 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99109 | 0.99567
58919 | PEARSALLSCG2 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99123 | 0.9958
58919 | PEARSALLSCG2 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99137 | 0.99592
58919 | PEARSALLSCG2 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99151 | 0.99605
58919 | PEARSALLSCG2 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99165 | 0.99617
58929 | PEARSALLSCG3 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99179 | 0.9963
58929 | PEARSALLSCG3 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99193 | 0.99643
58929 | PEARSALLSCG3 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99207 | 0.99655
58929 | PEARSALLSCG3 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99221 | 0.99668
58929 | PEARSALLSCG3 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99235 | 0.99681
58929 | PEARSALLSCG3 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99249 | 0.99693
58949 | PEARSALLSCG4 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99263 | 0.99706
58949 | PEARSALLSCG4 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99277 | 0.99718
58949 | PEARSALLSCG4 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99291 | 0.99731
58949 | PEARSALLSCG4 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99305 | 0.99744
58949 | PEARSALLSCG4 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99319 | 0.99756
58949 | PEARSALLSCG4 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | 0.99333 | 0.99769
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.001227 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.031266 | 0 | 0 |  |  |  |  | 0.031266 | 0 | 0.99333 | 0.99769
8262 | ELPS | 1 | South | YES | -0.006198 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.026295 | 0 | 0 |  |  |  |  | 0.026295 | 0 | 0.99333 | 0.99769
8032 | AMISTADHYD1 | 1 | South | YES | -0.008717 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 | 0.99333 | 0.99769
8033 | AMISTADHYD2 | 2 | South | YES | -0.008717 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 | 0.99333 | 0.99769
88253 | HAMILTON | F | South | YES | -0.008717 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 | 0.99333 | 0.99769
1437 | MESQUITW_1G | 1 | North | YES | -0.020371 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.012122 | 0 | 400 | -8.1484 | 400 |  |  | 0.012122 | 4.8488 | 1 | 1
1438 | MESQUITW_2G | 1 | North | YES | -0.020392 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.012101 | 0 | 236 | -4.8125 | 236 |  |  | 0.012101 | 2.8558 | 1.0039 | 1.0014
6100 | OKLA7A | EQ | West | YES | -0.01742 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.021055 | 0 | 0 |  |  | 0 | 0 | -0.021055 | 0
6752 | OKLA0A | 1 | West | YES | -0.01742 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.021055 | 0 | 649.7 |  |  | 0 | 0 | -0.021055 | 0
11056 | ROSCOE_1G | 1 | West | YES | -0.025191 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.028826 | 0 | 209 |  |  | 0 | 0 | -0.028826 | 0
11057 | CHAMPION_1G | 1 | West | YES | -0.025191 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.028826 | 0 | 126.5 |  |  | 0 | 0 | -0.028826 | 0
11058 | PYRON_1G | 1 | West | YES | -0.025191 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.028826 | 0 | 249 |  |  | 0 | 0 | -0.028826 | 0
11059 | INADALE_1G | 1 | West | YES | -0.025191 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.028826 | 0 | 197 |  |  | 0 | 0 | -0.028826 | 0
60202 | FRNDDRCS | F | West | YES | -0.025875 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.02951 | 0 | 0 |  |  | 0 | 0 | -0.02951 | 0
1416 | SWETWATR_1G | 1 | West | YES | -0.026126 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.029761 | 30 | 30 |  |  | -0.78378 | 30 | -0.029761 | -0.89284
1417 | SWETWATR_2G | 2 | West | YES | -0.026126 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.029761 | 72 | 72 |  |  | -1.8811 | 72 | -0.029761 | -2.1428
1418 | SWETWATR_3G | 3 | West | YES | -0.026126 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.029761 | 68 | 68 |  |  | -1.7766 | 68 | -0.029761 | -2.0238
1419 | SWETWATR_4G | 4 | West | YES | -0.026126 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.029761 | 61 | 61 |  |  | -1.5937 | 61 | -0.029761 | -1.8154
60058 | BUFF_GAP1A | 1 | West | YES | -0.026615 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.03025 | 0 | 120 |  |  | 0 | 0 | -0.03025 | 0
60060 | CIRELLO | 1 | West | YES | -0.026615 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.03025 | 0 | 233 |  |  | 0 | 0 | -0.03025 | 0
60063 | BUFF_GAP1B | 1 | West | YES | -0.026615 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.03025 | 0 | 170.2 |  |  | 0 | 0 | -0.03025 | 0
60066 | H_HOLLOW1A | 1 | West | YES | -0.026615 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.03025 | 0 | 222 |  |  | 0 | 0 | -0.03025 | 0
60068 | HHOLLOW21A | 1 | West | YES | -0.026615 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 184 |  |  | 0 | 0 | -0.03025 | 0
60070 | HHOLLOW31A | 1 | West | YES | -0.026615 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 224 |  |  | 0 | 0 | -0.03025 | 0
60072 | HHOLLOW41A | 1 | West | YES | -0.026615 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 115 |  |  | 0 | 0 | -0.03025 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.027538 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.031173 | 0 | 112.5 |  |  | 0 | 0 | -0.031173 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.027538 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 149.5 |  |  | 0 | 0 | -0.031173 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.027538 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 186 |  |  | 0 | 0 | -0.031173 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.027538 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 214.5 |  |  | 0 | 0 | -0.031173 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | -0.027909 | 30 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.031544 | 0 | 150 |  |  | 0 | 0 | -0.031544 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | -0.028811 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 37.5 |  |  | 0 | 0 | -0.032446 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | -0.028811 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 107.5 |  |  | 0 | 0 | -0.032446 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | -0.028811 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 135 |  |  | 0 | 0 | -0.032446 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | -0.028811 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 119 |  |  | 0 | 0 | -0.032446 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | -0.028811 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 105 |  |  | 0 | 0 | -0.032446 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | -0.028811 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 80.5 |  |  | 0 | 0 | -0.032446 | 0
60000 | DSKY2 | 1 | West | YES | -0.029087 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.032722 | 0 | 76.5 |  |  | 0 | 0 | -0.032722 | 0
60018 | DSKY1 | 1 | West | YES | -0.029123 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.032758 | 0 | 84 |  |  | 0 | 0 | -0.032758 | 0
60017 | ORNNWP1 | 1 | West | YES | -0.029339 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.032974 | 0 | 80 |  |  | 0 | 0 | -0.032974 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | -0.02998 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.033615 | 0 | 150 |  |  | 0 | 0 | -0.033615 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.03 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.033635 | 0 | 80 |  |  | 0 | 0 | -0.033635 | 0
60016 | WOODWRD11A | 1 | West | YES | -0.030004 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.033639 | 0 | 80 |  |  | 0 | 0 | -0.033639 | 0
6016 | SWMESA | 1 | West | YES | -0.030023 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.033658 | 0 | 75 |  |  | 0 | 0 | -0.033658 | 0
60003 | KING_NE1A | 1 | West | YES | -0.030023 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033658 | 0 | 80 |  |  | 0 | 0 | -0.033658 | 0
60005 | KING_SE1A | 1 | West | YES | -0.030023 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.033658 | 0 | 40 |  |  | 0 | 0 | -0.033658 | 0
60201 | RIO DRCS | F | West | YES | -0.030065 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.0337 | 0 | 0 |  |  | 0 | 0 | -0.0337 | 0
1058 | LONGSHORE_5 | 1 | West | YES | -0.030077 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.033712 | 0 | 150 |  |  | 0 | 0 | -0.033712 | 0
1058 | LONGSHORE_5 | 2 | West | YES | -0.030077 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.033712 | 0 | 220 |  |  | 0 | 0 | -0.033712 | 0
11065 | ELBOWCK_1G | 1 | West | YES | -0.030077 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.033712 | 0 | 121.9 |  |  | 0 | 0 | -0.033712 | 0
60007 | KING_SW1A | 1 | West | YES | -0.030138 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033773 | 0 | 80 |  |  | 0 | 0 | -0.033773 | 0
60019 | KING_NW1A | 1 | West | YES | -0.030138 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033773 | 0 | 80 |  |  | 0 | 0 | -0.033773 | 0
1045 | CALENG1G_1G | 1 | West | YES | -0.030406 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0
1046 | CALENG2G_2G | 2 | West | YES | -0.030406 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0
1047 | CALENG3G_3G | 3 | West | YES | -0.030406 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0
11001 | NAV1CT | 1 | West | YES | -0.031081 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.034716 | 70.4 | 70.4 |  |  | -2.1881 | 70.4 | -0.034716 | -2.444
11009 | NAV2CT | 1 | West | YES | -0.031081 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.034716 | 71.4 | 71.4 |  |  | -2.2192 | 71.4 | -0.034716 | -2.4788
11011 | NAV3ST | 1 | West | YES | -0.031081 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.034716 | 92.8 | 92.8 |  |  | -2.8843 | 92.8 | -0.034716 | -3.2217
11012 | NAV4CT | 1 | West | YES | -0.031081 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.034716 | 80 | 80 |  |  | -2.4865 | 80 | -0.034716 | -2.7773
11013 | NAV5CT | 1 | West | YES | -0.031081 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.034716 | 80 | 80 |  |  | -2.4865 | 80 | -0.034716 | -2.7773
11014 | NAV6ST | 1 | West | YES | -0.031081 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.034716 | 115 | 115 |  |  | -3.5743 | 115 | -0.034716 | -3.9924
11020 | TIEHVSG_1G | 1 | West | YES | -0.031092 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.034727 | 208.2 | 208.2 |  |  | -6.4734 | 208.2 | -0.034727 | -7.2303
11021 | TIEHVCG_1G | 1 | West | YES | -0.031092 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.034727 | 142.1 | 142.1 |  |  | -4.4182 | 142.1 | -0.034727 | -4.9348
11022 | TIEHVCG_2G | 1 | West | YES | -0.031092 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.034727 | 132.4 | 132.4 |  |  | -4.1166 | 132.4 | -0.034727 | -4.5979
11023 | TIEHVCG_3G | 1 | West | YES | -0.031092 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.034727 | 137.4 | 137.4 |  |  | -4.272 | 137.4 | -0.034727 | -4.7716
11024 | TIEHVCG_4G | 1 | West | YES | -0.031092 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.034727 | 147 | 147 |  |  | -4.5705 | 147 | -0.034727 | -5.1049
11025 | TIEHVSG_2G | 1 | West | YES | -0.031092 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.034727 | 213.2 | 213.2 |  |  | -6.6288 | 213.2 | -0.034727 | -7.4039
1002 | PBCTAGE_1G | A | West | YES | -0.032158 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.035793 | 66 | 66 |  |  | -2.1224 | 66 | -0.035793 | -2.3624
1003 | PBCTBGE_2G | B | West | YES | -0.032158 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.035793 | 66 | 66 |  |  | -2.1224 | 66 | -0.035793 | -2.3624
1004 | PBCTCGE_3G | C | West | YES | -0.032158 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.035793 | 67 | 67 |  |  | -2.1546 | 67 | -0.035793 | -2.3982
1005 | PBCTDGE_4G | D | West | YES | -0.032158 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.035793 | 68 | 68 |  |  | -2.1867 | 68 | -0.035793 | -2.434
1006 | PBCTEGE_5G | E | West | YES | -0.032158 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.035793 | 67 | 67 |  |  | -2.1546 | 67 | -0.035793 | -2.3982
1007 | PB5GEN_6G | 5 | West | YES | -0.032158 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.035793 | 114 | 114 |  |  | -3.666 | 114 | -0.035793 | -4.0805
1008 | PB6GEN_7G | 6 | West | YES | -0.032158 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.035793 | 515 | 515 |  |  | -16.5614 | 515 | -0.035793 | -18.4336
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.032489 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.036124 | 0 | 35 |  |  | 0 | 0 | -0.036124 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.032489 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.036124 | 0 | 30 |  |  | 0 | 0 | -0.036124 | 0
11147 | NOTREES_1G | 1 | West | YES | -0.033214 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.036849 | 0 | 149 |  |  | 0 | 0 | -0.036849 | 0
1326 | STANTONW_8 | 1 | West | YES | -0.035681 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.039316 | 0 | 100.5 |  |  | 0 | 0 | -0.039316 | 0
1328 | OCOTILLO_1G | 1 | West | YES | -0.037855 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.04149 | 0 | 58 |  |  | 0 | 0 | -0.04149 | 0
1349 | WESTXWIN_1G | 1 | West | YES | -0.038494 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.042129 | 0 | 6.6 |  |  | 0 | 0 | -0.042129 | 0
1350 | NWPWRG1_1G | 1 | West | YES | -0.038494 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.042129 | 0 | 34.3 |  |  | 0 | 0 | -0.042129 | 0
1333 | MCDDONAL_8 | 1 | West | YES | -0.038529 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.042164 | 0 | 214.2 |  |  | 0 | 0 | -0.042164 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.039546 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.043181 | 137 | 137 |  |  | -5.4178 | 137 | -0.043181 | -5.9159
1039 | MRGNAG_1G | A | West | YES | -0.039546 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.043181 | 69 | 69 |  |  | -2.7287 | 69 | -0.043181 | -2.9795
1040 | MRGNBG_2G | B | West | YES | -0.039546 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.043181 | 71 | 71 |  |  | -2.8078 | 71 | -0.043181 | -3.0659
1041 | MRGNCG_3G | C | West | YES | -0.039546 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.043181 | 70 | 70 |  |  | -2.7682 | 70 | -0.043181 | -3.0227
1042 | MRGNDG_4G | D | West | YES | -0.039546 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.043181 | 68 | 68 |  |  | -2.6891 | 68 | -0.043181 | -2.9363
1043 | MRGNEG_5G | E | West | YES | -0.039546 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.043181 | 70 | 70 |  |  | -2.7682 | 70 | -0.043181 | -3.0227
1044 | MRGNFG_6G | F | West | YES | -0.039546 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.043181 | 66 | 66 |  |  | -2.61 | 66 | -0.043181 | -2.85
1320 | BSP 1 | 1 | West | YES | -0.040237 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.043872 | 0 | 0 |  |  | 0 | 0 | -0.043872 | 0
1327 | WILDHRSE_1G | 1 | West | YES | -0.042121 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.045756 | 0 | 120 |  |  | 0 | 0 | -0.045756 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.043637 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.047272 | 0 | 120 |  |  | 0 | 0 | -0.047272 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.048542 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.052177 | 0 | 225 |  |  | 0 | 0 | -0.052177 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.049265 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.0529 | 0 | 180 |  |  | 0 | 0 | -0.0529 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.049265 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.0529 | 0 | 180 |  |  | 0 | 0 | -0.0529 | 0
6637 | SNYDERW1A | 1 | West | YES | -0.053701 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.057336 | 0 | 63 |  |  | 0 | 0 | -0.057336 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.05733 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.060965 | 0 | 141 |  |  | 0 | 0 | -0.060965 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.05733 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.060965 | 0 | 120 |  |  | 0 | 0 | -0.060965 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.057618 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.061253 | 0 | 99 |  |  | 0 | 0 | -0.061253 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.057618 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.061253 | 0 | 61 |  |  | 0 | 0 | -0.061253 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.057618 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.057618 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.057618 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.065277 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | -1 | 0.068912 | 0 | 114 |  |  | 0 | 0 | -0.068912 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.066301 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.069936 | 0 | 150 |  |  | 0 | 0 | -0.069936 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.066301 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.069936 | 0 | 101 |  |  | 0 | 0 | -0.069936 | 0
36998 | RDCNYNG1 | 1 | West | YES | -0.068089 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.071724 | 0 | 84 |  |  | 0 | 0 | -0.071724 | 0
6407 | TURKTRAK1A | 1 | West | YES | -0.077309 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.080944 | 0 | 169.5 |  |  | 0 | 0 | -0.080944 | 0
6144 | MCADOO1A | 1 | West | YES | -0.11402 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.11765 | 0 | 150 |  |  | 0 | 0 | -0.11765 | 0
60081 | WHRLWIND1A | 1 | West | YES | -0.13083 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.13446 | 0 | 60 |  |  | 0 | 0 | -0.13446 | 0
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ LonCrek2_5 to CokField_5 OL_ Murry to Paint |  | i_PTDF_INC_pt | 102 |  | MRGNFG_6G | Unit at max
60081 | WHRLWIND1A | 1 | West | YES | -0.13083 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.13446 | 0 | 60 |  |  | 0 | 0 | -0.13446 | 0 | 0 | 0 |  |  | i_10pctunit | 25 |  | 28 | # units @ max
6144 | MCADOO1A | 1 | West | YES | -0.11402 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.11765 | 0 | 150 |  |  | 0 | 0 | -0.11765 | 0 | 0 | 0 | [5 empty] | 0.033252 | delta max
6407 | TURKTRAK1A | 1 | West | YES | -0.077309 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.080944 | 0 | 169.5 |  |  | 0 | 0 | -0.080944 | 0 | 0 | 0 | [5 empty] | Delta
36998 | RDCNYNG1 | 1 | West | YES | -0.068089 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.071724 | 0 | 84 |  |  | 0 | 0 | -0.071724 | 0 | 0 | 0 | Weighted Shift Factors |  |  |  | 1 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.066301 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.069936 | 0 | 150 |  |  | 0 | 0 | -0.069936 | 0 | 0 | 0 | North | 0.0036354 |  |  | 2 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.066301 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.069936 | 0 | 101 |  |  | 0 | 0 | -0.069936 | 0 | 0 | 0 | West | -0.032493 |  |  | 3 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.065277 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | -1 | 0.068912 | 0 | 114 |  |  | 0 | 0 | -0.068912 | 0 | 0 | 0 |  |  |  |  | 4 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.057618 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.061253 | 0 | 99 |  |  | 0 | 0 | -0.061253 | 0 | 0 | 0 |  |  |  |  | 5 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.057618 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.061253 | 0 | 61 |  |  | 0 | 0 | -0.061253 | 0 | 0 | 0 |  |  |  |  | 6 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.057618 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0 | 0 | 0 |  |  |  |  | 7 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.057618 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0 | 0 | 0 |  |  |  |  | 8 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.057618 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0 | 0 | 0 |  |  |  |  | 9 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.05733 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.060965 | 0 | 141 |  |  | 0 | 0 | -0.060965 | 0 | 0 | 0 |  |  |  |  | 10 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.05733 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.060965 | 0 | 120 |  |  | 0 | 0 | -0.060965 | 0 | 0 | 0 |  |  |  |  | 11 | 0
6637 | SNYDERW1A | 1 | West | YES | -0.053701 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.057336 | 0 | 63 |  |  | 0 | 0 | -0.057336 | 0 | 0 | 0 |  |  |  |  | 12 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.049265 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.0529 | 0 | 180 |  |  | 0 | 0 | -0.0529 | 0 | 0 | 0 |  |  |  |  | 13 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.049265 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.0529 | 0 | 180 |  |  | 0 | 0 | -0.0529 | 0 | 0 | 0 |  |  |  |  | 14 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.048542 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.052177 | 0 | 225 |  |  | 0 | 0 | -0.052177 | 0 | 0 | 0 |  |  |  |  | 15 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.043637 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.047272 | 0 | 120 |  |  | 0 | 0 | -0.047272 | 0 | 0 | 0 |  |  |  |  | 16 | 0
1327 | WILDHRSE_1G | 1 | West | YES | -0.042121 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.045756 | 0 | 120 |  |  | 0 | 0 | -0.045756 | 0 | 0 | 0 |  |  |  |  | 17 | 0
1320 | BSP 1 | 1 | West | YES | -0.040237 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.043872 | 0 | 0 |  |  | 0 | 0 | -0.043872 | 0 | 0 | 0 |  |  |  |  | 18 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.039546 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.043181 | 137 | 137 |  |  | -5.4178 | 137 | -0.043181 | -5.9159 | 0.042351 | 0.050618 |  |  |  |  | 19 | 0
1039 | MRGNAG_1G | A | West | YES | -0.039546 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.043181 | 69 | 69 |  |  | -2.7287 | 69 | -0.043181 | -2.9795 | 0.06368 | 0.076112 |  |  |  |  | 20 | 0
1040 | MRGNBG_2G | B | West | YES | -0.039546 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.043181 | 71 | 71 |  |  | -2.8078 | 71 | -0.043181 | -3.0659 | 0.085629 | 0.10235 |  |  |  |  | 21 | 0
1041 | MRGNCG_3G | C | West | YES | -0.039546 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.043181 | 70 | 70 |  |  | -2.7682 | 70 | -0.043181 | -3.0227 | 0.10727 | 0.12821 |  |  |  |  | 22 | 0.0082678
1042 | MRGNDG_4G | D | West | YES | -0.039546 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.043181 | 68 | 68 |  |  | -2.6891 | 68 | -0.043181 | -2.9363 | 0.12829 | 0.15333 |  |  |  |  | 23 | 0.012432
1043 | MRGNEG_5G | E | West | YES | -0.039546 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.043181 | 70 | 70 |  |  | -2.7682 | 70 | -0.043181 | -3.0227 | 0.14993 | 0.1792 |  |  |  |  | 24 | 0.016717
1044 | MRGNFG_6G | F | West | YES | -0.039546 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.043181 | 66 | 66 |  |  | -2.61 | 66 | -0.043181 | -2.85 | 0.17033 | 0.20358 |  |  |  |  | 25 | 0.020941
1333 | MCDDONAL_8 | 1 | West | YES | -0.038529 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.042164 | 0 | 214.2 |  |  | 0 | 0 | -0.042164 | 0 | 0.17033 | 0.20358 |  |  |  |  | 26 | 0.025045
1349 | WESTXWIN_1G | 1 | West | YES | -0.038494 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.042129 | 0 | 6.6 |  |  | 0 | 0 | -0.042129 | 0 | 0.17033 | 0.20358 |  |  |  |  | 27 | 0.029269
1350 | NWPWRG1_1G | 1 | West | YES | -0.038494 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.042129 | 0 | 34.3 |  |  | 0 | 0 | -0.042129 | 0 | 0.17033 | 0.20358 |  |  |  |  | 28 | 0.033252
1328 | OCOTILLO_1G | 1 | West | YES | -0.037855 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.04149 | 0 | 58 |  |  | 0 | 0 | -0.04149 | 0 | 0.17033 | 0.20358 |  |  |  |  | 29 | 0.033252
1326 | STANTONW_8 | 1 | West | YES | -0.035681 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.039316 | 0 | 100.5 |  |  | 0 | 0 | -0.039316 | 0 | 0.17033 | 0.20358 |  |  |  |  | 30 | 0.033252
11147 | NOTREES_1G | 1 | West | YES | -0.033214 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.036849 | 0 | 149 |  |  | 0 | 0 | -0.036849 | 0 | 0.17033 | 0.20358 |  |  |  |  | 31 | 0.033252
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.032489 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.036124 | 0 | 35 |  |  | 0 | 0 | -0.036124 | 0 | 0.17033 | 0.20358 |  |  |  |  | 32 | 0.033252
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.032489 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.036124 | 0 | 30 |  |  | 0 | 0 | -0.036124 | 0 | 0.17033 | 0.20358 |  |  |  |  | 33 | 0.033252
1002 | PBCTAGE_1G | A | West | YES | -0.032158 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.035793 | 66 | 66 |  |  | -2.1224 | 66 | -0.035793 | -2.3624 | 0.19073 | 0.2238 |  |  |  |  | 34 | 0.033252
1003 | PBCTBGE_2G | B | West | YES | -0.032158 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.035793 | 66 | 66 |  |  | -2.1224 | 66 | -0.035793 | -2.3624 | 0.21113 | 0.24401 |  |  |  |  | 35 | 0.033252
1004 | PBCTCGE_3G | C | West | YES | -0.032158 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.035793 | 67 | 67 |  |  | -2.1546 | 67 | -0.035793 | -2.3982 | 0.23185 | 0.26453 |  |  |  |  | 36 | 0.033252
1005 | PBCTDGE_4G | D | West | YES | -0.032158 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.035793 | 68 | 68 |  |  | -2.1867 | 68 | -0.035793 | -2.434 | 0.25287 | 0.28535 |  |  |  |  | 37 | 0.033063
1006 | PBCTEGE_5G | E | West | YES | -0.032158 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.035793 | 67 | 67 |  |  | -2.1546 | 67 | -0.035793 | -2.3982 | 0.27358 | 0.30587 |  |  |  |  | 38 | 0.032874
1007 | PB5GEN_6G | 5 | West | YES | -0.032158 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.035793 | 114 | 114 |  |  | -3.666 | 114 | -0.035793 | -4.0805 | 0.30882 | 0.34079 |  |  |  |  | 39 | 0.032682
1008 | PB6GEN_7G | 6 | West | YES | -0.032158 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.035793 | 515 | 515 |  |  | -16.5614 | 515 | -0.035793 | -18.4336 | 0.46802 | 0.49851 |  |  |  |  | 40 | 0.032487
11020 | TIEHVSG_1G | 1 | West | YES | -0.031092 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.034727 | 208.2 | 208.2 |  |  | -6.4734 | 208.2 | -0.034727 | -7.2303 | 0.53238 | 0.56038 |  |  |  |  | 41 | 0.032295
11021 | TIEHVCG_1G | 1 | West | YES | -0.031092 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.034727 | 142.1 | 142.1 |  |  | -4.4182 | 142.1 | -0.034727 | -4.9348 | 0.57631 | 0.6026 |  |  |  |  | 42 | 0.031968
11022 | TIEHVCG_2G | 1 | West | YES | -0.031092 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.034727 | 132.4 | 132.4 |  |  | -4.1166 | 132.4 | -0.034727 | -4.5979 | 0.61724 | 0.64194 |  |  |  |  | 43 | 0.030492
11023 | TIEHVCG_3G | 1 | West | YES | -0.031092 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.034727 | 137.4 | 137.4 |  |  | -4.272 | 137.4 | -0.034727 | -4.7716 | 0.65971 | 0.68277 |  |  |  |  | 44 | 0.027996
11024 | TIEHVCG_4G | 1 | West | YES | -0.031092 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.034727 | 147 | 147 |  |  | -4.5705 | 147 | -0.034727 | -5.1049 | 0.70515 | 0.72645 |  |  |  |  | 45 | 0.026293
11025 | TIEHVSG_2G | 1 | West | YES | -0.031092 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.034727 | 213.2 | 213.2 |  |  | -6.6288 | 213.2 | -0.034727 | -7.4039 | 0.77106 | 0.7898 |  |  |  |  | 46 | 0.024706
11001 | NAV1CT | 1 | West | YES | -0.031081 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.034716 | 70.4 | 70.4 |  |  | -2.1881 | 70.4 | -0.034716 | -2.444 | 0.79282 | 0.81071 |  |  |  |  | 47 | 0.023059
11009 | NAV2CT | 1 | West | YES | -0.031081 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.034716 | 71.4 | 71.4 |  |  | -2.2192 | 71.4 | -0.034716 | -2.4788 | 0.81489 | 0.83192 |  |  |  |  | 48 | 0.021297
11011 | NAV3ST | 1 | West | YES | -0.031081 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.034716 | 92.8 | 92.8 |  |  | -2.8843 | 92.8 | -0.034716 | -3.2217 | 0.84358 | 0.85949 |  |  |  |  | 49 | 0.018741
11012 | NAV4CT | 1 | West | YES | -0.031081 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.034716 | 80 | 80 |  |  | -2.4865 | 80 | -0.034716 | -2.7773 | 0.86831 | 0.88325 |  |  |  |  | 50 | 0.017891
11013 | NAV5CT | 1 | West | YES | -0.031081 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.034716 | 80 | 80 |  |  | -2.4865 | 80 | -0.034716 | -2.7773 | 0.89304 | 0.90702 |  |  |  |  | 51 | 0.017028
11014 | NAV6ST | 1 | West | YES | -0.031081 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.034716 | 115 | 115 |  |  | -3.5743 | 115 | -0.034716 | -3.9924 | 0.92859 | 0.94118 |  |  |  |  | 52 | 0.015907
1045 | CALENG1G_1G | 1 | West | YES | -0.030406 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0 | 0.92859 | 0.94118 |  |  |  |  | 53 | 0.01494
1046 | CALENG2G_2G | 2 | West | YES | -0.030406 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0 | 0.92859 | 0.94118 |  |  |  |  | 54 | 0.013974
1047 | CALENG3G_3G | 3 | West | YES | -0.030406 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0 | 0.92859 | 0.94118 |  |  |  |  | 55 | 0.012584
60007 | KING_SW1A | 1 | West | YES | -0.030138 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033773 | 0 | 80 |  |  | 0 | 0 | -0.033773 | 0 | 0.92859 | 0.94118 |  |  |  |  | 56 | 0.012584
60019 | KING_NW1A | 1 | West | YES | -0.030138 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033773 | 0 | 80 |  |  | 0 | 0 | -0.033773 | 0 | 0.92859 | 0.94118 |  |  |  |  | 57 | 0.012584
1058 | LONGSHORE_5 | 1 | West | YES | -0.030077 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.033712 | 0 | 150 |  |  | 0 | 0 | -0.033712 | 0 | 0.92859 | 0.94118 |  |  |  |  | 58 | 0.012584
1058 | LONGSHORE_5 | 2 | West | YES | -0.030077 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.033712 | 0 | 220 |  |  | 0 | 0 | -0.033712 | 0 | 0.92859 | 0.94118 |  |  |  |  | 59 | 0.012584
11065 | ELBOWCK_1G | 1 | West | YES | -0.030077 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.033712 | 0 | 121.9 |  |  | 0 | 0 | -0.033712 | 0 | 0.92859 | 0.94118 |  |  |  |  | 60 | 0.012584
60201 | RIO DRCS | F | West | YES | -0.030065 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.0337 | 0 | 0 |  |  | 0 | 0 | -0.0337 | 0 | 0.92859 | 0.94118 |  |  |  |  | 61 | 0.012584
6016 | SWMESA | 1 | West | YES | -0.030023 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.033658 | 0 | 75 |  |  | 0 | 0 | -0.033658 | 0 | 0.92859 | 0.94118 |  |  |  |  | 62 | 0.012584
60003 | KING_NE1A | 1 | West | YES | -0.030023 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033658 | 0 | 80 |  |  | 0 | 0 | -0.033658 | 0 | 0.92859 | 0.94118 |  |  |  |  | 63 | 0.012584
60005 | KING_SE1A | 1 | West | YES | -0.030023 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.033658 | 0 | 40 |  |  | 0 | 0 | -0.033658 | 0 | 0.92859 | 0.94118 |  |  |  |  | 64 | 0.012584
60016 | WOODWRD11A | 1 | West | YES | -0.030004 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.033639 | 0 | 80 |  |  | 0 | 0 | -0.033639 | 0 | 0.92859 | 0.94118 |  |  |  |  | 65 | 0.012584
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.03 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.033635 | 0 | 80 |  |  | 0 | 0 | -0.033635 | 0 | 0.92859 | 0.94118 |  |  |  |  | 66 | 0.012584
38437 | TNSRBNMESA9 | 1 | West | YES | -0.02998 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.033615 | 0 | 150 |  |  | 0 | 0 | -0.033615 | 0 | 0.92859 | 0.94118 |  |  |  |  | 67 | 0.012584
60017 | ORNNWP1 | 1 | West | YES | -0.029339 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.032974 | 0 | 80 |  |  | 0 | 0 | -0.032974 | 0 | 0.92859 | 0.94118 |  |  |  |  | 68 | 0.012584
60018 | DSKY1 | 1 | West | YES | -0.029123 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.032758 | 0 | 84 |  |  | 0 | 0 | -0.032758 | 0 | 0.92859 | 0.94118 |  |  |  |  | 69 | 0.012584
60000 | DSKY2 | 1 | West | YES | -0.029087 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.032722 | 0 | 76.5 |  |  | 0 | 0 | -0.032722 | 0 | 0.92859 | 0.94118 |  |  |  |  | 70 | 0.012584
71051 | L_BITTCR1_1N | W1 | West | YES | -0.028811 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 37.5 |  |  | 0 | 0 | -0.032446 | 0 | 0.92859 | 0.94118 |  |  |  |  | 71 | 0.012584
71054 | L_SWEETW1_1N | W1 | West | YES | -0.028811 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 107.5 |  |  | 0 | 0 | -0.032446 | 0 | 0.92859 | 0.94118 |  |  |  |  | 72 | 0.012584
71057 | L_SWEETW1_2N | W1 | West | YES | -0.028811 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 135 |  |  | 0 | 0 | -0.032446 | 0 | 0.92859 | 0.94118 |  |  |  |  | 73 | 0.012584
71059 | L_SWEETW1_3N | W1 | West | YES | -0.028811 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 119 |  |  | 0 | 0 | -0.032446 | 0 | 0.92859 | 0.94118 |  |  |  |  | 74 | 0.012584
71060 | L_SWEETW1_4N | W1 | West | YES | -0.028811 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 105 |  |  | 0 | 0 | -0.032446 | 0 | 0.92859 | 0.94118 |  |  |  |  | 75 | 0.012584
71061 | L_SWEETW1_5N | W1 | West | YES | -0.028811 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 80.5 |  |  | 0 | 0 | -0.032446 | 0 | 0.92859 | 0.94118 |  |  |  |  | 76 | 0.012584
76031 | L_GASCCR1_1N | W1 | West | YES | -0.027909 | 30 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.031544 | 0 | 150 |  |  | 0 | 0 | -0.031544 | 0 | 0.92859 | 0.94118 |  |  |  |  | 77 | 0.012584
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.027538 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.031173 | 0 | 112.5 |  |  | 0 | 0 | -0.031173 | 0 | 0.92859 | 0.94118 |  |  |  |  | 78 | 0.012584
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.027538 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 149.5 |  |  | 0 | 0 | -0.031173 | 0 | 0.92859 | 0.94118 |  |  |  |  | 79 | 0.012584
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.027538 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 186 |  |  | 0 | 0 | -0.031173 | 0 | 0.92859 | 0.94118 |  |  |  |  | 80 | 0.012584
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.027538 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 214.5 |  |  | 0 | 0 | -0.031173 | 0 | 0.92859 | 0.94118 |  |  |  |  | 81 | 0.012584
60058 | BUFF_GAP1A | 1 | West | YES | -0.026615 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.03025 | 0 | 120 |  |  | 0 | 0 | -0.03025 | 0 | 0.92859 | 0.94118 |  |  |  |  | 82 | 0.012584
60060 | CIRELLO | 1 | West | YES | -0.026615 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.03025 | 0 | 233 |  |  | 0 | 0 | -0.03025 | 0 | 0.92859 | 0.94118 |  |  |  |  | 83 | 0.012584
60063 | BUFF_GAP1B | 1 | West | YES | -0.026615 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.03025 | 0 | 170.2 |  |  | 0 | 0 | -0.03025 | 0 | 0.92859 | 0.94118 |  |  |  |  | 84 | 0.012584
60066 | H_HOLLOW1A | 1 | West | YES | -0.026615 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.03025 | 0 | 222 |  |  | 0 | 0 | -0.03025 | 0 | 0.92859 | 0.94118 |  |  |  |  | 85 | 0.012584
60068 | HHOLLOW21A | 1 | West | YES | -0.026615 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 184 |  |  | 0 | 0 | -0.03025 | 0 | 0.92859 | 0.94118 |  |  |  |  | 86 | 0.012584
60070 | HHOLLOW31A | 1 | West | YES | -0.026615 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 224 |  |  | 0 | 0 | -0.03025 | 0 | 0.92859 | 0.94118 |  |  |  |  | 87 | 0.012584
60072 | HHOLLOW41A | 1 | West | YES | -0.026615 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 115 |  |  | 0 | 0 | -0.03025 | 0 | 0.92859 | 0.94118 |  |  |  |  | 88 | 0.012584
1416 | SWETWATR_1G | 1 | West | YES | -0.026126 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.029761 | 30 | 30 |  |  | -0.78378 | 30 | -0.029761 | -0.89284 | 0.93787 | 0.94882 |  |  |  |  | 89 | 0.012584
1417 | SWETWATR_2G | 2 | West | YES | -0.026126 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.029761 | 72 | 72 |  |  | -1.8811 | 72 | -0.029761 | -2.1428 | 0.96012 | 0.96715 |  |  |  |  | 90 | 0.012584
1418 | SWETWATR_3G | 3 | West | YES | -0.026126 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.029761 | 68 | 68 |  |  | -1.7766 | 68 | -0.029761 | -2.0238 | 0.98114 | 0.98447 |  |  |  |  | 91 | 0.012584
1419 | SWETWATR_4G | 4 | West | YES | -0.026126 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.029761 | 61 | 61 |  |  | -1.5937 | 61 | -0.029761 | -1.8154 | 1 | 1 |  |  |  |  | 92 | 0.01095
60202 | FRNDDRCS | F | West | YES | -0.025875 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.02951 | 0 | 0 |  |  | 0 | 0 | -0.02951 | 0 | 1 | 1 |  |  |  |  | 93 | 0.0070277
11056 | ROSCOE_1G | 1 | West | YES | -0.025191 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.028826 | 0 | 209 |  |  | 0 | 0 | -0.028826 | 0 | 1 | 1 |  |  |  |  | 94 | 0.0033232
11057 | CHAMPION_1G | 1 | West | YES | -0.025191 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.028826 | 0 | 126.5 |  |  | 0 | 0 | -0.028826 | 0 | 1 | 1 |  |  |  |  | 95 | 0
11058 | PYRON_1G | 1 | West | YES | -0.025191 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.028826 | 0 | 249 |  |  | 0 | 0 | -0.028826 | 0 | 1 | 1 |  |  |  |  | 96 | 0
11059 | INADALE_1G | 1 | West | YES | -0.025191 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.028826 | 0 | 197 |  |  | 0 | 0 | -0.028826 | 0 | 1 | 1 |  |  |  |  | 97 | 0
6100 | OKLA7A | EQ | West | YES | -0.01742 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.021055 | 0 | 0 |  |  | 0 | 0 | -0.021055 | 0 | 1 | 1 |  |  |  |  | 98 | 0
6752 | OKLA0A | 1 | West | YES | -0.01742 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.021055 | 0 | 649.7 |  |  | 0 | 0 | -0.021055 | 0 | 1 | 1 |  |  |  |  | 99 | 0
1438 | MESQUITW_2G | 1 | North | YES | -0.020392 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.012101 | 0 | 236 | -4.8125 | 236 |  |  | 0.012101 | 2.8558 | [6 empty] | 100 | 0
1437 | MESQUITW_1G | 1 | North | YES | -0.020371 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.012122 | 0 | 400 | -8.1484 | 400 |  |  | 0.012122 | 4.8488 | [6 empty] | 101 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.008717 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 | [6 empty] | 102 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.008717 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 | [6 empty] | 103 | 0
88253 | HAMILTON | F | South | YES | -0.008717 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 | [6 empty] | 104 | 0
8262 | ELPS | 1 | South | YES | -0.006198 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.026295 | 0 | 0 |  |  |  |  | 0.026295 | 0 | [6 empty] | 105 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.001227 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.031266 | 0 | 0 |  |  |  |  | 0.031266 | 0 | [6 empty] | 106 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 107 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 108 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 109 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 110 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 111 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 112 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 113 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 114 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 115 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 116 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 117 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 118 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 119 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 120 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 121 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 122 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 123 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 124 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 125 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 126 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 127 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 128 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 129 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 | [6 empty] | 130 | 0
80265 | LARECU40A | 4 | South | YES | -0.000703 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.03179 | 100 | 100 |  |  |  |  | 0.03179 | 3.179 | [6 empty] | 131 | 0
80266 | LARECU50A | 5 | South | YES | -0.000703 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.03179 | 100 | 100 |  |  |  |  | 0.03179 | 3.179 | [6 empty] | 132 | 0
80012 | LAR | F | South | YES | -0.000702 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.031791 | 0 | 0 |  |  |  |  | 0.031791 | 0 | [6 empty] | 133 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.00068 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 | [6 empty] | 134 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.00068 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 | [6 empty] | 135 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.00068 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 | [6 empty] | 136 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.000641 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.031852 | 423.3 | 423.3 |  |  |  |  | 0.031852 | 13.4829 | [6 empty] | 137 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.000627 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.031866 | 24 | 24 |  |  |  |  | 0.031866 | 0.76478 | [6 empty] | 138 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.000627 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.031866 | 24.3 | 24.3 |  |  |  |  | 0.031866 | 0.77434 | [6 empty] | 139 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.000627 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.031866 | 23.9 | 23.9 |  |  |  |  | 0.031866 | 0.7616 | [6 empty] | 140 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.000551 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.031942 | 0 | 0 |  |  |  |  | 0.031942 | 0 | [6 empty] | 141 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.000551 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.031942 | 0 | 0 |  |  |  |  | 0.031942 | 0 | [6 empty] | 142 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.000264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.032229 | 0 | 0 |  |  |  |  | 0.032229 | 0 | [6 empty] | 143 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.000264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.032229 | 0 | 0 |  |  |  |  | 0.032229 | 0 | [6 empty] | 144 | 0
88299 | ZAPATA | F | South | YES | -0.000168 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.032325 | 0 | 0 |  |  |  |  | 0.032325 | 0 | [6 empty] | 145 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.032493 | 15 | 15 |  |  |  |  | 0.032493 | 0.48739 | [6 empty] | 146 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 147 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 148 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 149 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 150 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 151 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 152 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 153 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 154 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 | [6 empty] | 155 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | 0.000195 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 | [6 empty] | 156 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 0.000195 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 | [6 empty] | 157 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 0.000195 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 | [6 empty] | 158 | 0
88508 | FALFURRI | F | South | YES | 0.000253 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.032746 | 0 | 0 |  |  |  |  | 0.032746 | 0 | [6 empty] | 159 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | 0.000486 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.032979 | 58 | 58 |  |  |  |  | 0.032979 | 1.9128 | [6 empty] | 160 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | 0.000486 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.032979 | 89 | 89 |  |  |  |  | 0.032979 | 2.9351 | [6 empty] | 161 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | 0.000486 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.032979 | 44 | 44 |  |  |  |  | 0.032979 | 1.4511 | [6 empty] | 162 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | 0.000486 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.032979 | 44 | 44 |  |  |  |  | 0.032979 | 1.4511 | [6 empty] | 163 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | 0.000486 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.032979 | 43 | 43 |  |  |  |  | 0.032979 | 1.4181 | [6 empty] | 164 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | 0.000486 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.032979 | 45 | 45 |  |  |  |  | 0.032979 | 1.4841 | [6 empty] | 165 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.000517 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 | [6 empty] | 166 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.000517 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 | [6 empty] | 167 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.000517 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 | [6 empty] | 168 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.000546 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.033039 | 407 | 407 |  |  |  |  | 0.033039 | 13.4469 | [6 empty] | 169 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.000564 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.033057 | 215 | 215 |  |  |  |  | 0.033057 | 7.1072 | [6 empty] | 170 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.000564 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.033057 | 216 | 216 |  |  |  |  | 0.033057 | 7.1403 | [6 empty] | 171 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | 0.000565 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.033058 | 418 | 418 |  |  |  |  | 0.033058 | 13.8182 | [6 empty] | 172 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | 0.000565 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.033058 | 400 | 400 |  |  |  |  | 0.033058 | 13.2232 | [6 empty] | 173 | 0
8933 | FGNTS001 | 1 | South | YES | 0.000574 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.033067 | 146.5 | 146.5 |  |  |  |  | 0.033067 | 4.8443 | [6 empty] | 174 | 0
8934 | FGNTS101 | 2 | South | YES | 0.000574 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.033067 | 147.9 | 147.9 |  |  |  |  | 0.033067 | 4.8906 | [6 empty] | 175 | 0
8935 | FGNTS201 | 3 | South | YES | 0.000574 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.033067 | 173 | 173 |  |  |  |  | 0.033067 | 5.7206 | [6 empty] | 176 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | 0.000576 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.033069 | 0 | 430 |  |  |  |  | 0.033069 | 14.2197 | [6 empty] | 177 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | 0.000576 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.033069 | 0 | 430 |  |  |  |  | 0.033069 | 14.2197 | [6 empty] | 178 | 0
88198 | BEEVILLE | F | South | YES | 0.000577 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.03307 | 0 | 0 |  |  |  |  | 0.03307 | 0 | [6 empty] | 179 | 0
5903 | SANMIGUELGEN | 1 | South | YES | 0.000611 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.033104 | 0 | 396.3 |  |  |  |  | 0.033104 | 13.1191 | [6 empty] | 180 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.000615 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.033108 | 61 | 61 |  |  |  |  | 0.033108 | 2.0196 | [6 empty] | 181 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.000615 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.033108 | 95 | 95 |  |  |  |  | 0.033108 | 3.1453 | [6 empty] | 182 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.000615 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.033108 | 151 | 151 |  |  |  |  | 0.033108 | 4.9993 | [6 empty] | 183 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.00063 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.033123 | 155 | 155 |  |  |  |  | 0.033123 | 5.1341 | [6 empty] | 184 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | 0.00063 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.033123 | 174 | 174 |  |  |  |  | 0.033123 | 5.7634 | [6 empty] | 185 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.00063 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.033123 | 155 | 155 |  |  |  |  | 0.033123 | 5.1341 | [6 empty] | 186 | 0
8936 | MVGN#1 | 1 | South | YES | 0.000638 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.033131 | 216.6 | 216.6 |  |  |  |  | 0.033131 | 7.1762 | [6 empty] | 187 | 0
8937 | MVGN#2 | 2 | South | YES | 0.000638 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.033131 | 216.7 | 216.7 |  |  |  |  | 0.033131 | 7.1795 | [6 empty] | 188 | 0
8938 | MVGN#3 | 3 | South | YES | 0.000638 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.033131 | 250.9 | 250.9 |  |  |  |  | 0.033131 | 8.3126 | [6 empty] | 189 | 0
8981 | HECN1 | 1 | South | YES | 0.000638 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.033131 | 144.8 | 144.8 |  |  |  |  | 0.033131 | 4.7974 | [6 empty] | 190 | 0
8982 | HECN2 | 2 | South | YES | 0.000638 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.033131 | 144.1 | 144.1 |  |  |  |  | 0.033131 | 4.7742 | [6 empty] | 191 | 0
8983 | HECN3 | 3 | South | YES | 0.000638 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.033131 | 171.9 | 171.9 |  |  |  |  | 0.033131 | 5.6952 | [6 empty] | 192 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | 0.000649 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.033142 | 0 | 562 |  |  |  |  | 0.033142 | 18.6258 | [6 empty] | 193 | 0
5932 | SI_RAY9 | 9 | South | YES | 0.000665 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.033158 | 38 | 38 |  |  |  |  | 0.033158 | 1.26 | [6 empty] | 194 | 0
5933 | SI_RAY6 | 6 | South | YES | 0.000665 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.033158 | 19.3 | 19.3 |  |  |  |  | 0.033158 | 0.63995 | [6 empty] | 195 | 0
5935 | SI_RAY10 | 10 | South | YES | 0.000665 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.033158 | 47 | 47 |  |  |  |  | 0.033158 | 1.5584 | [6 empty] | 196 | 0
80003 | MILHWYS | F | South | YES | 0.000665 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.033158 | 0 | 0 |  |  |  |  | 0.033158 | 0 | [6 empty] | 197 | 0
8517 | CELANEBI0A | 1 | South | YES | 0.000679 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.033172 | 0 | 0 |  |  |  |  | 0.033172 | 0 | [6 empty] | 198 | 0
80080 | GWINDT11A | 3 | South | YES | 0.000682 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 38 |  |  |  |  | 0.033175 | 1.2606 | [6 empty] | 199 | 0
80080 | GWINDT11A | 4 | South | YES | 0.000682 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 19 |  |  |  |  | 0.033175 | 0.63032 | [6 empty] | 200 | 0
80080 | GWINDT11A | 2 | South | YES | 0.000682 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 41 |  |  |  |  | 0.033175 | 1.3602 | [6 empty] | 201 | 0
80080 | GWINDT11A | 1 | South | YES | 0.000682 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 94 |  |  |  |  | 0.033175 | 3.1184 | [6 empty] | 202 | 0
80081 | GWINDT21A | 4 | South | YES | 0.000682 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 22 |  |  |  |  | 0.033175 | 0.72985 | [6 empty] | 203 | 0
80081 | GWINDT21A | 1 | South | YES | 0.000682 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 94 |  |  |  |  | 0.033175 | 3.1184 | [6 empty] | 204 | 0
80081 | GWINDT21A | 3 | South | YES | 0.000682 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 43 |  |  |  |  | 0.033175 | 1.4265 | [6 empty] | 205 | 0
80081 | GWINDT21A | 2 | South | YES | 0.000682 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 36 |  |  |  |  | 0.033175 | 1.1943 | [6 empty] | 206 | 0
80180 | PNSCALT11A | 2 | South | YES | 0.000682 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 50 |  |  |  |  | 0.033175 | 1.6587 | [6 empty] | 207 | 0
80180 | PNSCALT11A | 1 | South | YES | 0.000682 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 148 |  |  |  |  | 0.033175 | 4.9099 | [6 empty] | 208 | 0
80181 | PNSCALT21A | 2 | South | YES | 0.000682 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 50 |  |  |  |  | 0.033175 | 1.6587 | [6 empty] | 209 | 0
80181 | PNSCALT21A | 1 | South | YES | 0.000682 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 55 |  |  |  |  | 0.033175 | 1.8246 | [6 empty] | 210 | 0
8461 | KOCH_UP0A | 1 | South | YES | 0.000693 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.033186 | 0 | 0 |  |  |  |  | 0.033186 | 0 | [6 empty] | 211 | 0
8506 | VAL #1 | 1 | South | YES | 0.000697 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 | [6 empty] | 212 | 0
8507 | VAL #2 | 2 | South | YES | 0.000697 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 | [6 empty] | 213 | 0
8511 | OXY_CC0A | 1 | South | YES | 0.000697 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 | [6 empty] | 214 | 0
8459 | B_DAVIS0B | MB | South | YES | 0.000704 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.033197 | 0 | 0 |  |  |  |  | 0.033197 | 0 | [6 empty] | 215 | 0
8460 | B_DAVIS0A | MB | South | YES | 0.000704 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.033197 | 0 | 0 |  |  |  |  | 0.033197 | 0 | [6 empty] | 216 | 0
80263 | B_DAVIS31A | 3 | South | YES | 0.000704 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.033197 | 180 | 180 |  |  |  |  | 0.033197 | 5.9755 | [6 empty] | 217 | 0
80264 | B_DAVIS41A | 4 | South | YES | 0.000704 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.033197 | 180 | 180 |  |  |  |  | 0.033197 | 5.9755 | [6 empty] | 218 | 0
8456 | COSW#1 | 1 | South | YES | 0.000706 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.033199 | 0 | 0 |  |  |  |  | 0.033199 | 0 | [6 empty] | 219 | 0
8457 | COSW#2 | 2 | South | YES | 0.000706 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.033199 | 0 | 0 |  |  |  |  | 0.033199 | 0 | [6 empty] | 220 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.000707 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 | [6 empty] | 221 | 0
8560 | CNOPGT1 | 1 | South | YES | 0.000707 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 | [6 empty] | 222 | 0
8561 | CNOPGT2 | 2 | South | YES | 0.000707 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 | [6 empty] | 223 | 0
8562 | CNOPST1 | 3 | South | YES | 0.000707 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 | [6 empty] | 224 | 0
8442 | NBEC7 | 7 | South | YES | 0.000708 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.033201 | 367 | 367 |  |  |  |  | 0.033201 | 12.1848 | [6 empty] | 225 | 0
8442 | NBEC7 | MB | South | YES | 0.000708 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.033201 | 0 | 0 |  |  |  |  | 0.033201 | 0 | [6 empty] | 226 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.000724 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.033217 | 0 | 0 |  |  |  |  | 0.033217 | 0 | [6 empty] | 227 | 0
8926 | LGE_GT10A | 1 | South | YES | 0.000739 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | [6 empty] | 228 | 0
8927 | LGE_GT20A | 2 | South | YES | 0.000739 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | [6 empty] | 229 | 0
8928 | LGE_STG0A | 3 | South | YES | 0.000739 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | [6 empty] | 230 | 0
8930 | ICPGN10A | 1 | South | YES | 0.000739 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | [6 empty] | 231 | 0
8931 | ICPGN20A | 2 | South | YES | 0.000739 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | [6 empty] | 232 | 0
8932 | ICPGN30A | 3 | South | YES | 0.000739 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | [6 empty] | 233 | 0
80223 | REYSHR G | 1 | South | YES | 0.000739 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 | [6 empty] | 234 | 0
8161 | COLETO0A | 1 | South | YES | 0.000745 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.033238 | 0 | 633 |  |  |  |  | 0.033238 | 21.0396 | [6 empty] | 235 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.000759 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.033252 | 147 | 147 |  |  |  |  | 0.033252 | 4.888 | [6 empty] | 236 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.000759 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.033252 | 138 | 138 |  |  |  |  | 0.033252 | 4.5888 | [6 empty] | 237 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.000759 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.033252 | 146 | 146 |  |  |  |  | 0.033252 | 4.8548 | [6 empty] | 238 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.000759 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.033252 | 149 | 149 |  |  |  |  | 0.033252 | 4.9545 | [6 empty] | 239 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.000759 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.033252 | 182 | 182 |  |  |  |  | 0.033252 | 6.0519 | [6 empty] | 240 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.000759 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.033252 | 203 | 203 |  |  |  |  | 0.033252 | 6.7501 | [6 empty] | 241 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.000769 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 | [6 empty] | 242 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.000769 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 | [6 empty] | 243 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.000769 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 | [6 empty] | 244 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.00079 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.033283 | 148 | 148 |  |  |  |  | 0.033283 | 4.9259 | [6 empty] | 245 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.00079 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.033283 | 148 | 148 |  |  |  |  | 0.033283 | 4.9259 | [6 empty] | 246 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.00079 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.033283 | 154 | 154 |  |  |  |  | 0.033283 | 5.1256 | [6 empty] | 247 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.00079 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.033283 | 293 | 293 |  |  |  |  | 0.033283 | 9.7519 | [6 empty] | 248 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.00081 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.033303 | 0 | 0 |  |  |  |  | 0.033303 | 0 | [6 empty] | 249 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.00081 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.033303 | 0 | 0 |  |  |  |  | 0.033303 | 0 | [6 empty] | 250 | 0
8189 | CUECPL2A | 1 | South | YES | 0.000815 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.033308 | 0 | 0 |  |  |  |  | 0.033308 | 0 | [6 empty] | 251 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | 0.000821 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.033314 | 22 | 22 |  |  |  |  | 0.033314 | 0.73291 | [6 empty] | 252 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | 0.000821 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.033314 | 11 | 11 |  |  |  |  | 0.033314 | 0.36645 | [6 empty] | 253 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | 0.000821 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.033314 | 11 | 11 |  |  |  |  | 0.033314 | 0.36645 | [6 empty] | 254 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.000821 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.033314 | 223.9 | 223.9 |  |  |  |  | 0.033314 | 7.459 | [6 empty] | 255 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.000821 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.033314 | 225 | 225 |  |  |  |  | 0.033314 | 7.4956 | [6 empty] | 256 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.000821 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.033314 | 224.6 | 224.6 |  |  |  |  | 0.033314 | 7.4823 | [6 empty] | 257 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.000821 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.033314 | 226.7 | 226.7 |  |  |  |  | 0.033314 | 7.5523 | [6 empty] | 258 | 0
5508 | RAYBURNCC9 | 1 | South | YES | 0.000848 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.033341 | 47.7 | 47.7 |  |  |  |  | 0.033341 | 1.5904 | [6 empty] | 259 | 0
5509 | RAYBURNCC10 | 1 | South | YES | 0.000848 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.033341 | 37.3 | 37.3 |  |  |  |  | 0.033341 | 1.2436 | [6 empty] | 260 | 0
5511 | RAYBURNCC7 | 1 | South | YES | 0.000848 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.033341 | 47.5 | 47.5 |  |  |  |  | 0.033341 | 1.5837 | [6 empty] | 261 | 0
5512 | RAYBURNCC8 | 1 | South | YES | 0.000848 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.033341 | 49.3 | 49.3 |  |  |  |  | 0.033341 | 1.6437 | [6 empty] | 262 | 0
8173 | VICEC51A | 5 | South | YES | 0.000854 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.033347 | 144 | 144 |  |  |  |  | 0.033347 | 4.802 | [6 empty] | 263 | 0
8174 | VICEC61A | 6 | South | YES | 0.000854 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.033347 | 188 | 188 |  |  |  |  | 0.033347 | 6.2692 | [6 empty] | 264 | 0
8066 | DUP1V#1 | 1 | South | YES | 0.000866 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.033359 | 0 | 0 |  |  |  |  | 0.033359 | 0 | [6 empty] | 265 | 0
80224 | VISTRONG1 | 1 | South | YES | 0.000882 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.033375 | 0 | 0 |  |  |  |  | 0.033375 | 0 | [6 empty] | 266 | 0
80225 | VISTRONG2 | 2 | South | YES | 0.000882 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.033375 | 0 | 0 |  |  |  |  | 0.033375 | 0 | [6 empty] | 267 | 0
80227 | AIRCO G | 1 | South | YES | 0.000884 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.033377 | 0 | 0 |  |  |  |  | 0.033377 | 0 | [6 empty] | 268 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.000891 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.033384 | 0 | 0 |  |  |  |  | 0.033384 | 0 | [6 empty] | 269 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.000891 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.033384 | 0 | 0 |  |  |  |  | 0.033384 | 0 | [6 empty] | 270 | 0
8147 | UCAR #2 | 10 | South | YES | 0.000895 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | [6 empty] | 271 | 0
8148 | UCAR #1 | 2 | South | YES | 0.000895 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | [6 empty] | 272 | 0
80137 | CSDR89 | 9 | South | YES | 0.000895 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | [6 empty] | 273 | 0
80137 | CSDR89 | 8 | South | YES | 0.000895 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | [6 empty] | 274 | 0
80138 | CSDR7 | 7 | South | YES | 0.000895 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | [6 empty] | 275 | 0
80139 | CSDR56 | 6 | South | YES | 0.000895 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | [6 empty] | 276 | 0
80139 | CSDR56 | 5 | South | YES | 0.000895 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | [6 empty] | 277 | 0
80140 | CSDR11 | 11 | South | YES | 0.000895 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 | [6 empty] | 278 | 0
9016 | SANDH_G1 | 1 | South | YES | 0.00093 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.033423 | 49 | 49 |  |  |  |  | 0.033423 | 1.6377 | [6 empty] | 279 | 0
9017 | SANDH_G2 | 2 | South | YES | 0.00093 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.033423 | 46 | 46 |  |  |  |  | 0.033423 | 1.5375 | [6 empty] | 280 | 0
9018 | SANDH_G3 | 3 | South | YES | 0.00093 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.033423 | 46 | 46 |  |  |  |  | 0.033423 | 1.5375 | [6 empty] | 281 | 0
9019 | SANDH_G4 | 4 | South | YES | 0.00093 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.033423 | 47 | 47 |  |  |  |  | 0.033423 | 1.5709 | [6 empty] | 282 | 0
9020 | SANDHG5A | 5A | South | YES | 0.00093 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.033423 | 155 | 155 |  |  |  |  | 0.033423 | 5.1806 | [6 empty] | 283 | 0
9021 | SANDHG5C | 5C | South | YES | 0.00093 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.033423 | 148 | 148 |  |  |  |  | 0.033423 | 4.9466 | [6 empty] | 284 | 0
9000 | DECKR_G1 | 1 | South | YES | 0.000931 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.033424 | 321 | 321 |  |  |  |  | 0.033424 | 10.7291 | [6 empty] | 285 | 0
9001 | DECKR_G2 | 2 | South | YES | 0.000931 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.033424 | 426 | 426 |  |  |  |  | 0.033424 | 14.2386 | [6 empty] | 286 | 0
80226 | ALCOA G | 1 | South | YES | 0.000945 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.033438 | 0 | 0 |  |  |  |  | 0.033438 | 0 | [6 empty] | 287 | 0
8134 | FOR #1 | 1 | South | YES | 0.000958 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 288 | 0
8138 | FOR #2 | 2 | South | YES | 0.000958 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 289 | 0
8153 | FOR #3 | 3 | South | YES | 0.000958 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 290 | 0
8154 | FOR #4 | 4 | South | YES | 0.000958 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 291 | 0
8155 | FOR #5 | 5 | South | YES | 0.000958 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 292 | 0
8156 | FOR #6 | 6 | South | YES | 0.000958 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 293 | 0
8157 | FOR #7 | 7 | South | YES | 0.000958 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 294 | 0
9002 | DECKR_G3 | 3 | South | YES | 0.000958 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.033451 | 42 | 42 |  |  |  |  | 0.033451 | 1.4049 | [6 empty] | 295 | 0
9003 | DECKR_G4 | 4 | South | YES | 0.000958 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.033451 | 44 | 44 |  |  |  |  | 0.033451 | 1.4718 | [6 empty] | 296 | 0
9004 | DECKR_G5 | 5 | South | YES | 0.000958 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.033451 | 44 | 44 |  |  |  |  | 0.033451 | 1.4718 | [6 empty] | 297 | 0
9005 | DECKR_G6 | 6 | South | YES | 0.000958 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.033451 | 47 | 47 |  |  |  |  | 0.033451 | 1.5722 | [6 empty] | 298 | 0
80051 | FOR #8 | 8 | South | YES | 0.000958 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 299 | 0
80052 | FOR #9 | 9 | South | YES | 0.000958 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 300 | 0
80053 | FOR #10 | 10 | South | YES | 0.000958 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 | [6 empty] | 301 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.001025 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.033518 | 132 | 132 |  |  |  |  | 0.033518 | 4.4244 | [6 empty] | 302 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.001025 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.033518 | 139 | 139 |  |  |  |  | 0.033518 | 4.659 | [6 empty] | 303 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.001025 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.033518 | 329 | 329 |  |  |  |  | 0.033518 | 11.0274 | [6 empty] | 304 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.001094 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.033587 | 152.5 | 152.5 |  |  |  |  | 0.033587 | 5.122 | [6 empty] | 305 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.001094 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.033587 | 149.5 | 149.5 |  |  |  |  | 0.033587 | 5.0213 | [6 empty] | 306 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.001094 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.033587 | 232.6 | 232.6 |  |  |  |  | 0.033587 | 7.8123 | [6 empty] | 307 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 | [6 empty] | 308 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 | [6 empty] | 309 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 | [6 empty] | 310 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 | [6 empty] | 311 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.001161 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.033654 | 0 | 436 |  |  |  |  | 0.033654 | 14.6731 | [6 empty] | 312 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.001162 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.033655 | 158 | 158 |  |  |  |  | 0.033655 | 5.3175 | [6 empty] | 313 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.001162 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.033655 | 160 | 160 |  |  |  |  | 0.033655 | 5.3848 | [6 empty] | 314 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.001162 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.033655 | 175 | 175 |  |  |  |  | 0.033655 | 5.8896 | [6 empty] | 315 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.001162 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.033655 | 0 | 606 |  |  |  |  | 0.033655 | 20.3949 | [6 empty] | 316 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.001162 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.033655 | 0 | 598 |  |  |  |  | 0.033655 | 20.1257 | [6 empty] | 317 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | 0.001404 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.033897 | 0 | 0 |  |  |  |  | 0.033897 | 0 | [6 empty] | 318 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | 0.001404 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.033897 | 0 | 0 |  |  |  |  | 0.033897 | 0 | [6 empty] | 319 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.00141 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.033903 | 0 | 580 |  |  |  |  | 0.033903 | 19.6637 | [6 empty] | 320 | 0
48731 | CBE_GT1 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 | [6 empty] | 321 | 0
48732 | CBE_GT2 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 | [6 empty] | 322 | 0
48733 | CBE_ST12 | 1 | Houston | YES | 0.001422 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.033915 | 105 | 105 |  |  |  |  | 0.033915 | 3.5611 | [6 empty] | 323 | 0
48734 | CBE_GT3 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 | [6 empty] | 324 | 0
48735 | CBE_GT4 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 | [6 empty] | 325 | 0
48736 | CBE_ST34 | 1 | Houston | YES | 0.001422 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.033915 | 105 | 105 |  |  |  |  | 0.033915 | 3.5611 | [6 empty] | 326 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.00144 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.033933 | 0 | 0 |  |  |  |  | 0.033933 | 0 | [6 empty] | 327 | 0
49851 | DOW17000 | 37 | Houston | YES | 0.001551 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 328 | 0
49858 | DOW38100 | 31 | Houston | YES | 0.001551 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 329 | 0
49859 | DOW38200 | 33 | Houston | YES | 0.001551 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 330 | 0
49860 | DOW38300 | 32 | Houston | YES | 0.001551 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 331 | 0
49862 | DOW39100 | 36 | Houston | YES | 0.001551 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 332 | 0
49863 | DOW39200 | 35 | Houston | YES | 0.001551 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 333 | 0
49865 | DOW41000 | 41 | Houston | YES | 0.001551 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 334 | 0
49866 | DOW42000 | 42 | Houston | YES | 0.001551 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 335 | 0
49869 | DOW49000 | 45 | Houston | YES | 0.001551 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 336 | 0
49870 | DOW61000 | 61 | Houston | YES | 0.001551 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 337 | 0
49871 | DOW62000 | 62 | Houston | YES | 0.001551 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 338 | 0
49872 | DOW63000 | 63 | Houston | YES | 0.001551 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 339 | 0
49873 | DOW64000 | 64 | Houston | YES | 0.001551 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 340 | 0
49876 | DOW65000 | 65 | Houston | YES | 0.001551 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 341 | 0
49877 | DOW66000 | 66 | Houston | YES | 0.001551 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 342 | 0
49878 | DOW67000 | 67 | Houston | YES | 0.001551 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 343 | 0
49882 | DOW81000 | 81 | Houston | YES | 0.001551 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 344 | 0
49884 | DOW82000 | 82 | Houston | YES | 0.001551 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 345 | 0
49885 | DOW83000 | 83 | Houston | YES | 0.001551 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 346 | 0
49886 | DOW84000 | 84 | Houston | YES | 0.001551 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 | [6 empty] | 347 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.001577 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.03407 | 0 | 0 |  |  |  |  | 0.03407 | 0 | [6 empty] | 348 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.001577 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.03407 | 0 | 0 |  |  |  |  | 0.03407 | 0 | [6 empty] | 349 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.001588 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.034081 | 0 | 581 |  |  |  |  | 0.034081 | 19.801 | [6 empty] | 350 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.0016 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 | [6 empty] | 351 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.0016 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 | [6 empty] | 352 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.0016 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 | [6 empty] | 353 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.0016 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 | [6 empty] | 354 | 0
48730 | MNS_GT | 1 | Houston | YES | 0.001674 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.034167 | 0 | 0 |  |  |  |  | 0.034167 | 0 | [6 empty] | 355 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.001679 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.034172 | 167.7 | 167.7 |  |  |  |  | 0.034172 | 5.7306 | [6 empty] | 356 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.001679 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.034172 | 166.4 | 166.4 |  |  |  |  | 0.034172 | 5.6862 | [6 empty] | 357 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.001679 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.034172 | 252.4 | 252.4 |  |  |  |  | 0.034172 | 8.625 | [6 empty] | 358 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.001679 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 651 |  |  |  |  | 0.034172 | 22.2459 | [6 empty] | 359 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.001679 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 564 |  |  |  |  | 0.034172 | 19.273 | [6 empty] | 360 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.001679 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 603 |  |  |  |  | 0.034172 | 20.6057 | [6 empty] | 361 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.001685 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.034178 | 0 | 0 |  |  |  |  | 0.034178 | 0 | [6 empty] | 362 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.001693 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.034186 | 166 | 166 |  |  |  |  | 0.034186 | 5.6749 | [6 empty] | 363 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.001693 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.034186 | 166 | 166 |  |  |  |  | 0.034186 | 5.6749 | [6 empty] | 364 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.001693 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.034186 | 248 | 248 |  |  |  |  | 0.034186 | 8.4781 | [6 empty] | 365 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.001693 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.034186 | 546 | 546 |  |  |  |  | 0.034186 | 18.6655 | [6 empty] | 366 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.001693 | 585.3 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.034186 | 0 | 654 |  |  |  |  | 0.034186 | 22.3576 | [6 empty] | 367 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.001693 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.034186 | 13 | 13 |  |  |  |  | 0.034186 | 0.44442 | [6 empty] | 368 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.001734 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 369 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.001734 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 370 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.001734 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 371 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.001734 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 372 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.001734 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 373 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.001734 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 374 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.001734 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 375 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.001734 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 376 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.001734 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 377 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.001734 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 378 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.001734 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 379 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.001734 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 380 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.001734 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 381 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.001734 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 382 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.001734 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 | [6 empty] | 383 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | 0.001753 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.034246 | 0 | 0 |  |  |  |  | 0.034246 | 0 | [6 empty] | 384 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.001767 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | [6 empty] | 385 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.001767 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | [6 empty] | 386 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.001767 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | [6 empty] | 387 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.001767 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | [6 empty] | 388 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.001767 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 | [6 empty] | 389 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.001772 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 | [6 empty] | 390 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.001772 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.001772 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.001772 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0
48691 | GBY_73741085 | B | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108
48691 | GBY_73741085 | A | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108
48692 | GBY_81821075 | D | Houston | YES | 0.00178 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.034273 | 55 | 55 |  |  |  |  | 0.034273 | 1.885
48692 | GBY_81821075 | C | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108
48693 | GBY_83841065 | F | Houston | YES | 0.00178 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.034273 | 54 | 54 |  |  |  |  | 0.034273 | 1.8507
48693 | GBY_83841065 | E | Houston | YES | 0.00178 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.034273 | 57 | 57 |  |  |  |  | 0.034273 | 1.9536
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.001782 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.034275 | 0 | 0 |  |  |  |  | 0.034275 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.001782 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.034275 | 0 | 0 |  |  |  |  | 0.034275 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.001784 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.034277 | 163.2 | 163.2 |  |  |  |  | 0.034277 | 5.594
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.001784 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.034277 | 157.1 | 157.1 |  |  |  |  | 0.034277 | 5.3849
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.001784 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.034277 | 157.5 | 157.5 |  |  |  |  | 0.034277 | 5.3986
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.001784 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.034277 | 157 | 157 |  |  |  |  | 0.034277 | 5.3815
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.001784 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.034277 | 282 | 282 |  |  |  |  | 0.034277 | 9.6661
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.001787 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.03428 | 0 | 0 |  |  |  |  | 0.03428 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.00179 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.034283 | 0 | 0 |  |  |  |  | 0.034283 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.00179 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.034283 | 0 | 0 |  |  |  |  | 0.034283 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.00179 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.034283 | 165 | 165 |  |  |  |  | 0.034283 | 5.6567
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.00179 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.034283 | 176 | 176 |  |  |  |  | 0.034283 | 6.0338
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.00179 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.034283 | 213 | 213 |  |  |  |  | 0.034283 | 7.3023
48855 | SRB_GT211035 | B1 | Houston | YES | 0.00179 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.034283 | 18 | 18 |  |  |  |  | 0.034283 | 0.61709
48855 | SRB_GT211035 | B2 | Houston | YES | 0.00179 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.034283 | 12 | 12 |  |  |  |  | 0.034283 | 0.4114
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.001791 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.001791 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.001791 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.001791 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.001791 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.001791 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.001791 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0
48845 | SOL_GT1 | 1 | Houston | YES | 0.001791 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.034284 | 16.2 | 16.2 |  |  |  |  | 0.034284 | 0.5554
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.001791 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.034284 | 228 | 228 |  |  |  |  | 0.034284 | 7.8167
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.001794 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0
48821 | SHELLG2 | 2 | Houston | YES | 0.001794 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.001794 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.001794 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.001799 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.034292 | 0 | 0 |  |  |  |  | 0.034292 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.0018 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.034293 | 42 | 42 |  |  |  |  | 0.034293 | 1.4403
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.0018 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.034293 | 42 | 42 |  |  |  |  | 0.034293 | 1.4403
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.0018 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.034293 | 39 | 39 |  |  |  |  | 0.034293 | 1.3374
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.0018 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.034293 | 39 | 39 |  |  |  |  | 0.034293 | 1.3374
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.001801 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.034294 | 0 | 0 |  |  |  |  | 0.034294 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.001801 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.034294 | 0 | 0 |  |  |  |  | 0.034294 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.001809 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.034302 | 107 | 107 |  |  |  |  | 0.034302 | 3.6703
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.001809 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.034302 | 108 | 108 |  |  |  |  | 0.034302 | 3.7046
48875 | THW_3132 | A | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866
48875 | THW_3132 | B | Houston | YES | 0.001809 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.034302 | 53 | 53 |  |  |  |  | 0.034302 | 1.818
48877 | THW_3334 | C | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866
48877 | THW_3334 | D | Houston | YES | 0.001809 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.034302 | 57 | 57 |  |  |  |  | 0.034302 | 1.9552
48879 | THW_4142 | E | Houston | YES | 0.001809 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.034302 | 56 | 56 |  |  |  |  | 0.034302 | 1.9209
48879 | THW_4142 | F | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866
48881 | THW_4344 | G | Houston | YES | 0.001809 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.034302 | 58 | 58 |  |  |  |  | 0.034302 | 1.9895
48881 | THW_4344 | H | Houston | YES | 0.001809 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.034302 | 58 | 58 |  |  |  |  | 0.034302 | 1.9895
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.001813 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.034306 | 746 | 746 |  |  |  |  | 0.034306 | 25.5922
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.001817 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.03431 | 12 | 12 |  |  |  |  | 0.03431 | 0.41172
49803 | EXN_15GT | 1 | Houston | YES | 0.001817 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49804 | EXN_16GT | 2 | Houston | YES | 0.001817 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49805 | EXN_17GT | 3 | Houston | YES | 0.001817 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49826 | EXN938GT | 5 | Houston | YES | 0.001817 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49828 | EXN941GT | 10 | Houston | YES | 0.001817 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49829 | EXN942GT | 11 | Houston | YES | 0.001817 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49830 | EXN943GT | 12 | Houston | YES | 0.001817 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49831 | EXN944GT | 13 | Houston | YES | 0.001817 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49832 | EXN945GT | 9 | Houston | YES | 0.001817 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49837 | EXN_GT | 4 | Houston | YES | 0.001817 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
49838 | EXN_14GT | 14 | Houston | YES | 0.001817 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.001821 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.034314 | 744 | 744 |  |  |  |  | 0.034314 | 25.5296
48651 | EP_1_2 | 1 | Houston | YES | 0.001821 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48651 | EP_1_2 | 2 | Houston | YES | 0.001821 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.001821 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.001821 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.001821 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.001821 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.001821 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.001821 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.001821 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.001821 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.001823 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.034316 | 0 | 0 |  |  |  |  | 0.034316 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.00183 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.034323 | 162.8 | 162.8 |  |  |  |  | 0.034323 | 5.5878
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.00183 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.034323 | 161.4 | 161.4 |  |  |  |  | 0.034323 | 5.5397
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.00183 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.034323 | 158.9 | 158.9 |  |  |  |  | 0.034323 | 5.4539
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.00183 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.034323 | 269.2 | 269.2 |  |  |  |  | 0.034323 | 9.2397
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.001833 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.034326 | 398 | 398 |  |  |  |  | 0.034326 | 13.6617
48885 | THW_5152 | B | Houston | YES | 0.001836 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.034329 | 59 | 59 |  |  |  |  | 0.034329 | 2.0254
48885 | THW_5152 | A | Houston | YES | 0.001836 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.034329 | 58 | 58 |  |  |  |  | 0.034329 | 1.9911
48886 | THW_5354 | D | Houston | YES | 0.001836 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.034329 | 58 | 58 |  |  |  |  | 0.034329 | 1.9911
48886 | THW_5354 | C | Houston | YES | 0.001836 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.034329 | 57 | 57 |  |  |  |  | 0.034329 | 1.9568
48887 | THW_5556 | E | Houston | YES | 0.001836 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.034329 | 59 | 59 |  |  |  |  | 0.034329 | 2.0254
48887 | THW_5556 | F | Houston | YES | 0.001836 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.034329 | 57 | 57 |  |  |  |  | 0.034329 | 1.9568
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.001873 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.001873 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.001873 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.001873 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.001873 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.002026 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.034519 | 0 | 0 | 0 | 0 |  |  | 0.034519 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.002026 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.034519 | 0 | 0 | 0 | 0 |  |  | 0.034519 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.00218 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.034673 | 217.3 | 217.3 | 0.47371 | 217.3 |  |  | 0.034673 | 7.5344
1878 | WLFHOLW_2G | 2 | North | YES | 0.00218 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.034673 | 215.7 | 215.7 | 0.47023 | 215.7 |  |  | 0.034673 | 7.479
1879 | WLFHOLW_3G | 3 | North | YES | 0.00218 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.034673 | 272.4 | 272.4 | 0.59383 | 272.4 |  |  | 0.034673 | 9.4449
48671 | FTR_GT1_5105 | 1 | North | YES | 0.002212 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.034705 | 154.2 | 154.2 | 0.34109 | 154.2 |  |  | 0.034705 | 5.3515
48672 | FTR_GT2_5110 | 2 | North | YES | 0.002212 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.034705 | 159 | 159 | 0.35171 | 159 |  |  | 0.034705 | 5.5181
48673 | FTR_GT3_5085 | 3 | North | YES | 0.002212 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.034705 | 158 | 158 | 0.3495 | 158 |  |  | 0.034705 | 5.4834
48674 | FTR_CN4_5095 | 4 | North | YES | 0.002212 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.034705 | 380 | 380 | 0.84056 | 380 |  |  | 0.034705 | 13.1879
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.002279 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.034772 | 48 | 48 | 0.10939 | 48 |  |  | 0.034772 | 1.6691
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.002279 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.034772 | 46 | 46 | 0.10483 | 46 |  |  | 0.034772 | 1.5995
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.002279 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.034772 | 105 | 105 | 0.2393 | 105 |  |  | 0.034772 | 3.6511
990 | GIBN_CREK_G1 | 1 | North | YES | 0.002282 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.034775 | 0 | 463 | 1.0566 | 463 |  |  | 0.034775 | 16.1008
32886 | BRYN_ATKINS3 | MB | North | YES | 0.002284 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.002284 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.002284 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.034777 | 17 | 17 | 0.038828 | 17 |  |  | 0.034777 | 0.59121
32890 | BRYN_ATKINS4 | MB | North | YES | 0.002284 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.002284 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.002285 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.034778 | 32 | 32 | 0.07312 | 32 |  |  | 0.034778 | 1.1129
3416 | LAKE_CRK1_G | 1 | North | YES | 0.002329 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.034822 | 75 | 75 | 0.17467 | 75 |  |  | 0.034822 | 2.6116
3417 | LAKE_CRK2_G | 2 | North | YES | 0.002329 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.034822 | 222 | 222 | 0.51704 | 222 |  |  | 0.034822 | 7.7305
3403 | THOUSE_1G | 1 | North | YES | 0.002398 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.034891 | 563 | 563 | 1.3501 | 563 |  |  | 0.034891 | 19.6436
3404 | THOUSE_2G | 2 | North | YES | 0.002398 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.034891 | 807 | 807 | 1.9352 | 807 |  |  | 0.034891 | 28.157
238 | BOSQUESW505 | 1 | North | YES | 0.00249 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.034983 | 255 | 255 | 0.63495 | 255 |  |  | 0.034983 | 8.9207
239 | BOSQUESW502 | 1 | North | YES | 0.00249 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.034983 | 149 | 149 | 0.37101 | 149 |  |  | 0.034983 | 5.2125
247 | BOSQUESW501 | 2 | North | YES | 0.00249 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.034983 | 156 | 156 | 0.38844 | 156 |  |  | 0.034983 | 5.4573
39960 | TNTNPONE_18 | 1 | North | YES | 0.002507 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.035 | 0 | 152.3 | 0.38182 | 152.3 |  |  | 0.035 | 5.3305
39970 | TNTNPONE_28 | 1 | North | YES | 0.002507 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.035 | 0 | 153 | 0.38357 | 153 |  |  | 0.035 | 5.355
48721 | LEG_1___1 | 1 | North | YES | 0.002597 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.03509 | 0 | 827 | 2.1477 | 827 |  |  | 0.03509 | 29.0194
48722 | LEG_2___2 | 2 | North | YES | 0.002597 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.03509 | 0 | 819 | 2.1269 | 819 |  |  | 0.03509 | 28.7387
251 | BOSQUESW803 | 2 | North | YES | 0.002639 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.035132 | 150 | 150 | 0.39585 | 150 |  |  | 0.035132 | 5.2698
253 | BOSQUESW804 | 2 | North | YES | 0.002639 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.035132 | 80 | 80 | 0.21112 | 80 |  |  | 0.035132 | 2.8106
1889 | DECRDOVA_1G | 1 | North | YES | 0.002771 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.035264 | 779 | 779 | 2.1586 | 779 |  |  | 0.035264 | 27.4706
3381 | BBRN_1G | 1 | North | YES | 0.002832 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.035325 | 0 | 618 | 1.7502 | 618 |  |  | 0.035325 | 21.8308
3382 | BBRN_2G | 2 | North | YES | 0.002832 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.035325 | 0 | 589 | 1.668 | 589 |  |  | 0.035325 | 20.8064
13131 | CALFREST_1G | 1 | North | YES | 0.002871 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.035364 | 150.7 | 150.7 | 0.43266 | 150.7 |  |  | 0.035364 | 5.3293
13132 | CALFREST_2G | 2 | North | YES | 0.002871 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.035364 | 151 | 151 | 0.43352 | 151 |  |  | 0.035364 | 5.34
13133 | CALFREST_3G | 3 | North | YES | 0.002871 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.035364 | 177.4 | 177.4 | 0.50932 | 177.4 |  |  | 0.035364 | 6.2736
13134 | CALFREST_4G | 4 | North | YES | 0.002882 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.035375 | 151.5 | 151.5 | 0.43662 | 151.5 |  |  | 0.035375 | 5.3593
13135 | CALFREST_5G | 5 | North | YES | 0.002882 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.035375 | 152.3 | 152.3 | 0.43893 | 152.3 |  |  | 0.035375 | 5.3876
13136 | CALFREST_6G | 6 | North | YES | 0.002882 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.035375 | 177.5 | 177.5 | 0.51155 | 177.5 |  |  | 0.035375 | 6.2791
1937 | MDLTHELP_5G | 5 | North | YES | 0.00297 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.035463 | 224 | 224 | 0.66528 | 224 |  |  | 0.035463 | 7.9437
1938 | MDLTHELP_6G | 6 | North | YES | 0.00297 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.035463 | 226 | 226 | 0.67122 | 226 |  |  | 0.035463 | 8.0146
1943 | MDLTHELP_3G | 3 | North | YES | 0.00297 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.035463 | 212 | 212 | 0.62964 | 212 |  |  | 0.035463 | 7.5181
1944 | MDLTHELP_4G | 4 | North | YES | 0.00297 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.035463 | 211 | 211 | 0.62667 | 211 |  |  | 0.035463 | 7.4827
244 | WHITNYDM01 | 1 | North | YES | 0.003046 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.035539 | 0 | 0 | 0 | 0 |  |  | 0.035539 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.003046 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.035539 | 0 | 0 | 0 | 0 |  |  | 0.035539 | 0
1941 | MDLTHELP_1G | 1 | North | YES | 0.00305 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.035543 | 216.4 | 216.4 | 0.66002 | 216.4 |  |  | 0.035543 | 7.6915
1942 | MDLTHELP_2G | 2 | North | YES | 0.00305 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.035543 | 216.1 | 216.1 | 0.65911 | 216.1 |  |  | 0.035543 | 7.6808
3126 | TRINIDAD_6G | 1 | North | YES | 0.003054 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.035547 | 224 | 224 | 0.6841 | 224 |  |  | 0.035547 | 7.9625
3107 | STRYKER_1G | 1 | North | YES | 0.003085 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.035578 | 182 | 182 | 0.56147 | 182 |  |  | 0.035578 | 6.4752
3108 | STRYKER_2G | 2 | North | YES | 0.003085 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.035578 | 484 | 484 | 1.4931 | 484 |  |  | 0.035578 | 17.2197
3309 | ASPN_G | 1 | North | YES | 0.003088 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.035581 | 50 | 50 | 0.1544 | 50 |  |  | 0.035581 | 1.779
3348 | CHAMPION_1G | MB | North | YES | 0.00309 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.035583 | 0 | 0 | 0 | 0 |  |  | 0.035583 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.003092 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.035585 | 0 | 0 | 0 | 0 |  |  | 0.035585 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.003092 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.035585 | 0 | 0 | 0 | 0 |  |  | 0.035585 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | 0.003103 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.035596 | 196 | 196 | 0.60819 | 196 |  |  | 0.035596 | 6.9768
12323 | ENNSTRAC_2G | 2 | North | YES | 0.003103 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.035596 | 116 | 116 | 0.35995 | 116 |  |  | 0.035596 | 4.1291
13116 | TGATEWAY_1G | 1 | North | YES | 0.003111 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.035604 | 151 | 151 | 0.46976 | 151 |  |  | 0.035604 | 5.3762
13117 | TGATEWAY_2G | 2 | North | YES | 0.003111 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.035604 | 130 | 130 | 0.40443 | 130 |  |  | 0.035604 | 4.6285
13118 | TGATEWAY_3G | 3 | North | YES | 0.003111 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.035604 | 148 | 148 | 0.46043 | 148 |  |  | 0.035604 | 5.2694
13119 | TGATEWAY_4G | 4 | North | YES | 0.003111 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.035604 | 399 | 399 | 1.2413 | 399 |  |  | 0.035604 | 14.206
3097 | MARTLAKE_1G | 1 | North | YES | 0.003135 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 790 | 2.4766 | 790 |  |  | 0.035628 | 28.1461
3098 | MARTLAKE_2G | 2 | North | YES | 0.003135 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 795 | 2.4923 | 795 |  |  | 0.035628 | 28.3242
3099 | MARTLAKE_3G | 3 | North | YES | 0.003135 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 804 | 2.5205 | 804 |  |  | 0.035628 | 28.6449
2413 | MTCK6_G | 6 | North | YES | 0.003263 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.035756 | 118 | 118 | 0.38503 | 118 |  |  | 0.035756 | 4.2192
2414 | MTCK7_G | 7 | North | YES | 0.003263 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.035756 | 115 | 115 | 0.37524 | 115 |  |  | 0.035756 | 4.1119
2417 | MTCK8_G | 8 | North | YES | 0.003263 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.035756 | 556 | 556 | 1.8142 | 556 |  |  | 0.035756 | 19.8803
12440 | PARKD_1SVC8 | 1 | North | YES | 0.003301 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035794 | 0 | 0 | 0 | 0 |  |  | 0.035794 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.003301 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035794 | 0 | 0 | 0 | 0 |  |  | 0.035794 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.003313 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035806 | 161 | 161 | 0.53339 | 161 |  |  | 0.035806 | 5.7648
12412 | FPLEFR1B_G | 2 | North | YES | 0.003313 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035806 | 164 | 164 | 0.54333 | 164 |  |  | 0.035806 | 5.8722
12413 | FPLEFR1C_G | 3 | North | YES | 0.003313 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035806 | 164 | 164 | 0.54333 | 164 |  |  | 0.035806 | 5.8722
12414 | FPLEFR1S_G | 4 | North | YES | 0.003313 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.035806 | 414 | 414 | 1.3716 | 414 |  |  | 0.035806 | 14.8237
12421 | FPLEFR2A_G | 1 | North | YES | 0.003313 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.035806 | 162 | 162 | 0.53671 | 162 |  |  | 0.035806 | 5.8006
12422 | FPLEFR2B_G | 2 | North | YES | 0.003313 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035806 | 161 | 161 | 0.53339 | 161 |  |  | 0.035806 | 5.7648
12423 | FPLEFR2C_G | 3 | North | YES | 0.003313 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.035806 | 163 | 163 | 0.54002 | 163 |  |  | 0.035806 | 5.8364
12424 | FPLEFR2S_G | 4 | North | YES | 0.003313 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.035806 | 415 | 415 | 1.3749 | 415 |  |  | 0.035806 | 14.8595
2451 | LKHB1_G | 1 | North | YES | 0.003324 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.035817 | 391 | 391 | 1.2997 | 391 |  |  | 0.035817 | 14.0044
2452 | LKHB2_G | 2 | North | YES | 0.003324 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.035817 | 516 | 516 | 1.7152 | 516 |  |  | 0.035817 | 18.4816
1892 | DECRDOVA_2G | A | North | YES | 0.003377 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.03587 | 70 | 70 | 0.23639 | 70 |  |  | 0.03587 | 2.5109
1893 | DECRDOVA_3G | B | North | YES | 0.003377 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.03587 | 69 | 69 | 0.23301 | 69 |  |  | 0.03587 | 2.475
1894 | DECRDOVA_4G | C | North | YES | 0.003377 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.03587 | 69 | 69 | 0.23301 | 69 |  |  | 0.03587 | 2.475
1895 | DECRDOVA_5G | D | North | YES | 0.003377 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.03587 | 68 | 68 | 0.22964 | 68 |  |  | 0.03587 | 2.4392
948 | STEAM1 | 1 | North | YES | 0.003387 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.03588 | 20 | 20 | 0.06774 | 20 |  |  | 0.03588 | 0.7176
949 | STEAM2 | 1 | North | YES | 0.003387 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.03588 | 26 | 26 | 0.088062 | 26 |  |  | 0.03588 | 0.93288
950 | STEAM3 | 1 | North | YES | 0.003387 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.03588 | 42 | 42 | 0.14225 | 42 |  |  | 0.03588 | 1.507
837 | NEWMAN_G5 | 1 | North | YES | 0.00339 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.035883 | 40 | 40 | 0.1356 | 40 |  |  | 0.035883 | 1.4353
842 | OLINGER_G1 | 1 | North | YES | 0.003399 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.035892 | 79 | 79 | 0.26852 | 79 |  |  | 0.035892 | 2.8355
843 | OLINGER_G2 | 1 | North | YES | 0.003399 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.035892 | 110 | 110 | 0.37389 | 110 |  |  | 0.035892 | 3.9481
844 | OLINGER_G3 | 1 | North | YES | 0.003399 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.035892 | 150 | 150 | 0.50985 | 150 |  |  | 0.035892 | 5.3838
845 | OLINGER_G4 | 1 | North | YES | 0.003399 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.035892 | 76 | 76 | 0.25832 | 76 |  |  | 0.035892 | 2.7278
1701 | MOSES_1G | 1 | North | YES | 0.003456 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 558 | 1.9284 | 558 |  |  | 0.035949 | 20.0595
1702 | MOSES_2G | 2 | North | YES | 0.003456 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 579 | 2.001 | 579 |  |  | 0.035949 | 20.8144
1703 | MOSES_3G | 3 | North | YES | 0.003456 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 808 | 2.7924 | 808 |  |  | 0.035949 | 29.0468
5925 | DCEAST | EQ | North | YES | 0.003456 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.035949 | 0 | 0 | 0 | 0 |  |  | 0.035949 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.003496 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.035989 | 160 | 160 | 0.55936 | 160 |  |  | 0.035989 | 5.7582
1679 | LAMARPWR_2G | 2 | North | YES | 0.003496 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.035989 | 156 | 156 | 0.54538 | 156 |  |  | 0.035989 | 5.6143
1680 | LAMARPWR_3G | 3 | North | YES | 0.003496 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.035989 | 196 | 196 | 0.68522 | 196 |  |  | 0.035989 | 7.0538
1681 | LAMARPWR_4G | 4 | North | YES | 0.003496 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.035989 | 156 | 156 | 0.54538 | 156 |  |  | 0.035989 | 5.6143
1682 | LAMARPWR_5G | 5 | North | YES | 0.003496 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.035989 | 157 | 157 | 0.54887 | 157 |  |  | 0.035989 | 5.6503
1683 | LAMARPWR_6G | 6 | North | YES | 0.003496 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.035989 | 198 | 198 | 0.69221 | 198 |  |  | 0.035989 | 7.1258
1675 | PEC_1G | 1 | North | YES | 0.003499 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0
1676 | PEC_2G | 2 | North | YES | 0.003499 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0
1677 | PEC_3G | 3 | North | YES | 0.003499 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.003508 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.036001 | 156 | 156 | 0.54725 | 156 |  |  | 0.036001 | 5.6161
2382 | NTHLK2_G | 2 | North | YES | 0.003508 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.036001 | 181 | 181 | 0.63495 | 181 |  |  | 0.036001 | 6.5162
2383 | NTHLK3_G | 3 | North | YES | 0.003508 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.036001 | 329 | 329 | 1.1541 | 329 |  |  | 0.036001 | 11.8443
1947 | HANDLEY_3G | 3 | North | YES | 0.003509 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.036002 | 395 | 395 | 1.3861 | 395 |  |  | 0.036002 | 14.2208
1949 | HANDLEY_5G | 5 | North | YES | 0.003509 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.036002 | 435 | 435 | 1.5264 | 435 |  |  | 0.036002 | 15.6609
1948 | HANDLEY_4G | 4 | North | YES | 0.00351 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.036003 | 435 | 435 | 1.5269 | 435 |  |  | 0.036003 | 15.6613
1689 | VALLEY_3G | 3 | North | YES | 0.003511 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.036004 | 375 | 375 | 1.3166 | 375 |  |  | 0.036004 | 13.5015
11691 | KMICHICT1_G | 1 | North | YES | 0.003511 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036004 | 144 | 144 | 0.50558 | 144 |  |  | 0.036004 | 5.1846
11692 | KMICHICT2_G | 2 | North | YES | 0.003511 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.036004 | 146 | 146 | 0.51261 | 146 |  |  | 0.036004 | 5.2566
11693 | KMICHIST3_G | 3 | North | YES | 0.003511 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.036004 | 312 | 312 | 1.0954 | 312 |  |  | 0.036004 | 11.2332
11694 | KMICHICT4_G | 4 | North | YES | 0.003511 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036004 | 144 | 144 | 0.50558 | 144 |  |  | 0.036004 | 5.1846
11695 | KMICHICT5_G | 5 | North | YES | 0.003511 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.036004 | 148 | 148 | 0.51963 | 148 |  |  | 0.036004 | 5.3286
11696 | KMICHIST6_G | 6 | North | YES | 0.003511 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.036004 | 310 | 310 | 1.0884 | 310 |  |  | 0.036004 | 11.1612
1687 | VALLEY_1G | 1 | North | YES | 0.003619 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.036112 | 170 | 170 | 0.61523 | 170 |  |  | 0.036112 | 6.139
1688 | VALLEY_2G | 2 | North | YES | 0.003619 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.036112 | 527 | 527 | 1.9072 | 527 |  |  | 0.036112 | 19.031
2371 | COLLIN_1G | MB | North | YES | 0.003631 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.036124 | 0 | 0 | 0 | 0 |  |  | 0.036124 | 0
6948 | DENISNDM | 1 | North | YES | 0.003692 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.036185 | 0 | 0 | 0 | 0 |  |  | 0.036185 | 0
6948 | DENISNDM | 2 | North | YES | 0.003692 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.036185 | 0 | 0 | 0 | 0 |  |  | 0.036185 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.004247 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.03674 | 61 | 61 | 0.25907 | 61 |  |  | 0.03674 | 2.2411
924 | SPENCER_G5 | 1 | North | YES | 0.004247 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.03674 | 66 | 66 | 0.2803 | 66 |  |  | 0.03674 | 2.4248
1453 | WCPWRCO_1G | 1 | North | YES | 0.004266 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.036759 | 204 | 204 | 0.87026 | 204 |  |  | 0.036759 | 7.4988
1454 | WCPWRCO_2G | 2 | North | YES | 0.004266 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.036759 | 204 | 204 | 0.87026 | 204 |  |  | 0.036759 | 7.4988
1455 | WCPWRCO_3G | 3 | North | YES | 0.004266 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.036759 | 242 | 242 | 1.0324 | 242 |  |  | 0.036759 | 8.8957
1861 | EAGLEMNT_1G | MB | North | YES | 0.004873 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.004873 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.004873 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.005397 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.03789 | 0 | 60 | 0.32382 | 60 |  |  | 0.03789 | 2.2734
1432 | GRHAMSES_2G | 2 | North | YES | 0.005683 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.038176 | 366 | 366 | 2.08 | 366 |  |  | 0.038176 | 13.9724
1442 | COKFIELD_5 | 1 | North | YES | 0.005683 | 16.5 | 0 | 165 | 0 | 1.029 | Wind | 1 | 0.038176 | 0 | 165 | 0.93769 | 165 |  |  | 0.038176 | 6.299
728 | WOLFRIDGE801 | 1 | North | YES | 0.007076 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.039569 | 0 | 112.5 | 0.79605 | 112.5 |  |  | 0.039569 | 4.4515
580 | JCKCNTY801 | 1 | North | YES | 0.00999 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.042483 | 288 | 288 | 2.8771 | 288 |  |  | 0.042483 | 12.2351
581 | JCKCNTY802 | 2 | North | YES | 0.00999 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.042483 | 147 | 147 | 1.4685 | 147 |  |  | 0.042483 | 6.245
582 | JCKCNTY803 | 3 | North | YES | 0.00999 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.042483 | 147 | 147 | 1.4685 | 147 |  |  | 0.042483 | 6.245
1479 | WFCOGEN_1G | 1 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.01168 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0
332 | RWMILLER01 | 1 | North | YES | 0.012387 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.04488 | 73 | 73 | 0.90425 | 73 |  |  | 0.04488 | 3.2762
333 | RWMILLER02 | 2 | North | YES | 0.012387 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.04488 | 119 | 119 | 1.4741 | 119 |  |  | 0.04488 | 5.3407
334 | RWMILLER03 | 3 | North | YES | 0.012387 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.04488 | 208 | 208 | 2.5765 | 208 |  |  | 0.04488 | 9.335
335 | RWMILLER04 | 4 | North | YES | 0.012387 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.04488 | 102 | 102 | 1.2635 | 102 |  |  | 0.04488 | 4.5778
336 | RWMILLER05 | 5 | North | YES | 0.012387 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.04488 | 101 | 101 | 1.2511 | 101 |  |  | 0.04488 | 4.5329
503 | NTHTEXAS01 | 1 | North | YES | 0.012564 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.045057 | 18 | 18 | 0.22615 | 18 |  |  | 0.045057 | 0.81103
504 | NTHTEXAS02 | 2 | North | YES | 0.012564 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.045057 | 18 | 18 | 0.22615 | 18 |  |  | 0.045057 | 0.81103
505 | NTHTEXAS03 | 3 | North | YES | 0.012564 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.045057 | 38 | 38 | 0.47743 | 38 |  |  | 0.045057 | 1.7122
344 | MRSSHPRD | 1 | North | YES | 0.022736 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.055229 | 0 | 0 | 0 | 0 |  |  | 0.055229 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.022736 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.055229 | 0 | 0 | 0 | 0 |  |  | 0.055229 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.038401 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.070894 | 0 | 120 | 4.6081 | 120 |  |  | 0.070894 | 8.5073
1433 | GRHAMSES_1G | 1 | North | YES | 0.067419 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.099912 | 242 | 242 | 16.3154 | 242 |  |  | 0.099912 | 24.1787
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Bound Gen
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | max of zone correlation | 0.012101 |  |  | Neg PTDF weight | Pos PTDF weight
1438 | MESQUITW_2G | 1 | North | YES | -0.020392 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.012101 | 0 | 236 | -4.8125 | 236 |  |  | 0.012101 | 2.8558 |  |  |  |  | 0 | 0
1437 | MESQUITW_1G | 1 | North | YES | -0.020371 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.012122 | 0 | 400 | -8.1484 | 400 |  |  | 0.012122 | 4.8488 |  |  |  |  | 0 | 0
6100 | OKLA7A | EQ | West | YES | -0.01742 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.021055 | 0 | 0 |  |  | 0 | 0 | -0.021055 | 0 |  |  |  |  | 0 | 0
6752 | OKLA0A | 1 | West | YES | -0.01742 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.021055 | 0 | 649.7 |  |  | 0 | 0 | -0.021055 | 0 |  |  | Weighted Shift Factors |  | 0 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.008717 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 |  |  | North | 0.0036354 | 0 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.008717 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 |  |  | West | -0.032493 | 0 | 0
88253 | HAMILTON | F | South | YES | -0.008717 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.023776 | 0 | 0 |  |  |  |  | 0.023776 | 0 |  |  |  |  | 0 | 0
8262 | ELPS | 1 | South | YES | -0.006198 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.026295 | 0 | 0 |  |  |  |  | 0.026295 | 0 | West |  |  |  | 0 | 0
11056 | ROSCOE_1G | 1 | West | YES | -0.025191 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.028826 | 0 | 209 |  |  | 0 | 0 | -0.028826 | 0 | Line Rating |  | 155 |  | 0 | 0
11057 | CHAMPION_1G | 1 | West | YES | -0.025191 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.028826 | 0 | 126.5 |  |  | 0 | 0 | -0.028826 | 0 | Impact Counter to Zone: |  | 0 |  | 0 | 0
11058 | PYRON_1G | 1 | West | YES | -0.025191 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.028826 | 0 | 249 |  |  | 0 | 0 | -0.028826 | 0 |  |  | 0% |  | 0 | 0
11059 | INADALE_1G | 1 | West | YES | -0.025191 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.028826 | 0 | 197 |  |  | 0 | 0 | -0.028826 | 0 |  |  |  |  | 0 | 0
60202 | FRNDDRCS | F | West | YES | -0.025875 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.02951 | 0 | 0 |  |  | 0 | 0 | -0.02951 | 0 | North |  |  |  | 0 | 0
1417 | SWETWATR_2G | 2 | West | YES | -0.026126 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.029761 | 72 | 72 |  |  | -1.8811 | 72 | -0.029761 | -2.1428 | Line Rating |  | 155 |  | 0 | 0
1418 | SWETWATR_3G | 3 | West | YES | -0.026126 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.029761 | 68 | 68 |  |  | -1.7766 | 68 | -0.029761 | -2.0238 | Impact Counter to Zone: |  | 0 |  | 0 | 0
1419 | SWETWATR_4G | 4 | West | YES | -0.026126 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.029761 | 61 | 61 |  |  | -1.5937 | 61 | -0.029761 | -1.8154 |  |  | 0% |  | 0 | 0
1416 | SWETWATR_1G | 1 | West | YES | -0.026126 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.029761 | 30 | 30 |  |  | -0.78378 | 30 | -0.029761 | -0.89284 |  |  |  |  | 0 | 0
60058 | BUFF_GAP1A | 1 | West | YES | -0.026615 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.03025 | 0 | 120 |  |  | 0 | 0 | -0.03025 | 0 |  |  |  |  | 0 | 0
60060 | CIRELLO | 1 | West | YES | -0.026615 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.03025 | 0 | 233 |  |  | 0 | 0 | -0.03025 | 0 |  |  |  |  | 0 | 0
60063 | BUFF_GAP1B | 1 | West | YES | -0.026615 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.03025 | 0 | 170.2 |  |  | 0 | 0 | -0.03025 | 0 |  |  |  |  | 0 | 0
60066 | H_HOLLOW1A | 1 | West | YES | -0.026615 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.03025 | 0 | 222 |  |  | 0 | 0 | -0.03025 | 0 |  |  |  |  | 0 | 0
60068 | HHOLLOW21A | 1 | West | YES | -0.026615 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 184 |  |  | 0 | 0 | -0.03025 | 0 |  |  |  |  | 0 | 0
60070 | HHOLLOW31A | 1 | West | YES | -0.026615 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 224 |  |  | 0 | 0 | -0.03025 | 0 |  |  |  |  | 0 | 0
60072 | HHOLLOW41A | 1 | West | YES | -0.026615 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.03025 | 0 | 115 |  |  | 0 | 0 | -0.03025 | 0 |  |  |  |  | 0 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.027538 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.031173 | 0 | 112.5 |  |  | 0 | 0 | -0.031173 | 0 |  |  |  |  | 0 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.027538 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 149.5 |  |  | 0 | 0 | -0.031173 | 0 |  |  |  |  | 0 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.027538 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 186 |  |  | 0 | 0 | -0.031173 | 0 |  |  |  |  | 0 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.027538 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.031173 | 0 | 214.5 |  |  | 0 | 0 | -0.031173 | 0 |  |  |  |  | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.001227 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.031266 | 0 | 0 |  |  |  |  | 0.031266 | 0 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | -0.000973 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.03152 | 8.4 | 8.4 |  |  |  |  | 0.03152 | 0.26477 |  |  |  |  | 0 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | -0.027909 | 30 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.031544 | 0 | 150 |  |  | 0 | 0 | -0.031544 | 0 |  |  |  |  | 0 | 0
80265 | LARECU40A | 4 | South | YES | -0.000703 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.03179 | 100 | 100 |  |  |  |  | 0.03179 | 3.179 |  |  |  |  | 0 | 0
80266 | LARECU50A | 5 | South | YES | -0.000703 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.03179 | 100 | 100 |  |  |  |  | 0.03179 | 3.179 |  |  |  |  | 0 | 0
80012 | LAR | F | South | YES | -0.000702 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.031791 | 0 | 0 |  |  |  |  | 0.031791 | 0 |  |  |  |  | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.00068 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 |  |  |  |  | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.00068 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 |  |  |  |  | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.00068 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.031813 | 0 | 0 |  |  |  |  | 0.031813 | 0 |  |  |  |  | 0 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.000641 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.031852 | 423.3 | 423.3 |  |  |  |  | 0.031852 | 13.4829 |  |  |  |  | 0 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | -0.000627 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.031866 | 23.9 | 23.9 |  |  |  |  | 0.031866 | 0.7616 |  |  |  |  | 0 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.000627 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.031866 | 24 | 24 |  |  |  |  | 0.031866 | 0.76478 |  |  |  |  | 0 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | -0.000627 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.031866 | 24.3 | 24.3 |  |  |  |  | 0.031866 | 0.77434 |  |  |  |  | 0 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.000551 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.031942 | 0 | 0 |  |  |  |  | 0.031942 | 0 |  |  |  |  | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.000551 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.031942 | 0 | 0 |  |  |  |  | 0.031942 | 0 |  |  |  |  | 0 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.000264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.032229 | 0 | 0 |  |  |  |  | 0.032229 | 0 |  |  |  |  | 0 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.000264 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.032229 | 0 | 0 |  |  |  |  | 0.032229 | 0 |  |  |  |  | 0 | 0
88299 | ZAPATA | F | South | YES | -0.000168 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.032325 | 0 | 0 |  |  |  |  | 0.032325 | 0 |  |  |  |  | 0 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | -0.028811 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 37.5 |  |  | 0 | 0 | -0.032446 | 0 |  |  |  |  | 0 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | -0.028811 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 107.5 |  |  | 0 | 0 | -0.032446 | 0 |  |  |  |  | 0 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | -0.028811 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.032446 | 0 | 135 |  |  | 0 | 0 | -0.032446 | 0 |  |  |  |  | 0 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | -0.028811 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 119 |  |  | 0 | 0 | -0.032446 | 0 |  |  |  |  | 0 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | -0.028811 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 105 |  |  | 0 | 0 | -0.032446 | 0 |  |  |  |  | 0 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | -0.028811 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.032446 | 0 | 80.5 |  |  | 0 | 0 | -0.032446 | 0 |  |  |  |  | 0 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.032493 | 0 | 0 |  |  |  |  | 0.032493 | 0 |  |  |  |  | 0 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.032493 | 15 | 15 |  |  |  |  | 0.032493 | 0.48739 |  |  |  |  | 0 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | 0.000195 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 |  |  |  |  | 0 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 0.000195 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 |  |  |  |  | 0 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 0.000195 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.032688 | 0 | 0 |  |  |  |  | 0.032688 | 0 |  |  |  |  | 0 | 0
60000 | DSKY2 | 1 | West | YES | -0.029087 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.032722 | 0 | 76.5 |  |  | 0 | 0 | -0.032722 | 0 |  |  |  |  | 0 | 0
88508 | FALFURRI | F | South | YES | 0.000253 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.032746 | 0 | 0 |  |  |  |  | 0.032746 | 0 |  |  |  |  | 0 | 0
60018 | DSKY1 | 1 | West | YES | -0.029123 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.032758 | 0 | 84 |  |  | 0 | 0 | -0.032758 | 0 |  |  |  |  | 0 | 0
60017 | ORNNWP1 | 1 | West | YES | -0.029339 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.032974 | 0 | 80 |  |  | 0 | 0 | -0.032974 | 0 |  |  |  |  | 0 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | 0.000486 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.032979 | 43 | 43 |  |  |  |  | 0.032979 | 1.4181 |  |  |  |  | 0 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | 0.000486 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.032979 | 44 | 44 |  |  |  |  | 0.032979 | 1.4511 |  |  |  |  | 0 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | 0.000486 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.032979 | 44 | 44 |  |  |  |  | 0.032979 | 1.4511 |  |  |  |  | 0 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | 0.000486 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.032979 | 45 | 45 |  |  |  |  | 0.032979 | 1.4841 |  |  |  |  | 0 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | 0.000486 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.032979 | 58 | 58 |  |  |  |  | 0.032979 | 1.9128 |  |  |  |  | 0 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | 0.000486 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.032979 | 89 | 89 |  |  |  |  | 0.032979 | 2.9351 |  |  |  |  | 0 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.000517 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 |  |  |  |  | 0 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.000517 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 |  |  |  |  | 0 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.000517 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.03301 | 0 | 0 |  |  |  |  | 0.03301 | 0 |  |  |  |  | 0 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.000546 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.033039 | 407 | 407 |  |  |  |  | 0.033039 | 13.4469 |  |  |  |  | 0 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.000564 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.033057 | 215 | 215 |  |  |  |  | 0.033057 | 7.1072 |  |  |  |  | 0 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.000564 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.033057 | 216 | 216 |  |  |  |  | 0.033057 | 7.1403 |  |  |  |  | 0 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | 0.000565 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.033058 | 400 | 400 |  |  |  |  | 0.033058 | 13.2232 |  |  |  |  | 0 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | 0.000565 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.033058 | 418 | 418 |  |  |  |  | 0.033058 | 13.8182 |  |  |  |  | 0 | 0
8933 | FGNTS001 | 1 | South | YES | 0.000574 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.033067 | 146.5 | 146.5 |  |  |  |  | 0.033067 | 4.8443 |  |  |  |  | 0 | 0
8934 | FGNTS101 | 2 | South | YES | 0.000574 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.033067 | 147.9 | 147.9 |  |  |  |  | 0.033067 | 4.8906 |  |  |  |  | 0 | 0
8935 | FGNTS201 | 3 | South | YES | 0.000574 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.033067 | 173 | 173 |  |  |  |  | 0.033067 | 5.7206 |  |  |  |  | 0 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | 0.000576 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.033069 | 0 | 430 |  |  |  |  | 0.033069 | 14.2197 |  |  |  |  | 0 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | 0.000576 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.033069 | 0 | 430 |  |  |  |  | 0.033069 | 14.2197 |  |  |  |  | 0 | 0
88198 | BEEVILLE | F | South | YES | 0.000577 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.03307 | 0 | 0 |  |  |  |  | 0.03307 | 0 |  |  |  |  | 0 | 0
5903 | SANMIGUELGEN | 1 | South | YES | 0.000611 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.033104 | 0 | 396.3 |  |  |  |  | 0.033104 | 13.1191 |  |  |  |  | 0 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.000615 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.033108 | 61 | 61 |  |  |  |  | 0.033108 | 2.0196 |  |  |  |  | 0 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.000615 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.033108 | 95 | 95 |  |  |  |  | 0.033108 | 3.1453 |  |  |  |  | 0 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.000615 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.033108 | 151 | 151 |  |  |  |  | 0.033108 | 4.9993 |  |  |  |  | 0 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.00063 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.033123 | 155 | 155 |  |  |  |  | 0.033123 | 5.1341 |  |  |  |  | 0 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.00063 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.033123 | 155 | 155 |  |  |  |  | 0.033123 | 5.1341 |  |  |  |  | 0 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | 0.00063 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.033123 | 174 | 174 |  |  |  |  | 0.033123 | 5.7634 |  |  |  |  | 0 | 0
8982 | HECN2 | 2 | South | YES | 0.000638 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.033131 | 144.1 | 144.1 |  |  |  |  | 0.033131 | 4.7742 |  |  |  |  | 0 | 0
8981 | HECN1 | 1 | South | YES | 0.000638 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.033131 | 144.8 | 144.8 |  |  |  |  | 0.033131 | 4.7974 |  |  |  |  | 0 | 0
8983 | HECN3 | 3 | South | YES | 0.000638 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.033131 | 171.9 | 171.9 |  |  |  |  | 0.033131 | 5.6952 |  |  |  |  | 0 | 0
8936 | MVGN#1 | 1 | South | YES | 0.000638 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.033131 | 216.6 | 216.6 |  |  |  |  | 0.033131 | 7.1762 |  |  |  |  | 0 | 0
8937 | MVGN#2 | 2 | South | YES | 0.000638 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.033131 | 216.7 | 216.7 |  |  |  |  | 0.033131 | 7.1795 |  |  |  |  | 0 | 0
8938 | MVGN#3 | 3 | South | YES | 0.000638 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.033131 | 250.9 | 250.9 |  |  |  |  | 0.033131 | 8.3126 |  |  |  |  | 0 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | 0.000649 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.033142 | 0 | 562 |  |  |  |  | 0.033142 | 18.6258 |  |  |  |  | 0 | 0
80003 | MILHWYS | F | South | YES | 0.000665 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.033158 | 0 | 0 |  |  |  |  | 0.033158 | 0 |  |  |  |  | 0 | 0
5933 | SI_RAY6 | 6 | South | YES | 0.000665 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.033158 | 19.3 | 19.3 |  |  |  |  | 0.033158 | 0.63995 |  |  |  |  | 0 | 0
5932 | SI_RAY9 | 9 | South | YES | 0.000665 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.033158 | 38 | 38 |  |  |  |  | 0.033158 | 1.26 |  |  |  |  | 0 | 0
5935 | SI_RAY10 | 10 | South | YES | 0.000665 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.033158 | 47 | 47 |  |  |  |  | 0.033158 | 1.5584 |  |  |  |  | 0 | 0
8517 | CELANEBI0A | 1 | South | YES | 0.000679 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.033172 | 0 | 0 |  |  |  |  | 0.033172 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 4 | South | YES | 0.000682 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 19 |  |  |  |  | 0.033175 | 0.63032 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 4 | South | YES | 0.000682 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 22 |  |  |  |  | 0.033175 | 0.72985 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 2 | South | YES | 0.000682 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 36 |  |  |  |  | 0.033175 | 1.1943 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 3 | South | YES | 0.000682 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 38 |  |  |  |  | 0.033175 | 1.2606 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 2 | South | YES | 0.000682 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 41 |  |  |  |  | 0.033175 | 1.3602 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 3 | South | YES | 0.000682 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 43 |  |  |  |  | 0.033175 | 1.4265 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 2 | South | YES | 0.000682 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 50 |  |  |  |  | 0.033175 | 1.6587 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 2 | South | YES | 0.000682 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 50 |  |  |  |  | 0.033175 | 1.6587 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 1 | South | YES | 0.000682 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 55 |  |  |  |  | 0.033175 | 1.8246 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 1 | South | YES | 0.000682 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 94 |  |  |  |  | 0.033175 | 3.1184 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 1 | South | YES | 0.000682 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 94 |  |  |  |  | 0.033175 | 3.1184 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 1 | South | YES | 0.000682 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.033175 | 0 | 148 |  |  |  |  | 0.033175 | 4.9099 |  |  |  |  | 0 | 0
8461 | KOCH_UP0A | 1 | South | YES | 0.000693 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.033186 | 0 | 0 |  |  |  |  | 0.033186 | 0 |  |  |  |  | 0 | 0
8506 | VAL #1 | 1 | South | YES | 0.000697 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 |  |  |  |  | 0 | 0
8507 | VAL #2 | 2 | South | YES | 0.000697 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 |  |  |  |  | 0 | 0
8511 | OXY_CC0A | 1 | South | YES | 0.000697 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.03319 | 0 | 0 |  |  |  |  | 0.03319 | 0 |  |  |  |  | 0 | 0
8459 | B_DAVIS0B | MB | South | YES | 0.000704 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.033197 | 0 | 0 |  |  |  |  | 0.033197 | 0 |  |  |  |  | 0 | 0
8460 | B_DAVIS0A | MB | South | YES | 0.000704 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.033197 | 0 | 0 |  |  |  |  | 0.033197 | 0 |  |  |  |  | 0 | 0
80263 | B_DAVIS31A | 3 | South | YES | 0.000704 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.033197 | 180 | 180 |  |  |  |  | 0.033197 | 5.9755 |  |  |  |  | 0 | 0
80264 | B_DAVIS41A | 4 | South | YES | 0.000704 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.033197 | 180 | 180 |  |  |  |  | 0.033197 | 5.9755 |  |  |  |  | 0 | 0
8456 | COSW#1 | 1 | South | YES | 0.000706 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.033199 | 0 | 0 |  |  |  |  | 0.033199 | 0 |  |  |  |  | 0 | 0
8457 | COSW#2 | 2 | South | YES | 0.000706 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.033199 | 0 | 0 |  |  |  |  | 0.033199 | 0 |  |  |  |  | 0 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.000707 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 |  |  |  |  | 0 | 0
8560 | CNOPGT1 | 1 | South | YES | 0.000707 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 |  |  |  |  | 0 | 0
8561 | CNOPGT2 | 2 | South | YES | 0.000707 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 |  |  |  |  | 0 | 0
8562 | CNOPST1 | 3 | South | YES | 0.000707 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.0332 | 0 | 0 |  |  |  |  | 0.0332 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | MB | South | YES | 0.000708 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.033201 | 0 | 0 |  |  |  |  | 0.033201 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | 7 | South | YES | 0.000708 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.033201 | 367 | 367 |  |  |  |  | 0.033201 | 12.1848 |  |  |  |  | 0 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.000724 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.033217 | 0 | 0 |  |  |  |  | 0.033217 | 0 |  |  |  |  | 0 | 0
8926 | LGE_GT10A | 1 | South | YES | 0.000739 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 |  |  |  |  | 0 | 0
8927 | LGE_GT20A | 2 | South | YES | 0.000739 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 |  |  |  |  | 0 | 0
8928 | LGE_STG0A | 3 | South | YES | 0.000739 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 |  |  |  |  | 0 | 0
8930 | ICPGN10A | 1 | South | YES | 0.000739 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 |  |  |  |  | 0 | 0
8931 | ICPGN20A | 2 | South | YES | 0.000739 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 |  |  |  |  | 0 | 0
8932 | ICPGN30A | 3 | South | YES | 0.000739 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 |  |  |  |  | 0 | 0
80223 | REYSHR G | 1 | South | YES | 0.000739 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.033232 | 0 | 0 |  |  |  |  | 0.033232 | 0 |  |  |  |  | 0 | 0
8161 | COLETO0A | 1 | South | YES | 0.000745 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.033238 | 0 | 633 |  |  |  |  | 0.033238 | 21.0396 |  |  |  |  | 0 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.000759 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.033252 | 138 | 138 |  |  |  |  | 0.033252 | 4.5888 |  |  |  |  | 0 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.000759 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.033252 | 146 | 146 |  |  |  |  | 0.033252 | 4.8548 |  |  |  |  | 0 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.000759 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.033252 | 147 | 147 |  |  |  |  | 0.033252 | 4.888 |  |  |  |  | 0 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.000759 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.033252 | 149 | 149 |  |  |  |  | 0.033252 | 4.9545 |  |  |  |  | 0 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.000759 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.033252 | 182 | 182 |  |  |  |  | 0.033252 | 6.0519 |  |  |  |  | 0 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.000759 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.033252 | 203 | 203 |  |  |  |  | 0.033252 | 6.7501 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.000769 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.000769 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.000769 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.033262 | 0 | 0 |  |  |  |  | 0.033262 | 0 |  |  |  |  | 0 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.00079 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.033283 | 148 | 148 |  |  |  |  | 0.033283 | 4.9259 |  |  |  |  | 0 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.00079 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.033283 | 148 | 148 |  |  |  |  | 0.033283 | 4.9259 |  |  |  |  | 0 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.00079 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.033283 | 154 | 154 |  |  |  |  | 0.033283 | 5.1256 |  |  |  |  | 0 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.00079 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.033283 | 293 | 293 |  |  |  |  | 0.033283 | 9.7519 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.00081 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.033303 | 0 | 0 |  |  |  |  | 0.033303 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.00081 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.033303 | 0 | 0 |  |  |  |  | 0.033303 | 0 |  |  |  |  | 0 | 0
8189 | CUECPL2A | 1 | South | YES | 0.000815 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.033308 | 0 | 0 |  |  |  |  | 0.033308 | 0 |  |  |  |  | 0 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | 0.000821 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.033314 | 11 | 11 |  |  |  |  | 0.033314 | 0.36645 |  |  |  |  | 0 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | 0.000821 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.033314 | 11 | 11 |  |  |  |  | 0.033314 | 0.36645 |  |  |  |  | 0 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | 0.000821 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.033314 | 22 | 22 |  |  |  |  | 0.033314 | 0.73291 |  |  |  |  | 0 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.000821 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.033314 | 223.9 | 223.9 |  |  |  |  | 0.033314 | 7.459 |  |  |  |  | 0 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.000821 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.033314 | 224.6 | 224.6 |  |  |  |  | 0.033314 | 7.4823 |  |  |  |  | 0 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.000821 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.033314 | 225 | 225 |  |  |  |  | 0.033314 | 7.4956 |  |  |  |  | 0 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.000821 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.033314 | 226.7 | 226.7 |  |  |  |  | 0.033314 | 7.5523 |  |  |  |  | 0 | 0
5509 | RAYBURNCC10 | 1 | South | YES | 0.000848 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.033341 | 37.3 | 37.3 |  |  |  |  | 0.033341 | 1.2436 |  |  |  |  | 0 | 0
5511 | RAYBURNCC7 | 1 | South | YES | 0.000848 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.033341 | 47.5 | 47.5 |  |  |  |  | 0.033341 | 1.5837 |  |  |  |  | 0 | 0
5508 | RAYBURNCC9 | 1 | South | YES | 0.000848 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.033341 | 47.7 | 47.7 |  |  |  |  | 0.033341 | 1.5904 |  |  |  |  | 0 | 0
5512 | RAYBURNCC8 | 1 | South | YES | 0.000848 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.033341 | 49.3 | 49.3 |  |  |  |  | 0.033341 | 1.6437 |  |  |  |  | 0 | 0
8173 | VICEC51A | 5 | South | YES | 0.000854 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.033347 | 144 | 144 |  |  |  |  | 0.033347 | 4.802 |  |  |  |  | 0 | 0
8174 | VICEC61A | 6 | South | YES | 0.000854 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.033347 | 188 | 188 |  |  |  |  | 0.033347 | 6.2692 |  |  |  |  | 0 | 0
8066 | DUP1V#1 | 1 | South | YES | 0.000866 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.033359 | 0 | 0 |  |  |  |  | 0.033359 | 0 |  |  |  |  | 0 | 0
80224 | VISTRONG1 | 1 | South | YES | 0.000882 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.033375 | 0 | 0 |  |  |  |  | 0.033375 | 0 |  |  |  |  | 0 | 0
80225 | VISTRONG2 | 2 | South | YES | 0.000882 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.033375 | 0 | 0 |  |  |  |  | 0.033375 | 0 |  |  |  |  | 0 | 0
80227 | AIRCO G | 1 | South | YES | 0.000884 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.033377 | 0 | 0 |  |  |  |  | 0.033377 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.000891 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.033384 | 0 | 0 |  |  |  |  | 0.033384 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.000891 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.033384 | 0 | 0 |  |  |  |  | 0.033384 | 0 |  |  |  |  | 0 | 0
8147 | UCAR #2 | 10 | South | YES | 0.000895 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 |  |  |  |  | 0 | 0
8148 | UCAR #1 | 2 | South | YES | 0.000895 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 9 | South | YES | 0.000895 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 8 | South | YES | 0.000895 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 |  |  |  |  | 0 | 0
80138 | CSDR7 | 7 | South | YES | 0.000895 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 6 | South | YES | 0.000895 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 5 | South | YES | 0.000895 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 |  |  |  |  | 0 | 0
80140 | CSDR11 | 11 | South | YES | 0.000895 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.033388 | 0 | 0 |  |  |  |  | 0.033388 | 0 |  |  |  |  | 0 | 0
9017 | SANDH_G2 | 2 | South | YES | 0.00093 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.033423 | 46 | 46 |  |  |  |  | 0.033423 | 1.5375 |  |  |  |  | 0 | 0
9018 | SANDH_G3 | 3 | South | YES | 0.00093 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.033423 | 46 | 46 |  |  |  |  | 0.033423 | 1.5375 |  |  |  |  | 0 | 0
9019 | SANDH_G4 | 4 | South | YES | 0.00093 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.033423 | 47 | 47 |  |  |  |  | 0.033423 | 1.5709 |  |  |  |  | 0 | 0
9016 | SANDH_G1 | 1 | South | YES | 0.00093 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.033423 | 49 | 49 |  |  |  |  | 0.033423 | 1.6377 |  |  |  |  | 0 | 0
9021 | SANDHG5C | 5C | South | YES | 0.00093 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.033423 | 148 | 148 |  |  |  |  | 0.033423 | 4.9466 |  |  |  |  | 0 | 0
9020 | SANDHG5A | 5A | South | YES | 0.00093 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.033423 | 155 | 155 |  |  |  |  | 0.033423 | 5.1806 |  |  |  |  | 0 | 0
9000 | DECKR_G1 | 1 | South | YES | 0.000931 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.033424 | 321 | 321 |  |  |  |  | 0.033424 | 10.7291 |  |  |  |  | 0 | 0
9001 | DECKR_G2 | 2 | South | YES | 0.000931 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.033424 | 426 | 426 |  |  |  |  | 0.033424 | 14.2386 |  |  |  |  | 0 | 0
80226 | ALCOA G | 1 | South | YES | 0.000945 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.033438 | 0 | 0 |  |  |  |  | 0.033438 | 0 |  |  |  |  | 0 | 0
8134 | FOR #1 | 1 | South | YES | 0.000958 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
8138 | FOR #2 | 2 | South | YES | 0.000958 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
8153 | FOR #3 | 3 | South | YES | 0.000958 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
8154 | FOR #4 | 4 | South | YES | 0.000958 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
8155 | FOR #5 | 5 | South | YES | 0.000958 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
8156 | FOR #6 | 6 | South | YES | 0.000958 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
8157 | FOR #7 | 7 | South | YES | 0.000958 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
80051 | FOR #8 | 8 | South | YES | 0.000958 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
80052 | FOR #9 | 9 | South | YES | 0.000958 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
80053 | FOR #10 | 10 | South | YES | 0.000958 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.033451 | 0 | 0 |  |  |  |  | 0.033451 | 0 |  |  |  |  | 0 | 0
9002 | DECKR_G3 | 3 | South | YES | 0.000958 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.033451 | 42 | 42 |  |  |  |  | 0.033451 | 1.4049 |  |  |  |  | 0 | 0
9003 | DECKR_G4 | 4 | South | YES | 0.000958 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.033451 | 44 | 44 |  |  |  |  | 0.033451 | 1.4718 |  |  |  |  | 0 | 0
9004 | DECKR_G5 | 5 | South | YES | 0.000958 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.033451 | 44 | 44 |  |  |  |  | 0.033451 | 1.4718 |  |  |  |  | 0 | 0
9005 | DECKR_G6 | 6 | South | YES | 0.000958 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.033451 | 47 | 47 |  |  |  |  | 0.033451 | 1.5722 |  |  |  |  | 0 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.001025 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.033518 | 132 | 132 |  |  |  |  | 0.033518 | 4.4244 |  |  |  |  | 0 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.001025 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.033518 | 139 | 139 |  |  |  |  | 0.033518 | 4.659 |  |  |  |  | 0 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.001025 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.033518 | 329 | 329 |  |  |  |  | 0.033518 | 11.0274 |  |  |  |  | 0 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.001094 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.033587 | 149.5 | 149.5 |  |  |  |  | 0.033587 | 5.0213 |  |  |  |  | 0 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.001094 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.033587 | 152.5 | 152.5 |  |  |  |  | 0.033587 | 5.122 |  |  |  |  | 0 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.001094 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.033587 | 232.6 | 232.6 |  |  |  |  | 0.033587 | 7.8123 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.001098 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.033591 | 50 | 50 |  |  |  |  | 0.033591 | 1.6795 |  |  |  |  | 0 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | -0.02998 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.033615 | 0 | 150 |  |  | 0 | 0 | -0.033615 | 0 |  |  |  |  | 0 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.03 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.033635 | 0 | 80 |  |  | 0 | 0 | -0.033635 | 0 |  |  |  |  | 0 | 0
60016 | WOODWRD11A | 1 | West | YES | -0.030004 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.033639 | 0 | 80 |  |  | 0 | 0 | -0.033639 | 0 |  |  |  |  | 0 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.001161 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.033654 | 0 | 436 |  |  |  |  | 0.033654 | 14.6731 |  |  |  |  | 0 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.001162 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.033655 | 158 | 158 |  |  |  |  | 0.033655 | 5.3175 |  |  |  |  | 0 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.001162 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.033655 | 160 | 160 |  |  |  |  | 0.033655 | 5.3848 |  |  |  |  | 0 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.001162 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.033655 | 175 | 175 |  |  |  |  | 0.033655 | 5.8896 |  |  |  |  | 0 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.001162 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.033655 | 0 | 598 |  |  |  |  | 0.033655 | 20.1257 |  |  |  |  | 0 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.001162 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.033655 | 0 | 606 |  |  |  |  | 0.033655 | 20.3949 |  |  |  |  | 0 | 0
6016 | SWMESA | 1 | West | YES | -0.030023 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.033658 | 0 | 75 |  |  | 0 | 0 | -0.033658 | 0 |  |  |  |  | 0 | 0
60003 | KING_NE1A | 1 | West | YES | -0.030023 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033658 | 0 | 80 |  |  | 0 | 0 | -0.033658 | 0 |  |  |  |  | 0 | 0
60005 | KING_SE1A | 1 | West | YES | -0.030023 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.033658 | 0 | 40 |  |  | 0 | 0 | -0.033658 | 0 |  |  |  |  | 0 | 0
60201 | RIO DRCS | F | West | YES | -0.030065 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.0337 | 0 | 0 |  |  | 0 | 0 | -0.0337 | 0 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 1 | West | YES | -0.030077 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.033712 | 0 | 150 |  |  | 0 | 0 | -0.033712 | 0 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 2 | West | YES | -0.030077 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.033712 | 0 | 220 |  |  | 0 | 0 | -0.033712 | 0 |  |  |  |  | 0 | 0
11065 | ELBOWCK_1G | 1 | West | YES | -0.030077 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.033712 | 0 | 121.9 |  |  | 0 | 0 | -0.033712 | 0 |  |  |  |  | 0 | 0
60007 | KING_SW1A | 1 | West | YES | -0.030138 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033773 | 0 | 80 |  |  | 0 | 0 | -0.033773 | 0 |  |  |  |  | 0 | 0
60019 | KING_NW1A | 1 | West | YES | -0.030138 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.033773 | 0 | 80 |  |  | 0 | 0 | -0.033773 | 0 |  |  |  |  | 0 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | 0.001404 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.033897 | 0 | 0 |  |  |  |  | 0.033897 | 0 |  |  |  |  | 0 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | 0.001404 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.033897 | 0 | 0 |  |  |  |  | 0.033897 | 0 |  |  |  |  | 0 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.00141 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.033903 | 0 | 580 |  |  |  |  | 0.033903 | 19.6637 |  |  |  |  | 0 | 0
48731 | CBE_GT1 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 |  |  |  |  | 0 | 0
48732 | CBE_GT2 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 |  |  |  |  | 0 | 0
48734 | CBE_GT3 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 |  |  |  |  | 0 | 0
48735 | CBE_GT4 | 1 | Houston | YES | 0.001422 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.033915 | 76 | 76 |  |  |  |  | 0.033915 | 2.5775 |  |  |  |  | 0 | 0
48733 | CBE_ST12 | 1 | Houston | YES | 0.001422 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.033915 | 105 | 105 |  |  |  |  | 0.033915 | 3.5611 |  |  |  |  | 0 | 0
48736 | CBE_ST34 | 1 | Houston | YES | 0.001422 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.033915 | 105 | 105 |  |  |  |  | 0.033915 | 3.5611 |  |  |  |  | 0 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.00144 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.033933 | 0 | 0 |  |  |  |  | 0.033933 | 0 |  |  |  |  | 0 | 0
1045 | CALENG1G_1G | 1 | West | YES | -0.030406 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0 |  |  |  |  | 0 | 0
1046 | CALENG2G_2G | 2 | West | YES | -0.030406 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0 |  |  |  |  | 0 | 0
1047 | CALENG3G_3G | 3 | West | YES | -0.030406 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.034041 | 0 | 0 |  |  | 0 | 0 | -0.034041 | 0 |  |  |  |  | 0 | 0
49851 | DOW17000 | 37 | Houston | YES | 0.001551 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49858 | DOW38100 | 31 | Houston | YES | 0.001551 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49859 | DOW38200 | 33 | Houston | YES | 0.001551 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49860 | DOW38300 | 32 | Houston | YES | 0.001551 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49862 | DOW39100 | 36 | Houston | YES | 0.001551 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49863 | DOW39200 | 35 | Houston | YES | 0.001551 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49865 | DOW41000 | 41 | Houston | YES | 0.001551 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49866 | DOW42000 | 42 | Houston | YES | 0.001551 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49869 | DOW49000 | 45 | Houston | YES | 0.001551 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49870 | DOW61000 | 61 | Houston | YES | 0.001551 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49871 | DOW62000 | 62 | Houston | YES | 0.001551 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49872 | DOW63000 | 63 | Houston | YES | 0.001551 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49873 | DOW64000 | 64 | Houston | YES | 0.001551 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49876 | DOW65000 | 65 | Houston | YES | 0.001551 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49877 | DOW66000 | 66 | Houston | YES | 0.001551 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49878 | DOW67000 | 67 | Houston | YES | 0.001551 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49882 | DOW81000 | 81 | Houston | YES | 0.001551 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49884 | DOW82000 | 82 | Houston | YES | 0.001551 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49885 | DOW83000 | 83 | Houston | YES | 0.001551 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
49886 | DOW84000 | 84 | Houston | YES | 0.001551 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.034044 | 0 | 0 |  |  |  |  | 0.034044 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.001577 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.03407 | 0 | 0 |  |  |  |  | 0.03407 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.001577 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.03407 | 0 | 0 |  |  |  |  | 0.03407 | 0 |  |  |  |  | 0 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.001588 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.034081 | 0 | 581 |  |  |  |  | 0.034081 | 19.801 |  |  |  |  | 0 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.0016 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 |  |  |  |  | 0 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.0016 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 |  |  |  |  | 0 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.0016 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 |  |  |  |  | 0 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.0016 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.034093 | 0 | 0 |  |  |  |  | 0.034093 | 0 |  |  |  |  | 0 | 0
48730 | MNS_GT | 1 | Houston | YES | 0.001674 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.034167 | 0 | 0 |  |  |  |  | 0.034167 | 0 |  |  |  |  | 0 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.001679 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.034172 | 166.4 | 166.4 |  |  |  |  | 0.034172 | 5.6862 |  |  |  |  | 0 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.001679 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.034172 | 167.7 | 167.7 |  |  |  |  | 0.034172 | 5.7306 |  |  |  |  | 0 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.001679 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.034172 | 252.4 | 252.4 |  |  |  |  | 0.034172 | 8.625 |  |  |  |  | 0 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.001679 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 564 |  |  |  |  | 0.034172 | 19.273 |  |  |  |  | 0 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.001679 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 603 |  |  |  |  | 0.034172 | 20.6057 |  |  |  |  | 0 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.001679 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.034172 | 0 | 651 |  |  |  |  | 0.034172 | 22.2459 |  |  |  |  | 0 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.001685 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.034178 | 0 | 0 |  |  |  |  | 0.034178 | 0 |  |  |  |  | 0 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.001693 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.034186 | 13 | 13 |  |  |  |  | 0.034186 | 0.44442 |  |  |  |  | 0 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.001693 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.034186 | 166 | 166 |  |  |  |  | 0.034186 | 5.6749 |  |  |  |  | 0 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.001693 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.034186 | 166 | 166 |  |  |  |  | 0.034186 | 5.6749 |  |  |  |  | 0 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.001693 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.034186 | 248 | 248 |  |  |  |  | 0.034186 | 8.4781 |  |  |  |  | 0 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.001693 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.034186 | 546 | 546 |  |  |  |  | 0.034186 | 18.6655 |  |  |  |  | 0 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.001693 | 585.3 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.034186 | 0 | 654 |  |  |  |  | 0.034186 | 22.3576 |  |  |  |  | 0 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.001734 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.001734 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.001734 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.001734 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.001734 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.001734 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.001734 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.001734 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.001734 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.001734 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.001734 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.001734 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.001734 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.001734 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.001734 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.034227 | 0 | 0 |  |  |  |  | 0.034227 | 0 |  |  |  |  | 0 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | 0.001753 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.034246 | 0 | 0 |  |  |  |  | 0.034246 | 0 |  |  |  |  | 0 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.001767 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 |  |  |  |  | 0 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.001767 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 |  |  |  |  | 0 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.001767 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 |  |  |  |  | 0 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.001767 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 |  |  |  |  | 0 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.001767 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.03426 | 0 | 0 |  |  |  |  | 0.03426 | 0 |  |  |  |  | 0 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.001772 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 |  |  |  |  | 0 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.001772 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 |  |  |  |  | 0 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.001772 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 |  |  |  |  | 0 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.001772 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.034265 | 0 | 0 |  |  |  |  | 0.034265 | 0 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | B | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | A | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | C | Houston | YES | 0.00178 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.034273 | 47 | 47 |  |  |  |  | 0.034273 | 1.6108 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | F | Houston | YES | 0.00178 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.034273 | 54 | 54 |  |  |  |  | 0.034273 | 1.8507 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | D | Houston | YES | 0.00178 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.034273 | 55 | 55 |  |  |  |  | 0.034273 | 1.885 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | E | Houston | YES | 0.00178 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.034273 | 57 | 57 |  |  |  |  | 0.034273 | 1.9536 |  |  |  |  | 0 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.001782 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.034275 | 0 | 0 |  |  |  |  | 0.034275 | 0 |  |  |  |  | 0 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.001782 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.034275 | 0 | 0 |  |  |  |  | 0.034275 | 0 |  |  |  |  | 0 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.001784 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.034277 | 157 | 157 |  |  |  |  | 0.034277 | 5.3815 |  |  |  |  | 0 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.001784 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.034277 | 157.1 | 157.1 |  |  |  |  | 0.034277 | 5.3849 |  |  |  |  | 0 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.001784 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.034277 | 157.5 | 157.5 |  |  |  |  | 0.034277 | 5.3986 |  |  |  |  | 0 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.001784 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.034277 | 163.2 | 163.2 |  |  |  |  | 0.034277 | 5.594 |  |  |  |  | 0 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.001784 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.034277 | 282 | 282 |  |  |  |  | 0.034277 | 9.6661 |  |  |  |  | 0 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.001787 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.03428 | 0 | 0 |  |  |  |  | 0.03428 | 0 |  |  |  |  | 0 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.00179 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.034283 | 0 | 0 |  |  |  |  | 0.034283 | 0 |  |  |  |  | 0 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.00179 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.034283 | 0 | 0 |  |  |  |  | 0.034283 | 0 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | 0.00179 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.034283 | 12 | 12 |  |  |  |  | 0.034283 | 0.4114 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | 0.00179 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.034283 | 18 | 18 |  |  |  |  | 0.034283 | 0.61709 |  |  |  |  | 0 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.00179 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.034283 | 165 | 165 |  |  |  |  | 0.034283 | 5.6567 |  |  |  |  | 0 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.00179 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.034283 | 176 | 176 |  |  |  |  | 0.034283 | 6.0338 |  |  |  |  | 0 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.00179 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.034283 | 213 | 213 |  |  |  |  | 0.034283 | 7.3023 |  |  |  |  | 0 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.001791 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 |  |  |  |  | 0 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.001791 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 |  |  |  |  | 0 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.001791 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 |  |  |  |  | 0 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.001791 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 |  |  |  |  | 0 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.001791 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 |  |  |  |  | 0 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.001791 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 |  |  |  |  | 0 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.001791 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.034284 | 0 | 0 |  |  |  |  | 0.034284 | 0 |  |  |  |  | 0 | 0
48845 | SOL_GT1 | 1 | Houston | YES | 0.001791 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.034284 | 16.2 | 16.2 |  |  |  |  | 0.034284 | 0.5554 |  |  |  |  | 0 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.001791 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.034284 | 228 | 228 |  |  |  |  | 0.034284 | 7.8167 |  |  |  |  | 0 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.001794 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0 |  |  |  |  | 0 | 0
48821 | SHELLG2 | 2 | Houston | YES | 0.001794 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.001794 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.001794 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.034287 | 0 | 0 |  |  |  |  | 0.034287 | 0 |  |  |  |  | 0 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.001799 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.034292 | 0 | 0 |  |  |  |  | 0.034292 | 0 |  |  |  |  | 0 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.0018 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.034293 | 39 | 39 |  |  |  |  | 0.034293 | 1.3374 |  |  |  |  | 0 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.0018 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.034293 | 39 | 39 |  |  |  |  | 0.034293 | 1.3374 |  |  |  |  | 0 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.0018 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.034293 | 42 | 42 |  |  |  |  | 0.034293 | 1.4403 |  |  |  |  | 0 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.0018 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.034293 | 42 | 42 |  |  |  |  | 0.034293 | 1.4403 |  |  |  |  | 0 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.001801 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.034294 | 0 | 0 |  |  |  |  | 0.034294 | 0 |  |  |  |  | 0 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.001801 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.034294 | 0 | 0 |  |  |  |  | 0.034294 | 0 |  |  |  |  | 0 | 0
48875 | THW_3132 | B | Houston | YES | 0.001809 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.034302 | 53 | 53 |  |  |  |  | 0.034302 | 1.818 |  |  |  |  | 0 | 0
48875 | THW_3132 | A | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866 |  |  |  |  | 0 | 0
48877 | THW_3334 | C | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866 |  |  |  |  | 0 | 0
48879 | THW_4142 | F | Houston | YES | 0.001809 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.034302 | 55 | 55 |  |  |  |  | 0.034302 | 1.8866 |  |  |  |  | 0 | 0
48879 | THW_4142 | E | Houston | YES | 0.001809 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.034302 | 56 | 56 |  |  |  |  | 0.034302 | 1.9209 |  |  |  |  | 0 | 0
48877 | THW_3334 | D | Houston | YES | 0.001809 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.034302 | 57 | 57 |  |  |  |  | 0.034302 | 1.9552 |  |  |  |  | 0 | 0
48881 | THW_4344 | G | Houston | YES | 0.001809 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.034302 | 58 | 58 |  |  |  |  | 0.034302 | 1.9895 |  |  |  |  | 0 | 0
48881 | THW_4344 | H | Houston | YES | 0.001809 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.034302 | 58 | 58 |  |  |  |  | 0.034302 | 1.9895 |  |  |  |  | 0 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.001809 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.034302 | 107 | 107 |  |  |  |  | 0.034302 | 3.6703 |  |  |  |  | 0 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.001809 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.034302 | 108 | 108 |  |  |  |  | 0.034302 | 3.7046 |  |  |  |  | 0 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.001813 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.034306 | 746 | 746 |  |  |  |  | 0.034306 | 25.5922 |  |  |  |  | 0 | 0
49803 | EXN_15GT | 1 | Houston | YES | 0.001817 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49804 | EXN_16GT | 2 | Houston | YES | 0.001817 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49805 | EXN_17GT | 3 | Houston | YES | 0.001817 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49826 | EXN938GT | 5 | Houston | YES | 0.001817 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49828 | EXN941GT | 10 | Houston | YES | 0.001817 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49829 | EXN942GT | 11 | Houston | YES | 0.001817 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49830 | EXN943GT | 12 | Houston | YES | 0.001817 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49831 | EXN944GT | 13 | Houston | YES | 0.001817 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49832 | EXN945GT | 9 | Houston | YES | 0.001817 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49837 | EXN_GT | 4 | Houston | YES | 0.001817 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
49838 | EXN_14GT | 14 | Houston | YES | 0.001817 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.03431 | 0 | 0 |  |  |  |  | 0.03431 | 0 |  |  |  |  | 0 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.001817 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.03431 | 12 | 12 |  |  |  |  | 0.03431 | 0.41172 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 1 | Houston | YES | 0.001821 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 2 | Houston | YES | 0.001821 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.001821 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.001821 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.001821 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.001821 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.001821 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.001821 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.001821 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.001821 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.034314 | 0 | 0 |  |  |  |  | 0.034314 | 0 |  |  |  |  | 0 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.001821 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.034314 | 744 | 744 |  |  |  |  | 0.034314 | 25.5296 |  |  |  |  | 0 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.001823 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.034316 | 0 | 0 |  |  |  |  | 0.034316 | 0 |  |  |  |  | 0 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025 |  |  |  |  | 0 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025 |  |  |  |  | 0 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.001824 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.034317 | 172 | 172 |  |  |  |  | 0.034317 | 5.9025 |  |  |  |  | 0 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.00183 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.034323 | 158.9 | 158.9 |  |  |  |  | 0.034323 | 5.4539 |  |  |  |  | 0 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.00183 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.034323 | 161.4 | 161.4 |  |  |  |  | 0.034323 | 5.5397 |  |  |  |  | 0 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.00183 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.034323 | 162.8 | 162.8 |  |  |  |  | 0.034323 | 5.5878 |  |  |  |  | 0 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.00183 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.034323 | 269.2 | 269.2 |  |  |  |  | 0.034323 | 9.2397 |  |  |  |  | 0 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.001833 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.034326 | 398 | 398 |  |  |  |  | 0.034326 | 13.6617 |  |  |  |  | 0 | 0
48886 | THW_5354 | C | Houston | YES | 0.001836 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.034329 | 57 | 57 |  |  |  |  | 0.034329 | 1.9568 |  |  |  |  | 0 | 0
48887 | THW_5556 | F | Houston | YES | 0.001836 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.034329 | 57 | 57 |  |  |  |  | 0.034329 | 1.9568 |  |  |  |  | 0 | 0
48885 | THW_5152 | A | Houston | YES | 0.001836 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.034329 | 58 | 58 |  |  |  |  | 0.034329 | 1.9911 |  |  |  |  | 0 | 0
48886 | THW_5354 | D | Houston | YES | 0.001836 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.034329 | 58 | 58 |  |  |  |  | 0.034329 | 1.9911 |  |  |  |  | 0 | 0
48885 | THW_5152 | B | Houston | YES | 0.001836 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.034329 | 59 | 59 |  |  |  |  | 0.034329 | 2.0254 |  |  |  |  | 0 | 0
48887 | THW_5556 | E | Houston | YES | 0.001836 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.034329 | 59 | 59 |  |  |  |  | 0.034329 | 2.0254 |  |  |  |  | 0 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.001873 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 |  |  |  |  | 0 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.001873 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 |  |  |  |  | 0 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.001873 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 |  |  |  |  | 0 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.001873 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 |  |  |  |  | 0 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.001873 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.034366 | 0 | 0 |  |  |  |  | 0.034366 | 0 |  |  |  |  | 0 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.002026 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | 0.034519 | 0 | 0 | 0 | 0 |  |  | 0.034519 | 0 |  |  |  |  | 0 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.002026 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.034519 | 0 | 0 | 0 | 0 |  |  | 0.034519 | 0 |  |  |  |  | 0 | 0
1878 | WLFHOLW_2G | 2 | North | YES | 0.00218 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.034673 | 215.7 | 215.7 | 0.47023 | 215.7 |  |  | 0.034673 | 7.479 |  |  |  |  | 0 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.00218 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.034673 | 217.3 | 217.3 | 0.47371 | 217.3 |  |  | 0.034673 | 7.5344 |  |  |  |  | 0 | 0
1879 | WLFHOLW_3G | 3 | North | YES | 0.00218 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.034673 | 272.4 | 272.4 | 0.59383 | 272.4 |  |  | 0.034673 | 9.4449 |  |  |  |  | 0 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.002212 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.034705 | 154.2 | 154.2 | 0.34109 | 154.2 |  |  | 0.034705 | 5.3515 |  |  |  |  | 0 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | 0.002212 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.034705 | 158 | 158 | 0.3495 | 158 |  |  | 0.034705 | 5.4834 |  |  |  |  | 0 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | 0.002212 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.034705 | 159 | 159 | 0.35171 | 159 |  |  | 0.034705 | 5.5181 |  |  |  |  | 0 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | 0.002212 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.034705 | 380 | 380 | 0.84056 | 380 |  |  | 0.034705 | 13.1879 |  |  |  |  | 0 | 0
11014 | NAV6ST | 1 | West | YES | -0.031081 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.034716 | 115 | 115 |  |  | -3.5743 | 115 | -0.034716 | -3.9924 |  |  |  |  | 0 | 0
11011 | NAV3ST | 1 | West | YES | -0.031081 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.034716 | 92.8 | 92.8 |  |  | -2.8843 | 92.8 | -0.034716 | -3.2217 |  |  |  |  | 0 | 0
11012 | NAV4CT | 1 | West | YES | -0.031081 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.034716 | 80 | 80 |  |  | -2.4865 | 80 | -0.034716 | -2.7773 |  |  |  |  | 0 | 0
11013 | NAV5CT | 1 | West | YES | -0.031081 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.034716 | 80 | 80 |  |  | -2.4865 | 80 | -0.034716 | -2.7773 |  |  |  |  | 0 | 0
11009 | NAV2CT | 1 | West | YES | -0.031081 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.034716 | 71.4 | 71.4 |  |  | -2.2192 | 71.4 | -0.034716 | -2.4788 |  |  |  |  | 0 | 0
11001 | NAV1CT | 1 | West | YES | -0.031081 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.034716 | 70.4 | 70.4 |  |  | -2.1881 | 70.4 | -0.034716 | -2.444 |  |  |  |  | 0 | 0
11025 | TIEHVSG_2G | 1 | West | YES | -0.031092 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.034727 | 213.2 | 213.2 |  |  | -6.6288 | 213.2 | -0.034727 | -7.4039 |  |  |  |  | 0 | 0
11020 | TIEHVSG_1G | 1 | West | YES | -0.031092 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.034727 | 208.2 | 208.2 |  |  | -6.4734 | 208.2 | -0.034727 | -7.2303 |  |  |  |  | 0 | 0
11024 | TIEHVCG_4G | 1 | West | YES | -0.031092 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.034727 | 147 | 147 |  |  | -4.5705 | 147 | -0.034727 | -5.1049 |  |  |  |  | 0 | 0
11021 | TIEHVCG_1G | 1 | West | YES | -0.031092 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.034727 | 142.1 | 142.1 |  |  | -4.4182 | 142.1 | -0.034727 | -4.9348 |  |  |  |  | 0 | 0
11023 | TIEHVCG_3G | 1 | West | YES | -0.031092 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.034727 | 137.4 | 137.4 |  |  | -4.272 | 137.4 | -0.034727 | -4.7716 |  |  |  |  | 0 | 0
11022 | TIEHVCG_2G | 1 | West | YES | -0.031092 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.034727 | 132.4 | 132.4 |  |  | -4.1166 | 132.4 | -0.034727 | -4.5979 |  |  |  |  | 0 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.002279 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.034772 | 46 | 46 | 0.10483 | 46 |  |  | 0.034772 | 1.5995 |  |  |  |  | 0 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.002279 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.034772 | 48 | 48 | 0.10939 | 48 |  |  | 0.034772 | 1.6691 |  |  |  |  | 0 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.002279 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.034772 | 105 | 105 | 0.2393 | 105 |  |  | 0.034772 | 3.6511 |  |  |  |  | 0 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | 0.002282 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.034775 | 0 | 463 | 1.0566 | 463 |  |  | 0.034775 | 16.1008 |  |  |  |  | 0 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | 0.002284 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0 |  |  |  |  | 0 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.002284 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0 |  |  |  |  | 0 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | 0.002284 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0 |  |  |  |  | 0 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.002284 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.034777 | 0 | 0 | 0 | 0 |  |  | 0.034777 | 0 |  |  |  |  | 0 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.002284 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.034777 | 17 | 17 | 0.038828 | 17 |  |  | 0.034777 | 0.59121 |  |  |  |  | 0 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.002285 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.034778 | 32 | 32 | 0.07312 | 32 |  |  | 0.034778 | 1.1129 |  |  |  |  | 0 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | 0.002329 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.034822 | 75 | 75 | 0.17467 | 75 |  |  | 0.034822 | 2.6116 |  |  |  |  | 0 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | 0.002329 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.034822 | 222 | 222 | 0.51704 | 222 |  |  | 0.034822 | 7.7305 |  |  |  |  | 0 | 0
3403 | THOUSE_1G | 1 | North | YES | 0.002398 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.034891 | 563 | 563 | 1.3501 | 563 |  |  | 0.034891 | 19.6436 |  |  |  |  | 0 | 0
3404 | THOUSE_2G | 2 | North | YES | 0.002398 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.034891 | 807 | 807 | 1.9352 | 807 |  |  | 0.034891 | 28.157 |  |  |  |  | 0 | 0
239 | BOSQUESW502 | 1 | North | YES | 0.00249 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.034983 | 149 | 149 | 0.37101 | 149 |  |  | 0.034983 | 5.2125 |  |  |  |  | 0 | 0
247 | BOSQUESW501 | 2 | North | YES | 0.00249 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.034983 | 156 | 156 | 0.38844 | 156 |  |  | 0.034983 | 5.4573 |  |  |  |  | 0 | 0
238 | BOSQUESW505 | 1 | North | YES | 0.00249 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.034983 | 255 | 255 | 0.63495 | 255 |  |  | 0.034983 | 8.9207 |  |  |  |  | 0 | 0
39960 | TNTNPONE_18 | 1 | North | YES | 0.002507 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.035 | 0 | 152.3 | 0.38182 | 152.3 |  |  | 0.035 | 5.3305 |  |  |  |  | 0 | 0
39970 | TNTNPONE_28 | 1 | North | YES | 0.002507 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.035 | 0 | 153 | 0.38357 | 153 |  |  | 0.035 | 5.355 |  |  |  |  | 0 | 0
48722 | LEG_2___2 | 2 | North | YES | 0.002597 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.03509 | 0 | 819 | 2.1269 | 819 |  |  | 0.03509 | 28.7387 |  |  |  |  | 0 | 0
48721 | LEG_1___1 | 1 | North | YES | 0.002597 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.03509 | 0 | 827 | 2.1477 | 827 |  |  | 0.03509 | 29.0194 |  |  |  |  | 0 | 0
253 | BOSQUESW804 | 2 | North | YES | 0.002639 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | 0.035132 | 80 | 80 | 0.21112 | 80 |  |  | 0.035132 | 2.8106 |  |  |  |  | 0 | 0
251 | BOSQUESW803 | 2 | North | YES | 0.002639 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | 0.035132 | 150 | 150 | 0.39585 | 150 |  |  | 0.035132 | 5.2698 |  |  |  |  | 0 | 0
1889 | DECRDOVA_1G | 1 | North | YES | 0.002771 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.035264 | 779 | 779 | 2.1586 | 779 |  |  | 0.035264 | 27.4706 |  |  |  |  | 0 | 0
3382 | BBRN_2G | 2 | North | YES | 0.002832 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.035325 | 0 | 589 | 1.668 | 589 |  |  | 0.035325 | 20.8064 |  |  |  |  | 0 | 0
3381 | BBRN_1G | 1 | North | YES | 0.002832 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.035325 | 0 | 618 | 1.7502 | 618 |  |  | 0.035325 | 21.8308 |  |  |  |  | 0 | 0
13131 | CALFREST_1G | 1 | North | YES | 0.002871 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.035364 | 150.7 | 150.7 | 0.43266 | 150.7 |  |  | 0.035364 | 5.3293 |  |  |  |  | 0 | 0
13132 | CALFREST_2G | 2 | North | YES | 0.002871 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.035364 | 151 | 151 | 0.43352 | 151 |  |  | 0.035364 | 5.34 |  |  |  |  | 0 | 0
13133 | CALFREST_3G | 3 | North | YES | 0.002871 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.035364 | 177.4 | 177.4 | 0.50932 | 177.4 |  |  | 0.035364 | 6.2736 |  |  |  |  | 0 | 0
13134 | CALFREST_4G | 4 | North | YES | 0.002882 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.035375 | 151.5 | 151.5 | 0.43662 | 151.5 |  |  | 0.035375 | 5.3593 |  |  |  |  | 0 | 0
13135 | CALFREST_5G | 5 | North | YES | 0.002882 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.035375 | 152.3 | 152.3 | 0.43893 | 152.3 |  |  | 0.035375 | 5.3876 |  |  |  |  | 0 | 0
13136 | CALFREST_6G | 6 | North | YES | 0.002882 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.035375 | 177.5 | 177.5 | 0.51155 | 177.5 |  |  | 0.035375 | 6.2791 |  |  |  |  | 0 | 0
1944 | MDLTHELP_4G | 4 | North | YES | 0.00297 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.035463 | 211 | 211 | 0.62667 | 211 |  |  | 0.035463 | 7.4827 |  |  |  |  | 0 | 0
1943 | MDLTHELP_3G | 3 | North | YES | 0.00297 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.035463 | 212 | 212 | 0.62964 | 212 |  |  | 0.035463 | 7.5181 |  |  |  |  | 0 | 0
1937 | MDLTHELP_5G | 5 | North | YES | 0.00297 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.035463 | 224 | 224 | 0.66528 | 224 |  |  | 0.035463 | 7.9437 |  |  |  |  | 0 | 0
1938 | MDLTHELP_6G | 6 | North | YES | 0.00297 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.035463 | 226 | 226 | 0.67122 | 226 |  |  | 0.035463 | 8.0146 |  |  |  |  | 0 | 0
244 | WHITNYDM01 | 1 | North | YES | 0.003046 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.035539 | 0 | 0 | 0 | 0 |  |  | 0.035539 | 0 |  |  |  |  | 0 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.003046 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.035539 | 0 | 0 | 0 | 0 |  |  | 0.035539 | 0 |  |  |  |  | 0 | 0
1942 | MDLTHELP_2G | 2 | North | YES | 0.00305 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.035543 | 216.1 | 216.1 | 0.65911 | 216.1 |  |  | 0.035543 | 7.6808 |  |  |  |  | 0 | 0
1941 | MDLTHELP_1G | 1 | North | YES | 0.00305 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.035543 | 216.4 | 216.4 | 0.66002 | 216.4 |  |  | 0.035543 | 7.6915 |  |  |  |  | 0 | 0
3126 | TRINIDAD_6G | 1 | North | YES | 0.003054 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.035547 | 224 | 224 | 0.6841 | 224 |  |  | 0.035547 | 7.9625 |  |  |  |  | 0 | 0
3107 | STRYKER_1G | 1 | North | YES | 0.003085 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.035578 | 182 | 182 | 0.56147 | 182 |  |  | 0.035578 | 6.4752 |  |  |  |  | 0 | 0
3108 | STRYKER_2G | 2 | North | YES | 0.003085 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.035578 | 484 | 484 | 1.4931 | 484 |  |  | 0.035578 | 17.2197 |  |  |  |  | 0 | 0
3309 | ASPN_G | 1 | North | YES | 0.003088 | 50 | 0 | 50 |  | 1 | Bio | 1 | 0.035581 | 50 | 50 | 0.1544 | 50 |  |  | 0.035581 | 1.779 |  |  |  |  | 0 | 0
3348 | CHAMPION_1G | MB | North | YES | 0.00309 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.035583 | 0 | 0 | 0 | 0 |  |  | 0.035583 | 0 |  |  |  |  | 0 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.003092 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.035585 | 0 | 0 | 0 | 0 |  |  | 0.035585 | 0 |  |  |  |  | 0 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.003092 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.035585 | 0 | 0 | 0 | 0 |  |  | 0.035585 | 0 |  |  |  |  | 0 | 0
12323 | ENNSTRAC_2G | 2 | North | YES | 0.003103 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.035596 | 116 | 116 | 0.35995 | 116 |  |  | 0.035596 | 4.1291 |  |  |  |  | 0 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | 0.003103 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.035596 | 196 | 196 | 0.60819 | 196 |  |  | 0.035596 | 6.9768 |  |  |  |  | 0 | 0
13117 | TGATEWAY_2G | 2 | North | YES | 0.003111 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.035604 | 130 | 130 | 0.40443 | 130 |  |  | 0.035604 | 4.6285 |  |  |  |  | 0 | 0
13118 | TGATEWAY_3G | 3 | North | YES | 0.003111 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.035604 | 148 | 148 | 0.46043 | 148 |  |  | 0.035604 | 5.2694 |  |  |  |  | 0 | 0
13116 | TGATEWAY_1G | 1 | North | YES | 0.003111 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.035604 | 151 | 151 | 0.46976 | 151 |  |  | 0.035604 | 5.3762 |  |  |  |  | 0 | 0
13119 | TGATEWAY_4G | 4 | North | YES | 0.003111 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.035604 | 399 | 399 | 1.2413 | 399 |  |  | 0.035604 | 14.206 |  |  |  |  | 0 | 0
3097 | MARTLAKE_1G | 1 | North | YES | 0.003135 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 790 | 2.4766 | 790 |  |  | 0.035628 | 28.1461 |  |  |  |  | 0 | 0
3098 | MARTLAKE_2G | 2 | North | YES | 0.003135 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 795 | 2.4923 | 795 |  |  | 0.035628 | 28.3242 |  |  |  |  | 0 | 0
3099 | MARTLAKE_3G | 3 | North | YES | 0.003135 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.035628 | 0 | 804 | 2.5205 | 804 |  |  | 0.035628 | 28.6449 |  |  |  |  | 0 | 0
2414 | MTCK7_G | 7 | North | YES | 0.003263 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.035756 | 115 | 115 | 0.37524 | 115 |  |  | 0.035756 | 4.1119 |  |  |  |  | 0 | 0
2413 | MTCK6_G | 6 | North | YES | 0.003263 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.035756 | 118 | 118 | 0.38503 | 118 |  |  | 0.035756 | 4.2192 |  |  |  |  | 0 | 0
2417 | MTCK8_G | 8 | North | YES | 0.003263 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.035756 | 556 | 556 | 1.8142 | 556 |  |  | 0.035756 | 19.8803 |  |  |  |  | 0 | 0
1008 | PB6GEN_7G | 6 | West | YES | -0.032158 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.035793 | 515 | 515 |  |  | -16.5614 | 515 | -0.035793 | -18.4336 |  |  |  |  | 0 | 0
1007 | PB5GEN_6G | 5 | West | YES | -0.032158 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.035793 | 114 | 114 |  |  | -3.666 | 114 | -0.035793 | -4.0805 |  |  |  |  | 0 | 0
1005 | PBCTDGE_4G | D | West | YES | -0.032158 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.035793 | 68 | 68 |  |  | -2.1867 | 68 | -0.035793 | -2.434 |  |  |  |  | 0 | 0
1004 | PBCTCGE_3G | C | West | YES | -0.032158 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.035793 | 67 | 67 |  |  | -2.1546 | 67 | -0.035793 | -2.3982 |  |  |  |  | 0 | 0
1006 | PBCTEGE_5G | E | West | YES | -0.032158 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.035793 | 67 | 67 |  |  | -2.1546 | 67 | -0.035793 | -2.3982 |  |  |  |  | 0 | 0
1002 | PBCTAGE_1G | A | West | YES | -0.032158 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.035793 | 66 | 66 |  |  | -2.1224 | 66 | -0.035793 | -2.3624 |  |  |  |  | 0 | 0
1003 | PBCTBGE_2G | B | West | YES | -0.032158 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.035793 | 66 | 66 |  |  | -2.1224 | 66 | -0.035793 | -2.3624 |  |  |  |  | 0 | 0
12440 | PARKD_1SVC8 | 1 | North | YES | 0.003301 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035794 | 0 | 0 | 0 | 0 |  |  | 0.035794 | 0 |  |  |  |  | 0 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.003301 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035794 | 0 | 0 | 0 | 0 |  |  | 0.035794 | 0 |  |  |  |  | 0 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.003313 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035806 | 161 | 161 | 0.53339 | 161 |  |  | 0.035806 | 5.7648 |  |  |  |  | 0 | 0
12422 | FPLEFR2B_G | 2 | North | YES | 0.003313 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035806 | 161 | 161 | 0.53339 | 161 |  |  | 0.035806 | 5.7648 |  |  |  |  | 0 | 0
12421 | FPLEFR2A_G | 1 | North | YES | 0.003313 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.035806 | 162 | 162 | 0.53671 | 162 |  |  | 0.035806 | 5.8006 |  |  |  |  | 0 | 0
12423 | FPLEFR2C_G | 3 | North | YES | 0.003313 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.035806 | 163 | 163 | 0.54002 | 163 |  |  | 0.035806 | 5.8364 |  |  |  |  | 0 | 0
12412 | FPLEFR1B_G | 2 | North | YES | 0.003313 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035806 | 164 | 164 | 0.54333 | 164 |  |  | 0.035806 | 5.8722 |  |  |  |  | 0 | 0
12413 | FPLEFR1C_G | 3 | North | YES | 0.003313 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035806 | 164 | 164 | 0.54333 | 164 |  |  | 0.035806 | 5.8722 |  |  |  |  | 0 | 0
12414 | FPLEFR1S_G | 4 | North | YES | 0.003313 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.035806 | 414 | 414 | 1.3716 | 414 |  |  | 0.035806 | 14.8237 |  |  |  |  | 0 | 0
12424 | FPLEFR2S_G | 4 | North | YES | 0.003313 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.035806 | 415 | 415 | 1.3749 | 415 |  |  | 0.035806 | 14.8595 |  |  |  |  | 0 | 0
2451 | LKHB1_G | 1 | North | YES | 0.003324 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.035817 | 391 | 391 | 1.2997 | 391 |  |  | 0.035817 | 14.0044 |  |  |  |  | 0 | 0
2452 | LKHB2_G | 2 | North | YES | 0.003324 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.035817 | 516 | 516 | 1.7152 | 516 |  |  | 0.035817 | 18.4816 |  |  |  |  | 0 | 0
1895 | DECRDOVA_5G | D | North | YES | 0.003377 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.03587 | 68 | 68 | 0.22964 | 68 |  |  | 0.03587 | 2.4392 |  |  |  |  | 0 | 0
1893 | DECRDOVA_3G | B | North | YES | 0.003377 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.03587 | 69 | 69 | 0.23301 | 69 |  |  | 0.03587 | 2.475 |  |  |  |  | 0 | 0
1894 | DECRDOVA_4G | C | North | YES | 0.003377 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.03587 | 69 | 69 | 0.23301 | 69 |  |  | 0.03587 | 2.475 |  |  |  |  | 0 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.003377 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.03587 | 70 | 70 | 0.23639 | 70 |  |  | 0.03587 | 2.5109 |  |  |  |  | 0 | 0
948 | STEAM1 | 1 | North | YES | 0.003387 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.03588 | 20 | 20 | 0.06774 | 20 |  |  | 0.03588 | 0.7176 |  |  |  |  | 0 | 0
949 | STEAM2 | 1 | North | YES | 0.003387 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.03588 | 26 | 26 | 0.088062 | 26 |  |  | 0.03588 | 0.93288 |  |  |  |  | 0 | 0
950 | STEAM3 | 1 | North | YES | 0.003387 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.03588 | 42 | 42 | 0.14225 | 42 |  |  | 0.03588 | 1.507 |  |  |  |  | 0 | 0
837 | NEWMAN_G5 | 1 | North | YES | 0.00339 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.035883 | 40 | 40 | 0.1356 | 40 |  |  | 0.035883 | 1.4353 |  |  |  |  | 0 | 0
845 | OLINGER_G4 | 1 | North | YES | 0.003399 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.035892 | 76 | 76 | 0.25832 | 76 |  |  | 0.035892 | 2.7278 |  |  |  |  | 0 | 0
842 | OLINGER_G1 | 1 | North | YES | 0.003399 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.035892 | 79 | 79 | 0.26852 | 79 |  |  | 0.035892 | 2.8355 |  |  |  |  | 0 | 0
843 | OLINGER_G2 | 1 | North | YES | 0.003399 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.035892 | 110 | 110 | 0.37389 | 110 |  |  | 0.035892 | 3.9481 |  |  |  |  | 0 | 0
844 | OLINGER_G3 | 1 | North | YES | 0.003399 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.035892 | 150 | 150 | 0.50985 | 150 |  |  | 0.035892 | 5.3838 |  |  |  |  | 0 | 0
5925 | DCEAST | EQ | North | YES | 0.003456 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.035949 | 0 | 0 | 0 | 0 |  |  | 0.035949 | 0 |  |  |  |  | 0 | 0
1701 | MOSES_1G | 1 | North | YES | 0.003456 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 558 | 1.9284 | 558 |  |  | 0.035949 | 20.0595 |  |  |  |  | 0 | 0
1702 | MOSES_2G | 2 | North | YES | 0.003456 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 579 | 2.001 | 579 |  |  | 0.035949 | 20.8144 |  |  |  |  | 0 | 0
1703 | MOSES_3G | 3 | North | YES | 0.003456 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.035949 | 0 | 808 | 2.7924 | 808 |  |  | 0.035949 | 29.0468 |  |  |  |  | 0 | 0
1679 | LAMARPWR_2G | 2 | North | YES | 0.003496 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.035989 | 156 | 156 | 0.54538 | 156 |  |  | 0.035989 | 5.6143 |  |  |  |  | 0 | 0
1681 | LAMARPWR_4G | 4 | North | YES | 0.003496 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.035989 | 156 | 156 | 0.54538 | 156 |  |  | 0.035989 | 5.6143 |  |  |  |  | 0 | 0
1682 | LAMARPWR_5G | 5 | North | YES | 0.003496 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.035989 | 157 | 157 | 0.54887 | 157 |  |  | 0.035989 | 5.6503 |  |  |  |  | 0 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.003496 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.035989 | 160 | 160 | 0.55936 | 160 |  |  | 0.035989 | 5.7582 |  |  |  |  | 0 | 0
1680 | LAMARPWR_3G | 3 | North | YES | 0.003496 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.035989 | 196 | 196 | 0.68522 | 196 |  |  | 0.035989 | 7.0538 |  |  |  |  | 0 | 0
1683 | LAMARPWR_6G | 6 | North | YES | 0.003496 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.035989 | 198 | 198 | 0.69221 | 198 |  |  | 0.035989 | 7.1258 |  |  |  |  | 0 | 0
1675 | PEC_1G | 1 | North | YES | 0.003499 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0 |  |  |  |  | 0 | 0
1676 | PEC_2G | 2 | North | YES | 0.003499 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0 |  |  |  |  | 0 | 0
1677 | PEC_3G | 3 | North | YES | 0.003499 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.035992 | 0 | 0 | 0 | 0 |  |  | 0.035992 | 0 |  |  |  |  | 0 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.003508 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.036001 | 156 | 156 | 0.54725 | 156 |  |  | 0.036001 | 5.6161 |  |  |  |  | 0 | 0
2382 | NTHLK2_G | 2 | North | YES | 0.003508 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.036001 | 181 | 181 | 0.63495 | 181 |  |  | 0.036001 | 6.5162 |  |  |  |  | 0 | 0
2383 | NTHLK3_G | 3 | North | YES | 0.003508 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.036001 | 329 | 329 | 1.1541 | 329 |  |  | 0.036001 | 11.8443 |  |  |  |  | 0 | 0
1947 | HANDLEY_3G | 3 | North | YES | 0.003509 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.036002 | 395 | 395 | 1.3861 | 395 |  |  | 0.036002 | 14.2208 |  |  |  |  | 0 | 0
1949 | HANDLEY_5G | 5 | North | YES | 0.003509 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.036002 | 435 | 435 | 1.5264 | 435 |  |  | 0.036002 | 15.6609 |  |  |  |  | 0 | 0
1948 | HANDLEY_4G | 4 | North | YES | 0.00351 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.036003 | 435 | 435 | 1.5269 | 435 |  |  | 0.036003 | 15.6613 |  |  |  |  | 0 | 0
11691 | KMICHICT1_G | 1 | North | YES | 0.003511 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036004 | 144 | 144 | 0.50558 | 144 |  |  | 0.036004 | 5.1846 |  |  |  |  | 0 | 0
11694 | KMICHICT4_G | 4 | North | YES | 0.003511 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036004 | 144 | 144 | 0.50558 | 144 |  |  | 0.036004 | 5.1846 |  |  |  |  | 0 | 0
11692 | KMICHICT2_G | 2 | North | YES | 0.003511 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.036004 | 146 | 146 | 0.51261 | 146 |  |  | 0.036004 | 5.2566 |  |  |  |  | 0 | 0
11695 | KMICHICT5_G | 5 | North | YES | 0.003511 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.036004 | 148 | 148 | 0.51963 | 148 |  |  | 0.036004 | 5.3286 |  |  |  |  | 0 | 0
11696 | KMICHIST6_G | 6 | North | YES | 0.003511 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.036004 | 310 | 310 | 1.0884 | 310 |  |  | 0.036004 | 11.1612 |  |  |  |  | 0 | 0
11693 | KMICHIST3_G | 3 | North | YES | 0.003511 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.036004 | 312 | 312 | 1.0954 | 312 |  |  | 0.036004 | 11.2332 |  |  |  |  | 0 | 0
1689 | VALLEY_3G | 3 | North | YES | 0.003511 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.036004 | 375 | 375 | 1.3166 | 375 |  |  | 0.036004 | 13.5015 |  |  |  |  | 0 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.003619 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.036112 | 170 | 170 | 0.61523 | 170 |  |  | 0.036112 | 6.139 |  |  |  |  | 0 | 0
1688 | VALLEY_2G | 2 | North | YES | 0.003619 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.036112 | 527 | 527 | 1.9072 | 527 |  |  | 0.036112 | 19.031 |  |  |  |  | 0 | 0
2371 | COLLIN_1G | MB | North | YES | 0.003631 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.036124 | 0 | 0 | 0 | 0 |  |  | 0.036124 | 0 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.032489 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.036124 | 0 | 35 |  |  | 0 | 0 | -0.036124 | 0 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.032489 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.036124 | 0 | 30 |  |  | 0 | 0 | -0.036124 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 1 | North | YES | 0.003692 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.036185 | 0 | 0 | 0 | 0 |  |  | 0.036185 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 2 | North | YES | 0.003692 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | 0.036185 | 0 | 0 | 0 | 0 |  |  | 0.036185 | 0 |  |  |  |  | 0 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.004247 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.03674 | 61 | 61 | 0.25907 | 61 |  |  | 0.03674 | 2.2411 |  |  |  |  | 0 | 0
924 | SPENCER_G5 | 1 | North | YES | 0.004247 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.03674 | 66 | 66 | 0.2803 | 66 |  |  | 0.03674 | 2.4248 |  |  |  |  | 0 | 0
1453 | WCPWRCO_1G | 1 | North | YES | 0.004266 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.036759 | 204 | 204 | 0.87026 | 204 |  |  | 0.036759 | 7.4988 |  |  |  |  | 0 | 0
1454 | WCPWRCO_2G | 2 | North | YES | 0.004266 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.036759 | 204 | 204 | 0.87026 | 204 |  |  | 0.036759 | 7.4988 |  |  |  |  | 0 | 0
1455 | WCPWRCO_3G | 3 | North | YES | 0.004266 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.036759 | 242 | 242 | 1.0324 | 242 |  |  | 0.036759 | 8.8957 |  |  |  |  | 0 | 0
11147 | NOTREES_1G | 1 | West | YES | -0.033214 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.036849 | 0 | 149 |  |  | 0 | 0 | -0.036849 | 0 |  |  |  |  | 0 | 0
1861 | EAGLEMNT_1G | MB | North | YES | 0.004873 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0 |  |  |  |  | 0 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.004873 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0 |  |  |  |  | 0 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.004873 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.037366 | 0 | 0 | 0 | 0 |  |  | 0.037366 | 0 |  |  |  |  | 0 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.005397 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.03789 | 0 | 60 | 0.32382 | 60 |  |  | 0.03789 | 2.2734 |  |  |  |  | 0 | 0
1442 | COKFIELD_5 | 1 | North | YES | 0.005683 | 16.5 | 0 | 165 | 0 | 1.029 | Wind | 1 | 0.038176 | 0 | 165 | 0.93769 | 165 |  |  | 0.038176 | 6.299 |  |  |  |  | 0 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.005683 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.038176 | 366 | 366 | 2.08 | 366 |  |  | 0.038176 | 13.9724 |  |  |  |  | 0 | 0
1326 | STANTONW_8 | 1 | West | YES | -0.035681 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.039316 | 0 | 100.5 |  |  | 0 | 0 | -0.039316 | 0 |  |  |  |  | 0 | 0
728 | WOLFRIDGE801 | 1 | North | YES | 0.007076 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.039569 | 0 | 112.5 | 0.79605 | 112.5 |  |  | 0.039569 | 4.4515 |  |  |  |  | 0 | 0
1328 | OCOTILLO_1G | 1 | West | YES | -0.037855 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.04149 | 0 | 58 |  |  | 0 | 0 | -0.04149 | 0 |  |  |  |  | 0 | 0
1349 | WESTXWIN_1G | 1 | West | YES | -0.038494 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.042129 | 0 | 6.6 |  |  | 0 | 0 | -0.042129 | 0 |  |  |  |  | 0 | 0
1350 | NWPWRG1_1G | 1 | West | YES | -0.038494 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.042129 | 0 | 34.3 |  |  | 0 | 0 | -0.042129 | 0 |  |  |  |  | 0 | 0
1333 | MCDDONAL_8 | 1 | West | YES | -0.038529 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.042164 | 0 | 214.2 |  |  | 0 | 0 | -0.042164 | 0 |  |  |  |  | 0 | 0
581 | JCKCNTY802 | 2 | North | YES | 0.00999 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.042483 | 147 | 147 | 1.4685 | 147 |  |  | 0.042483 | 6.245 |  |  |  |  | 0 | 0
582 | JCKCNTY803 | 3 | North | YES | 0.00999 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.042483 | 147 | 147 | 1.4685 | 147 |  |  | 0.042483 | 6.245 |  |  |  |  | 0 | 0
580 | JCKCNTY801 | 1 | North | YES | 0.00999 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.042483 | 288 | 288 | 2.8771 | 288 |  |  | 0.042483 | 12.2351 |  |  |  |  | 0 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.039546 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.043181 | 137 | 137 |  |  | -5.4178 | 137 | -0.043181 | -5.9159 |  |  |  |  | 0 | 0
1040 | MRGNBG_2G | B | West | YES | -0.039546 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.043181 | 71 | 71 |  |  | -2.8078 | 71 | -0.043181 | -3.0659 |  |  |  |  | 0 | 0
1041 | MRGNCG_3G | C | West | YES | -0.039546 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.043181 | 70 | 70 |  |  | -2.7682 | 70 | -0.043181 | -3.0227 |  |  |  |  | 0 | 0
1043 | MRGNEG_5G | E | West | YES | -0.039546 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.043181 | 70 | 70 |  |  | -2.7682 | 70 | -0.043181 | -3.0227 |  |  |  |  | 0 | 0
1039 | MRGNAG_1G | A | West | YES | -0.039546 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.043181 | 69 | 69 |  |  | -2.7287 | 69 | -0.043181 | -2.9795 |  |  |  |  | 0 | 0
1042 | MRGNDG_4G | D | West | YES | -0.039546 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.043181 | 68 | 68 |  |  | -2.6891 | 68 | -0.043181 | -2.9363 |  |  |  |  | 0 | 0
1044 | MRGNFG_6G | F | West | YES | -0.039546 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.043181 | 66 | 66 |  |  | -2.61 | 66 | -0.043181 | -2.85 |  |  |  |  | 0 | 0
1320 | BSP 1 | 1 | West | YES | -0.040237 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.043872 | 0 | 0 |  |  | 0 | 0 | -0.043872 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.01168 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.01168 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.044173 | 0 | 0 | 0 | 0 |  |  | 0.044173 | 0 |  |  |  |  | 0 | 0
332 | RWMILLER01 | 1 | North | YES | 0.012387 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.04488 | 73 | 73 | 0.90425 | 73 |  |  | 0.04488 | 3.2762 |  |  |  |  | 0 | 0
336 | RWMILLER05 | 5 | North | YES | 0.012387 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.04488 | 101 | 101 | 1.2511 | 101 |  |  | 0.04488 | 4.5329 |  |  |  |  | 0 | 0
335 | RWMILLER04 | 4 | North | YES | 0.012387 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.04488 | 102 | 102 | 1.2635 | 102 |  |  | 0.04488 | 4.5778 |  |  |  |  | 0 | 0
333 | RWMILLER02 | 2 | North | YES | 0.012387 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.04488 | 119 | 119 | 1.4741 | 119 |  |  | 0.04488 | 5.3407 |  |  |  |  | 0 | 0
334 | RWMILLER03 | 3 | North | YES | 0.012387 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.04488 | 208 | 208 | 2.5765 | 208 |  |  | 0.04488 | 9.335 |  |  |  |  | 0 | 0
503 | NTHTEXAS01 | 1 | North | YES | 0.012564 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.045057 | 18 | 18 | 0.22615 | 18 |  |  | 0.045057 | 0.81103 |  |  |  |  | 0 | 0
504 | NTHTEXAS02 | 2 | North | YES | 0.012564 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.045057 | 18 | 18 | 0.22615 | 18 |  |  | 0.045057 | 0.81103 |  |  |  |  | 0 | 0
505 | NTHTEXAS03 | 3 | North | YES | 0.012564 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.045057 | 38 | 38 | 0.47743 | 38 |  |  | 0.045057 | 1.7122 |  |  |  |  | 0 | 0
1327 | WILDHRSE_1G | 1 | West | YES | -0.042121 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.045756 | 0 | 120 |  |  | 0 | 0 | -0.045756 | 0 |  |  |  |  | 0 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.043637 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.047272 | 0 | 120 |  |  | 0 | 0 | -0.047272 | 0 |  |  |  |  | 0 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.048542 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.052177 | 0 | 225 |  |  | 0 | 0 | -0.052177 | 0 |  |  |  |  | 0 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.049265 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.0529 | 0 | 180 |  |  | 0 | 0 | -0.0529 | 0 |  |  |  |  | 0 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.049265 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.0529 | 0 | 180 |  |  | 0 | 0 | -0.0529 | 0 |  |  |  |  | 0 | 0
344 | MRSSHPRD | 1 | North | YES | 0.022736 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.055229 | 0 | 0 | 0 | 0 |  |  | 0.055229 | 0 |  |  |  |  | 0 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.022736 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.055229 | 0 | 0 | 0 | 0 |  |  | 0.055229 | 0 |  |  |  |  | 0 | 0
6637 | SNYDERW1A | 1 | West | YES | -0.053701 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.057336 | 0 | 63 |  |  | 0 | 0 | -0.057336 | 0 |  |  |  |  | 0 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.05733 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.060965 | 0 | 141 |  |  | 0 | 0 | -0.060965 | 0 |  |  |  |  | 0 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.05733 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.060965 | 0 | 120 |  |  | 0 | 0 | -0.060965 | 0 |  |  |  |  | 0 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.057618 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.061253 | 0 | 99 |  |  | 0 | 0 | -0.061253 | 0 |  |  |  |  | 0 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.057618 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.061253 | 0 | 61 |  |  | 0 | 0 | -0.061253 | 0 |  |  |  |  | 0 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.057618 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0 |  |  |  |  | 0 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.057618 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0 |  |  |  |  | 0 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.057618 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.061253 | 0 | 0 |  |  | 0 | 0 | -0.061253 | 0 |  |  |  |  | 0 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.065277 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | -1 | 0.068912 | 0 | 114 |  |  | 0 | 0 | -0.068912 | 0 |  |  |  |  | 0 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.066301 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.069936 | 0 | 150 |  |  | 0 | 0 | -0.069936 | 0 |  |  |  |  | 0 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.066301 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.069936 | 0 | 101 |  |  | 0 | 0 | -0.069936 | 0 |  |  |  |  | 0 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.038401 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.070894 | 0 | 120 | 4.6081 | 120 |  |  | 0.070894 | 8.5073 |  |  |  |  | 0 | 0
36998 | RDCNYNG1 | 1 | West | YES | -0.068089 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.071724 | 0 | 84 |  |  | 0 | 0 | -0.071724 | 0 |  |  |  |  | 0 | 0
6407 | TURKTRAK1A | 1 | West | YES | -0.077309 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.080944 | 0 | 169.5 |  |  | 0 | 0 | -0.080944 | 0 |  |  |  |  | 0 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.067419 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.099912 | 242 | 242 | 16.3154 | 242 |  |  | 0.099912 | 24.1787 |  |  |  |  | 0 | 0
6144 | MCADOO1A | 1 | West | YES | -0.11402 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.11765 | 0 | 150 |  |  | 0 | 0 | -0.11765 | 0 |  |  |  |  | 0 | 0
60081 | WHRLWIND1A | 1 | West | YES | -0.13083 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.13446 | 0 | 60 |  |  | 0 | 0 | -0.13446 | 0 |  |  |  |  | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0

## Zones
Houston | 1
North | 1
South | 1
West | -1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | West | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1073 | SCURRYCW_2G | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3126 | TRINIDAD_6G | GST
3309 | ASPN_G | Bio
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5920 | WELSHDC1 | DCTie
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6096 | NORTHDC7 | DCTie
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NBEC7 | GST
8442 | NBEC7 | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11056 | ROSCOE_1G | Wind
11057 | CHAMPION_1G | Wind
11058 | PYRON_1G | Wind
11059 | INADALE_1G | Wind
11065 | ELBOWCK_1G | Wind
11147 | NOTREES_1G | Wind
11309 | BULLCREK_2G | Wind
11310 | BULLCREK_1G | Wind
11320 | COYOTE_1G | Wind
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
48940 | WARVUE_GT1 | Cogen
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
71061 | L_SWEETW1_5N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
76095 | L_CAPRSI1_1N | Wind
76096 | L_CAPRSI1_2N | Wind
76097 | L_CAPRGE1_1N | Wind
80003 | MILHWYS | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80263 | B_DAVIS31A | CC
80264 | B_DAVIS41A | CC
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
86104 | CID-138 | DCTie
86105 | CID-230 | DCTie
86106 | CUF-230 | DCTie
86107 | CUF-138 | DCTie
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR