## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  | Summary of Key Data points | Value
File Description: Cont_ TempleSS to TemplePEC OL_ TempleSS to Sandow
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K27 |  | Number of units | 645
|  |  | Dec PTDF cutoff point | 387
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  | Dec PTDF cutoff unit | TNSLCGN1__8
|  |  | Dec 10% unit | L_FPPYD11_2Y
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  | Dec max cumltv zone impact - cumltv zone share | 0.12249
|  |  | Dec max cumltv zone impact - cumltv zone share pt | 173
Step 5 | Enter Dennis' file name into cell K27 |  | Dec max cumltv zone impact - cumltv zone share unit | RAYBURNGEN2
|  |  | South Zonal weighted AWGSF | 0.10565
Step 6 | click the step one button |  | North Zonal weighted AWGSF | -0.073157
|  |  | Inc PTDF cutoff point | 258
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  | Inc PTDF cutoff unit | BRYN_DNSBY14
| X6:X30, or to the end of the selected list. |  | Inc 10% unit | MDLTHELP_5G
|  |  | Inc max cumltv zone impact - cumltv zone share | 0.02591
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  | Inc max cumltv zone impact - cumltv zone share pt | 54
| of the formulas in columns L:V (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  | Inc max cumltv zone impact - cumltv zone share unit | SPENCER_G5
| If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct leng |  | South Zonal weighted AWGSF | 0.10565
| It is only necessary to match the Distributed Slack - Dec worksheet. |  | North Zonal weighted AWGSF | -0.073157
|  |  | Min of zone correlation | 0.073157
Step 9 | Click the step 2 button |  | Bounary gen in North Zone | 0
| The last file saved will still be open, yopu will need to close this file. |  | Bounary gen in soucre zone as % of line | 0%
| This sheet willno longer be open. |  | Bounary gen in South Zone | 0
|  |  | Bounary gen in soucre zone as % of line | 0
|  |  | OL element line rating | 1072
|  |  | South Zonal weighted AWGSF | 0.10565
|  | SN_043009automation.xls | North Zonal weighted AWGSF | -0.073157
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ TempleSS to TemplePEC OL_ TempleSS to Sandow |  | i_PTDF_DEC_pt | 387 |  | RAYBURNGEN2 | Unit at max
13432 | SANDOW_5G | 5 | South | YES | 0.1798 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.25295 | 0 | 581 | 104.4609 | 581 |  |  | 0.25295 | 146.9654 | 0.019641 | 0.033209 |  |  | i_10pctunit | 10 |  | 173 | # units @ max
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.13594 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.20909 | 158 | 158 | 21.4779 | 158 |  |  | 0.20909 | 33.0368 | 0.024983 | 0.040675 |  |  | # units | 645 |  | 0.12249 | delta max
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.13594 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.20909 | 160 | 160 | 21.7498 | 160 |  |  | 0.20909 | 33.4549 | 0.030392 | 0.048234 | [5 empty] | Delta
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.13594 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.20909 | 175 | 175 | 23.7888 | 175 |  |  | 0.20909 | 36.5914 | 0.036308 | 0.056503 | Weighted Shift Factors |  |  |  | 1 | 0.013568
3432 | SANDOW_4G | 4 | South | YES | 0.1349 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.20806 | 0 | 580 | 78.2426 | 580 |  |  | 0.20806 | 120.6739 | 0.055915 | 0.083771 | South | 0.10565 |  |  | 2 | 0.015692
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.13412 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.20728 | 152.5 | 152.5 | 20.4531 | 152.5 |  |  | 0.20728 | 31.6097 | 0.061071 | 0.090914 | North | -0.073157 |  |  | 3 | 0.017843
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.13412 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.20728 | 149.5 | 149.5 | 20.0508 | 149.5 |  |  | 0.20728 | 30.9878 | 0.066125 | 0.097916 |  |  |  |  | 4 | 0.020195
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.13412 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.20728 | 232.6 | 232.6 | 31.1961 | 232.6 |  |  | 0.20728 | 48.2125 | 0.073988 | 0.10881 |  |  |  |  | 5 | 0.027856
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.11871 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.19187 | 0 | 606 | 71.9377 | 606 |  |  | 0.19187 | 116.2711 | 0.094474 | 0.13508 |  |  |  |  | 6 | 0.029843
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.11871 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.19187 | 0 | 598 | 70.988 | 598 |  |  | 0.19187 | 114.7361 | 0.11469 | 0.16101 |  |  |  |  | 7 | 0.031792
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.11858 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.19174 | 0 | 436 | 51.7 | 436 |  |  | 0.19174 | 83.5966 | 0.12943 | 0.1799 |  |  |  |  | 8 | 0.034823
9002 | DECKR_G3 | 3 | South | YES | 0.11697 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.19013 | 42 | 42 | 4.9129 | 42 |  |  | 0.19013 | 7.9855 | 0.13085 | 0.18171 |  |  |  |  | 9 | 0.04061
9003 | DECKR_G4 | 4 | South | YES | 0.11697 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.19013 | 44 | 44 | 5.1469 | 44 |  |  | 0.19013 | 8.3658 | 0.13234 | 0.1836 |  |  |  |  | 10 | 0.046321
9004 | DECKR_G5 | 5 | South | YES | 0.11697 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.19013 | 44 | 44 | 5.1469 | 44 |  |  | 0.19013 | 8.3658 | 0.13382 | 0.18549 |  |  |  |  | 11 | 0.050471
9005 | DECKR_G6 | 6 | South | YES | 0.11697 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.19013 | 47 | 47 | 5.4978 | 47 |  |  | 0.19013 | 8.9362 | 0.13541 | 0.18751 |  |  |  |  | 12 | 0.050856
9016 | SANDH_G1 | 1 | South | YES | 0.11611 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.18927 | 49 | 49 | 5.6894 | 49 |  |  | 0.18927 | 9.2741 | 0.13707 | 0.1896 |  |  |  |  | 13 | 0.051259
9017 | SANDH_G2 | 2 | South | YES | 0.11611 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.18927 | 46 | 46 | 5.3411 | 46 |  |  | 0.18927 | 8.7063 | 0.13863 | 0.19157 |  |  |  |  | 14 | 0.051662
9018 | SANDH_G3 | 3 | South | YES | 0.11611 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.18927 | 46 | 46 | 5.3411 | 46 |  |  | 0.18927 | 8.7063 | 0.14018 | 0.19354 |  |  |  |  | 15 | 0.052092
9019 | SANDH_G4 | 4 | South | YES | 0.11611 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.18927 | 47 | 47 | 5.4572 | 47 |  |  | 0.18927 | 8.8956 | 0.14177 | 0.19555 |  |  |  |  | 16 | 0.052531
9020 | SANDHG5A | 5A | South | YES | 0.11611 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.18927 | 155 | 155 | 17.9971 | 155 |  |  | 0.18927 | 29.3365 | 0.14701 | 0.20218 |  |  |  |  | 17 | 0.052944
9021 | SANDHG5C | 5C | South | YES | 0.11611 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.18927 | 148 | 148 | 17.1843 | 148 |  |  | 0.18927 | 28.0116 | 0.15201 | 0.20851 |  |  |  |  | 18 | 0.053356
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.11605 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.1892 | 132 | 132 | 15.3182 | 132 |  |  | 0.1892 | 24.975 | 0.15647 | 0.21415 |  |  |  |  | 19 | 0.053777
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.11605 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.1892 | 139 | 139 | 16.1305 | 139 |  |  | 0.1892 | 26.2994 | 0.16117 | 0.22009 |  |  |  |  | 20 | 0.055166
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.11605 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.1892 | 329 | 329 | 38.1795 | 329 |  |  | 0.1892 | 62.2483 | 0.1723 | 0.23416 |  |  |  |  | 21 | 0.056493
9000 | DECKR_G1 | 1 | South | YES | 0.11502 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.18818 | 321 | 321 | 36.9217 | 321 |  |  | 0.18818 | 60.4053 | 0.18315 | 0.24781 |  |  |  |  | 22 | 0.057674
9001 | DECKR_G2 | 2 | South | YES | 0.11502 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.18818 | 426 | 426 | 48.9989 | 426 |  |  | 0.18818 | 80.164 | 0.19755 | 0.26592 |  |  |  |  | 23 | 0.058918
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.11267 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.18583 | 223.9 | 223.9 | 25.2277 | 223.9 |  |  | 0.18583 | 41.6077 | 0.20512 | 0.27532 |  |  |  |  | 24 | 0.061862
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.11267 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.18583 | 225 | 225 | 25.3516 | 225 |  |  | 0.18583 | 41.8121 | 0.21272 | 0.28477 |  |  |  |  | 25 | 0.064659
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.11267 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.18583 | 224.6 | 224.6 | 25.3066 | 224.6 |  |  | 0.18583 | 41.7377 | 0.22032 | 0.2942 |  |  |  |  | 26 | 0.068373
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.11267 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.18583 | 226.7 | 226.7 | 25.5432 | 226.7 |  |  | 0.18583 | 42.128 | 0.22798 | 0.30372 |  |  |  |  | 27 | 0.070205
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.11201 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.18517 | 0 | 0 | 0 | 0 |  |  | 0.18517 | 0 | 0.22798 | 0.30372 |  |  |  |  | 28 | 0.072047
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.11201 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.18517 | 0 | 0 | 0 | 0 |  |  | 0.18517 | 0 | 0.22798 | 0.30372 |  |  |  |  | 29 | 0.073886
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381 | 0.22967 | 0.30581 |  |  |  |  | 30 | 0.075742
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381 | 0.23136 | 0.3079 |  |  |  |  | 31 | 0.075742
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381 | 0.23305 | 0.30999 |  |  |  |  | 32 | 0.075742
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381 | 0.23474 | 0.31207 |  |  |  |  | 33 | 0.076139
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.10859 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.18174 | 0 | 0 | 0 | 0 |  |  | 0.18174 | 0 | 0.23474 | 0.31207 |  |  |  |  | 34 | 0.076536
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.10842 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.18158 | 148 | 148 | 16.0459 | 148 |  |  | 0.18158 | 26.8732 | 0.23975 | 0.31815 |  |  |  |  | 35 | 0.076933
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.10842 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.18158 | 148 | 148 | 16.0459 | 148 |  |  | 0.18158 | 26.8732 | 0.24475 | 0.32422 |  |  |  |  | 36 | 0.07733
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.10842 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.18158 | 154 | 154 | 16.6964 | 154 |  |  | 0.18158 | 27.9626 | 0.24996 | 0.33054 |  |  |  |  | 37 | 0.07733
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.10842 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.18158 | 293 | 293 | 31.7665 | 293 |  |  | 0.18158 | 53.2016 | 0.25986 | 0.34256 |  |  |  |  | 38 | 0.0784
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.10619 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0 | 0.25986 | 0.34256 |  |  |  |  | 39 | 0.079469
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.10619 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0 | 0.25986 | 0.34256 |  |  |  |  | 40 | 0.080581
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.10619 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0 | 0.25986 | 0.34256 |  |  |  |  | 41 | 0.082698
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.10567 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.17882 | 0 | 0 | 0 | 0 |  |  | 0.17882 | 0 | 0.25986 | 0.34256 |  |  |  |  | 42 | 0.082698
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.10451 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.17767 | 147 | 147 | 15.363 | 147 |  |  | 0.17767 | 26.1171 | 0.26483 | 0.34846 |  |  |  |  | 43 | 0.082698
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.10451 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.17767 | 138 | 138 | 14.4224 | 138 |  |  | 0.17767 | 24.5181 | 0.2695 | 0.354 |  |  |  |  | 44 | 0.082698
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.10451 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.17767 | 146 | 146 | 15.2585 | 146 |  |  | 0.17767 | 25.9394 | 0.27443 | 0.35986 |  |  |  |  | 45 | 0.082698
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.10451 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.17767 | 149 | 149 | 15.572 | 149 |  |  | 0.17767 | 26.4724 | 0.27947 | 0.36584 |  |  |  |  | 46 | 0.08363
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.10451 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.17767 | 182 | 182 | 19.0208 | 182 |  |  | 0.17767 | 32.3355 | 0.28562 | 0.37315 |  |  |  |  | 47 | 0.084505
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.10451 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.17767 | 203 | 203 | 21.2155 | 203 |  |  | 0.17767 | 36.0665 | 0.29248 | 0.3813 |  |  |  |  | 48 | 0.085431
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.10343 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.17659 | 0 | 0 | 0 | 0 |  |  | 0.17659 | 0 | 0.29248 | 0.3813 |  |  |  |  | 49 | 0.086376
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.10343 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.17659 | 0 | 0 | 0 | 0 |  |  | 0.17659 | 0 | 0.29248 | 0.3813 |  |  |  |  | 50 | 0.08753
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.10143 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.17459 | 61 | 61 | 6.1874 | 61 |  |  | 0.17459 | 10.65 | 0.29455 | 0.38371 |  |  |  |  | 51 | 0.088817
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.10143 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.17459 | 95 | 95 | 9.636 | 95 |  |  | 0.17459 | 16.586 | 0.29776 | 0.38745 |  |  |  |  | 52 | 0.088817
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.10143 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.17459 | 151 | 151 | 15.3162 | 151 |  |  | 0.17459 | 26.363 | 0.30286 | 0.39341 |  |  |  |  | 53 | 0.088817
5111 | CALAVER_JTD1 | 1 | South | YES | 0.10099 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.17415 | 0 | 430 | 43.4253 | 430 |  |  | 0.17415 | 74.883 | 0.3174 | 0.41033 |  |  |  |  | 54 | 0.089161
5112 | CALAVER_JTD2 | 2 | South | YES | 0.10099 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.17415 | 0 | 430 | 43.4253 | 430 |  |  | 0.17415 | 74.883 | 0.33193 | 0.42725 |  |  |  |  | 55 | 0.089698
5396 | CALAVER_OWS1 | 1 | South | YES | 0.10085 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.174 | 418 | 418 | 42.154 | 418 |  |  | 0.174 | 72.7339 | 0.34607 | 0.44369 |  |  |  |  | 56 | 0.09055
5397 | CALAVER_OWS2 | 2 | South | YES | 0.10085 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.174 | 400 | 400 | 40.3388 | 400 |  |  | 0.174 | 69.6018 | 0.35959 | 0.45942 |  |  |  |  | 57 | 0.092935
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.10072 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.17388 | 215 | 215 | 21.6546 | 215 |  |  | 0.17388 | 37.3834 | 0.36686 | 0.46786 |  |  |  |  | 58 | 0.095319
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.10072 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.17388 | 216 | 216 | 21.7553 | 216 |  |  | 0.17388 | 37.5573 | 0.37416 | 0.47635 |  |  |  |  | 59 | 0.097624
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.10067 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.17383 | 407 | 407 | 40.9743 | 407 |  |  | 0.17383 | 70.7494 | 0.38792 | 0.49234 |  |  |  |  | 60 | 0.099829
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.10033 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.17348 | 155 | 155 | 15.5507 | 155 |  |  | 0.17348 | 26.8901 | 0.39316 | 0.49842 |  |  |  |  | 61 | 0.10101
5477 | BRA_AVR1_ST | 1 | South | YES | 0.10033 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.17348 | 174 | 174 | 17.4569 | 174 |  |  | 0.17348 | 30.1863 | 0.39904 | 0.50524 |  |  |  |  | 62 | 0.10219
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.10033 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.17348 | 155 | 155 | 15.5507 | 155 |  |  | 0.17348 | 26.8901 | 0.40428 | 0.51131 |  |  |  |  | 63 | 0.10442
5264 | LEON_LCP3G3 | 3 | South | YES | 0.099997 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.17315 | 58 | 58 | 5.7998 | 58 |  |  | 0.17315 | 10.043 | 0.40624 | 0.51358 |  |  |  |  | 64 | 0.10526
5265 | LEON_LCP4G4 | 4 | South | YES | 0.099997 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.17315 | 89 | 89 | 8.8997 | 89 |  |  | 0.17315 | 15.4107 | 0.40925 | 0.51706 |  |  |  |  | 65 | 0.1062
5266 | LEON_LCPCT1 | 1 | South | YES | 0.099997 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.17315 | 44 | 44 | 4.3999 | 44 |  |  | 0.17315 | 7.6188 | 0.41074 | 0.51879 |  |  |  |  | 66 | 0.10703
5267 | LEON_LCPCT2 | 2 | South | YES | 0.099997 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.17315 | 44 | 44 | 4.3999 | 44 |  |  | 0.17315 | 7.6188 | 0.41222 | 0.52051 |  |  |  |  | 67 | 0.10734
5268 | LEON_LCPCT3 | 3 | South | YES | 0.099997 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.17315 | 43 | 43 | 4.2999 | 43 |  |  | 0.17315 | 7.4456 | 0.41368 | 0.52219 |  |  |  |  | 68 | 0.10781
5269 | LEON_LCPCT4 | 4 | South | YES | 0.099997 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.17315 | 45 | 45 | 4.4999 | 45 |  |  | 0.17315 | 7.7919 | 0.4152 | 0.52395 |  |  |  |  | 69 | 0.10805
5401 | CALAVER_JKS1 | 1 | South | YES | 0.099885 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.17304 | 0 | 562 | 56.1354 | 562 |  |  | 0.17304 | 97.2498 | 0.4342 | 0.54593 |  |  |  |  | 70 | 0.10828
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.099303 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0 | 0.4342 | 0.54593 |  |  |  |  | 71 | 0.10851
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.099303 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0 | 0.4342 | 0.54593 |  |  |  |  | 72 | 0.10875
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.099303 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0 | 0.4342 | 0.54593 |  |  |  |  | 73 | 0.11173
8189 | CUECPL2A | 1 | South | YES | 0.097885 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.17104 | 0 | 0 | 0 | 0 |  |  | 0.17104 | 0 | 0.4342 | 0.54593 |  |  |  |  | 74 | 0.11173
5903 | SANMIGUELGEN | 1 | South | YES | 0.095866 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.16902 | 0 | 396.3 | 37.9917 | 396.3 |  |  | 0.16902 | 66.984 | 0.4476 | 0.56106 |  |  |  |  | 75 | 0.11173
5890 | PEARSALLGEN1 | 1 | South | YES | 0.089443 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.1626 | 24 | 24 | 2.1466 | 24 |  |  | 0.1626 | 3.9024 | 0.44841 | 0.56194 |  |  |  |  | 76 | 0.11173
5891 | PEARSALLGEN2 | 1 | South | YES | 0.089443 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.1626 | 24.3 | 24.3 | 2.1735 | 24.3 |  |  | 0.1626 | 3.9512 | 0.44923 | 0.56284 |  |  |  |  | 77 | 0.11173
5892 | PEARSALLGEN3 | 1 | South | YES | 0.089443 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.1626 | 23.9 | 23.9 | 2.1377 | 23.9 |  |  | 0.1626 | 3.8862 | 0.45004 | 0.56372 |  |  |  |  | 78 | 0.11347
88198 | BEEVILLE | F | South | YES | 0.088248 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.16141 | 0 | 0 | 0 | 0 |  |  | 0.16141 | 0 | 0.45004 | 0.56372 |  |  |  |  | 79 | 0.11354
58909 | PEARSALLSCG1 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45032 | 0.56402 |  |  |  |  | 80 | 0.11361
58909 | PEARSALLSCG1 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.4506 | 0.56433 |  |  |  |  | 81 | 0.11368
58909 | PEARSALLSCG1 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45089 | 0.56463 |  |  |  |  | 82 | 0.11368
58909 | PEARSALLSCG1 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45117 | 0.56494 |  |  |  |  | 83 | 0.1137
58909 | PEARSALLSCG1 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45146 | 0.56524 |  |  |  |  | 84 | 0.11372
58909 | PEARSALLSCG1 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45174 | 0.56555 |  |  |  |  | 85 | 0.11374
58919 | PEARSALLSCG2 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45202 | 0.56585 |  |  |  |  | 86 | 0.11376
58919 | PEARSALLSCG2 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45231 | 0.56616 |  |  |  |  | 87 | 0.11379
58919 | PEARSALLSCG2 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45259 | 0.56646 |  |  |  |  | 88 | 0.11381
58919 | PEARSALLSCG2 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45288 | 0.56677 |  |  |  |  | 89 | 0.11383
58919 | PEARSALLSCG2 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45316 | 0.56707 |  |  |  |  | 90 | 0.11385
58919 | PEARSALLSCG2 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45344 | 0.56738 |  |  |  |  | 91 | 0.11387
58929 | PEARSALLSCG3 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45373 | 0.56768 |  |  |  |  | 92 | 0.11389
58929 | PEARSALLSCG3 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45401 | 0.56799 |  |  |  |  | 93 | 0.11391
58929 | PEARSALLSCG3 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.4543 | 0.5683 |  |  |  |  | 94 | 0.11394
58929 | PEARSALLSCG3 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45458 | 0.5686 |  |  |  |  | 95 | 0.11396
58929 | PEARSALLSCG3 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45486 | 0.56891 |  |  |  |  | 96 | 0.11398
58929 | PEARSALLSCG3 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45515 | 0.56921 |  |  |  |  | 97 | 0.114
58949 | PEARSALLSCG4 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45543 | 0.56952 |  |  |  |  | 98 | 0.11402
58949 | PEARSALLSCG4 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45572 | 0.56982 |  |  |  |  | 99 | 0.11404
58949 | PEARSALLSCG4 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.456 | 0.57013 |  |  |  |  | 100 | 0.11406
58949 | PEARSALLSCG4 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45628 | 0.57043 |  |  |  |  | 101 | 0.11409
58949 | PEARSALLSCG4 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45657 | 0.57074 |  |  |  |  | 102 | 0.11411
58949 | PEARSALLSCG4 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 | 0.45685 | 0.57104 |  |  |  |  | 103 | 0.11413
8161 | COLETO0A | 1 | South | YES | 0.0875 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.16066 | 0 | 633 | 55.3875 | 633 |  |  | 0.16066 | 101.6962 | 0.47825 | 0.59402 |  |  |  |  | 104 | 0.11415
80080 | GWINDT11A | 3 | South | YES | 0.084498 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 38 | 3.2109 | 38 |  |  | 0.15766 | 5.9909 | 0.47954 | 0.59538 |  |  |  |  | 105 | 0.11417
80080 | GWINDT11A | 4 | South | YES | 0.084498 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 19 | 1.6055 | 19 |  |  | 0.15766 | 2.9955 | 0.48018 | 0.59605 |  |  |  |  | 106 | 0.11419
80080 | GWINDT11A | 2 | South | YES | 0.084498 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 41 | 3.4644 | 41 |  |  | 0.15766 | 6.4639 | 0.48156 | 0.59752 |  |  |  |  | 107 | 0.11577
80080 | GWINDT11A | 1 | South | YES | 0.084498 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 94 | 7.9428 | 94 |  |  | 0.15766 | 14.8196 | 0.48474 | 0.60086 |  |  |  |  | 108 | 0.11584
80081 | GWINDT21A | 4 | South | YES | 0.084498 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 22 | 1.859 | 22 |  |  | 0.15766 | 3.4684 | 0.48549 | 0.60165 |  |  |  |  | 109 | 0.11588
80081 | GWINDT21A | 1 | South | YES | 0.084498 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 94 | 7.9428 | 94 |  |  | 0.15766 | 14.8196 | 0.48866 | 0.605 |  |  |  |  | 110 | 0.11595
80081 | GWINDT21A | 3 | South | YES | 0.084498 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 43 | 3.6334 | 43 |  |  | 0.15766 | 6.7792 | 0.49012 | 0.60653 |  |  |  |  | 111 | 0.11612
80081 | GWINDT21A | 2 | South | YES | 0.084498 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 36 | 3.0419 | 36 |  |  | 0.15766 | 5.6756 | 0.49133 | 0.60781 |  |  |  |  | 112 | 0.11616
80180 | PNSCALT11A | 2 | South | YES | 0.084498 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 50 | 4.2249 | 50 |  |  | 0.15766 | 7.8828 | 0.49302 | 0.60959 |  |  |  |  | 113 | 0.11633
80180 | PNSCALT11A | 1 | South | YES | 0.084498 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 148 | 12.5057 | 148 |  |  | 0.15766 | 23.333 | 0.49803 | 0.61486 |  |  |  |  | 114 | 0.11641
80181 | PNSCALT21A | 2 | South | YES | 0.084498 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 50 | 4.2249 | 50 |  |  | 0.15766 | 7.8828 | 0.49972 | 0.61665 |  |  |  |  | 115 | 0.11648
80181 | PNSCALT21A | 1 | South | YES | 0.084498 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 55 | 4.6474 | 55 |  |  | 0.15766 | 8.671 | 0.50158 | 0.61861 |  |  |  |  | 116 | 0.11657
5932 | SI_RAY9 | 9 | South | YES | 0.084476 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.15763 | 38 | 38 | 3.2101 | 38 |  |  | 0.15763 | 5.9901 | 0.50286 | 0.61996 |  |  |  |  | 117 | 0.11684
5933 | SI_RAY6 | 6 | South | YES | 0.084476 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.15763 | 19.3 | 19.3 | 1.6304 | 19.3 |  |  | 0.15763 | 3.0423 | 0.50351 | 0.62065 |  |  |  |  | 118 | 0.11693
5935 | SI_RAY10 | 10 | South | YES | 0.084476 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.15763 | 47 | 47 | 3.9704 | 47 |  |  | 0.15763 | 7.4088 | 0.5051 | 0.62232 |  |  |  |  | 119 | 0.11703
80003 | MILHWYS | F | South | YES | 0.084476 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.15763 | 0 | 0 | 0 | 0 |  |  | 0.15763 | 0 | 0.5051 | 0.62232 |  |  |  |  | 120 | 0.1171
8936 | MVGN#1 | 1 | South | YES | 0.084446 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.1576 | 216.6 | 216.6 | 18.291 | 216.6 |  |  | 0.1576 | 34.1369 | 0.51243 | 0.63003 |  |  |  |  | 121 | 0.11713
8937 | MVGN#2 | 2 | South | YES | 0.084446 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.1576 | 216.7 | 216.7 | 18.2994 | 216.7 |  |  | 0.1576 | 34.1527 | 0.51975 | 0.63775 |  |  |  |  | 122 | 0.11722
8938 | MVGN#3 | 3 | South | YES | 0.084446 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.1576 | 250.9 | 250.9 | 21.1875 | 250.9 |  |  | 0.1576 | 39.5427 | 0.52823 | 0.64669 |  |  |  |  | 123 | 0.11722
8981 | HECN1 | 1 | South | YES | 0.084446 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.1576 | 144.8 | 144.8 | 12.2278 | 144.8 |  |  | 0.1576 | 22.821 | 0.53313 | 0.65184 |  |  |  |  | 124 | 0.11761
8982 | HECN2 | 2 | South | YES | 0.084446 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.1576 | 144.1 | 144.1 | 12.1687 | 144.1 |  |  | 0.1576 | 22.7107 | 0.538 | 0.65698 |  |  |  |  | 125 | 0.118
8983 | HECN3 | 3 | South | YES | 0.084446 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.1576 | 171.9 | 171.9 | 14.5163 | 171.9 |  |  | 0.1576 | 27.092 | 0.54381 | 0.6631 |  |  |  |  | 126 | 0.11845
8517 | CELANEBI0A | 1 | South | YES | 0.084407 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.15756 | 0 | 0 | 0 | 0 |  |  | 0.15756 | 0 | 0.54381 | 0.6631 |  |  |  |  | 127 | 0.11872
8933 | FGNTS001 | 1 | South | YES | 0.084356 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.15751 | 146.5 | 146.5 | 12.3582 | 146.5 |  |  | 0.15751 | 23.0757 | 0.54876 | 0.66831 |  |  |  |  | 128 | 0.11898
8934 | FGNTS101 | 2 | South | YES | 0.084356 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.15751 | 147.9 | 147.9 | 12.4763 | 147.9 |  |  | 0.15751 | 23.2962 | 0.55376 | 0.67358 |  |  |  |  | 129 | 0.11929
8935 | FGNTS201 | 3 | South | YES | 0.084356 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.15751 | 173 | 173 | 14.5936 | 173 |  |  | 0.15751 | 27.2498 | 0.55961 | 0.67973 |  |  |  |  | 130 | 0.11929
8511 | OXY_CC0A | 1 | South | YES | 0.084121 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.15728 | 0 | 0 | 0 | 0 |  |  | 0.15728 | 0 | 0.55961 | 0.67973 |  |  |  |  | 131 | 0.11955
8461 | KOCH_UP0A | 1 | South | YES | 0.084115 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.15727 | 0 | 0 | 0 | 0 |  |  | 0.15727 | 0 | 0.55961 | 0.67973 |  |  |  |  | 132 | 0.11981
8506 | VAL #1 | 1 | South | YES | 0.084042 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.1572 | 0 | 0 | 0 | 0 |  |  | 0.1572 | 0 | 0.55961 | 0.67973 |  |  |  |  | 133 | 0.12012
8507 | VAL #2 | 2 | South | YES | 0.084042 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.1572 | 0 | 0 | 0 | 0 |  |  | 0.1572 | 0 | 0.55961 | 0.67973 |  |  |  |  | 134 | 0.12012
8459 | B_DAVIS0B | MB | South | YES | 0.084009 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.15717 | 0 | 0 | 0 | 0 |  |  | 0.15717 | 0 | 0.55961 | 0.67973 |  |  |  |  | 135 | 0.12012
8460 | B_DAVIS0A | MB | South | YES | 0.084009 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.15717 | 0 | 0 | 0 | 0 |  |  | 0.15717 | 0 | 0.55961 | 0.67973 |  |  |  |  | 136 | 0.12012
80263 | B_DAVIS31A | 3 | South | YES | 0.084009 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.15717 | 180 | 180 | 15.1216 | 180 |  |  | 0.15717 | 28.29 | 0.5657 | 0.68613 |  |  |  |  | 137 | 0.12012
80264 | B_DAVIS41A | 4 | South | YES | 0.084009 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.15717 | 180 | 180 | 15.1216 | 180 |  |  | 0.15717 | 28.29 | 0.57178 | 0.69252 |  |  |  |  | 138 | 0.12012
8456 | COSW#1 | 1 | South | YES | 0.083909 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.15707 | 0 | 0 | 0 | 0 |  |  | 0.15707 | 0 | 0.57178 | 0.69252 |  |  |  |  | 139 | 0.12012
8457 | COSW#2 | 2 | South | YES | 0.083909 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.15707 | 0 | 0 | 0 | 0 |  |  | 0.15707 | 0 | 0.57178 | 0.69252 |  |  |  |  | 140 | 0.12043
8560 | CNOPGT1 | 1 | South | YES | 0.083868 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0 | 0.57178 | 0.69252 |  |  |  |  | 141 | 0.12074
8561 | CNOPGT2 | 2 | South | YES | 0.083868 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0 | 0.57178 | 0.69252 |  |  |  |  | 142 | 0.12074
8562 | CNOPST1 | 3 | South | YES | 0.083868 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0 | 0.57178 | 0.69252 |  |  |  |  | 143 | 0.12074
8442 | NBEC7 | 7 | South | YES | 0.08386 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.15702 | 367 | 367 | 30.7766 | 367 |  |  | 0.15702 | 57.6254 | 0.58419 | 0.70554 |  |  |  |  | 144 | 0.12074
8442 | NBEC7 | MB | South | YES | 0.08386 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.15702 | 0 | 0 | 0 | 0 |  |  | 0.15702 | 0 | 0.58419 | 0.70554 |  |  |  |  | 145 | 0.12074
88508 | FALFURRI | F | South | YES | 0.083826 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0 | 0.58419 | 0.70554 |  |  |  |  | 146 | 0.12074
5728 | FALCONHYDRO2 | 2 | South | YES | 0.083825 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0 | 0.58419 | 0.70554 |  |  |  |  | 147 | 0.12135
5729 | FALCONHYDRO3 | 3 | South | YES | 0.083825 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0 | 0.58419 | 0.70554 |  |  |  |  | 148 | 0.12135
8048 | FALCONHYDRO1 | 1 | South | YES | 0.083825 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0 | 0.58419 | 0.70554 |  |  |  |  | 149 | 0.12135
8173 | VICEC51A | 5 | South | YES | 0.083722 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.15688 | 144 | 144 | 12.056 | 144 |  |  | 0.15688 | 22.5906 | 0.58906 | 0.71065 |  |  |  |  | 150 | 0.12135
8174 | VICEC61A | 6 | South | YES | 0.083722 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.15688 | 188 | 188 | 15.7397 | 188 |  |  | 0.15688 | 29.4933 | 0.59541 | 0.71731 |  |  |  |  | 151 | 0.12135
88299 | ZAPATA | F | South | YES | 0.083317 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.15647 | 0 | 0 | 0 | 0 |  |  | 0.15647 | 0 | 0.59541 | 0.71731 |  |  |  |  | 152 | 0.12135
8926 | LGE_GT10A | 1 | South | YES | 0.083143 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 | 0.59541 | 0.71731 |  |  |  |  | 153 | 0.12159
8927 | LGE_GT20A | 2 | South | YES | 0.083143 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 | 0.59541 | 0.71731 |  |  |  |  | 154 | 0.1219
8928 | LGE_STG0A | 3 | South | YES | 0.083143 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 | 0.59541 | 0.71731 |  |  |  |  | 155 | 0.1219
8930 | ICPGN10A | 1 | South | YES | 0.083143 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 | 0.59541 | 0.71731 |  |  |  |  | 156 | 0.1219
8931 | ICPGN20A | 2 | South | YES | 0.083143 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 | 0.59541 | 0.71731 |  |  |  |  | 157 | 0.1219
8932 | ICPGN30A | 3 | South | YES | 0.083143 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 | 0.59541 | 0.71731 |  |  |  |  | 158 | 0.1219
80223 | REYSHR G | 1 | South | YES | 0.083143 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 | 0.59541 | 0.71731 |  |  |  |  | 159 | 0.1219
8066 | DUP1V#1 | 1 | South | YES | 0.082883 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.15604 | 0 | 0 | 0 | 0 |  |  | 0.15604 | 0 | 0.59541 | 0.71731 |  |  |  |  | 160 | 0.1219
5508 | RAYBURNCC9 | 1 | South | YES | 0.082849 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.15601 | 47.7 | 47.7 | 3.9519 | 47.7 |  |  | 0.15601 | 7.4415 | 0.59703 | 0.71899 |  |  |  |  | 161 | 0.1219
5509 | RAYBURNCC10 | 1 | South | YES | 0.082849 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.15601 | 37.3 | 37.3 | 3.0903 | 37.3 |  |  | 0.15601 | 5.819 | 0.59829 | 0.72031 |  |  |  |  | 162 | 0.1219
5511 | RAYBURNCC7 | 1 | South | YES | 0.082849 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.15601 | 47.5 | 47.5 | 3.9353 | 47.5 |  |  | 0.15601 | 7.4103 | 0.59989 | 0.72198 |  |  |  |  | 163 | 0.1219
5512 | RAYBURNCC8 | 1 | South | YES | 0.082849 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.15601 | 49.3 | 49.3 | 4.0845 | 49.3 |  |  | 0.15601 | 7.6911 | 0.60156 | 0.72372 |  |  |  |  | 164 | 0.12197
80012 | LAR | F | South | YES | 0.082566 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.15572 | 0 | 0 | 0 | 0 |  |  | 0.15572 | 0 | 0.60156 | 0.72372 |  |  |  |  | 165 | 0.12202
80265 | LARECU40A | 4 | South | YES | 0.082565 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.15572 | 100 | 100 | 8.2565 | 100 |  |  | 0.15572 | 15.5722 | 0.60494 | 0.72724 |  |  |  |  | 166 | 0.12209
80266 | LARECU50A | 5 | South | YES | 0.082565 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.15572 | 100 | 100 | 8.2565 | 100 |  |  | 0.15572 | 15.5722 | 0.60832 | 0.73076 |  |  |  |  | 167 | 0.12216
5503 | RAYBURNGEN3 | 1 | South | YES | 0.082165 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.15532 | 22 | 22 | 1.8076 | 22 |  |  | 0.15532 | 3.4171 | 0.60906 | 0.73153 |  |  |  |  | 168 | 0.12216
5505 | RAYBURNGEN1 | 1 | South | YES | 0.082165 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.15532 | 11 | 11 | 0.90382 | 11 |  |  | 0.15532 | 1.7085 | 0.60944 | 0.73191 |  |  |  |  | 169 | 0.1223
5506 | RAYBURNGEN2 | 1 | South | YES | 0.082165 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.15532 | 11 | 11 | 0.90382 | 11 |  |  | 0.15532 | 1.7085 | 0.60981 | 0.7323 |  |  |  |  | 170 | 0.12244
7028 | L_MARBFA1_1Y | 1 | South | YES | 0.081623 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.15478 | 0 | 0 | 0 | 0 |  |  | 0.15478 | 0 | 0.60981 | 0.7323 |  |  |  |  | 171 | 0.12247
7029 | L_MARBFA1_2Y | 2 | South | YES | 0.081623 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.15478 | 0 | 0 | 0 | 0 |  |  | 0.15478 | 0 | 0.60981 | 0.7323 |  |  |  |  | 172 | 0.12248
80224 | VISTRONG1 | 1 | South | YES | 0.081411 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.15457 | 0 | 0 | 0 | 0 |  |  | 0.15457 | 0 | 0.60981 | 0.7323 |  |  |  |  | 173 | 0.12249
80225 | VISTRONG2 | 2 | South | YES | 0.081411 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.15457 | 0 | 0 | 0 | 0 |  |  | 0.15457 | 0 | 0.60981 | 0.7323 |  |  |  |  | 174 | 0.12249
80227 | AIRCO G | 1 | South | YES | 0.080868 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.15403 | 0 | 0 | 0 | 0 |  |  | 0.15403 | 0 | 0.60981 | 0.7323 |  |  |  |  | 175 | 0.12249
80140 | CSDR11 | 11 | South | YES | 0.080584 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 | 0.60981 | 0.7323 |  |  |  |  | 176 | 0.12249
8147 | UCAR #2 | 10 | South | YES | 0.080583 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 | 0.60981 | 0.7323 |  |  |  |  | 177 | 0.12249
8148 | UCAR #1 | 2 | South | YES | 0.080583 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 | 0.60981 | 0.7323 |  |  |  |  | 178 | 0.12249
80137 | CSDR89 | 9 | South | YES | 0.080583 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 | 0.60981 | 0.7323 |  |  |  |  | 179 | 0.12249
80137 | CSDR89 | 8 | South | YES | 0.080583 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 | 0.60981 | 0.7323 |  |  |  |  | 180 | 0.12249
80138 | CSDR7 | 7 | South | YES | 0.080583 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 | 0.60981 | 0.7323 |  |  |  |  | 181 | 0.12249
80139 | CSDR56 | 6 | South | YES | 0.080583 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 | 0.60981 | 0.7323 |  |  |  |  | 182 | 0.12249
80139 | CSDR56 | 5 | South | YES | 0.080583 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 | 0.60981 | 0.7323 |  |  |  |  | 183 | 0.12249
80226 | ALCOA G | 1 | South | YES | 0.078601 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.15176 | 0 | 0 | 0 | 0 |  |  | 0.15176 | 0 | 0.60981 | 0.7323 |  |  |  |  | 184 | 0.12249
8134 | FOR #1 | 1 | South | YES | 0.077991 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 185 | 0.12249
8138 | FOR #2 | 2 | South | YES | 0.077991 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 186 | 0.12249
8153 | FOR #3 | 3 | South | YES | 0.077991 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 187 | 0.12249
8154 | FOR #4 | 4 | South | YES | 0.077991 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 188 | 0.12249
8155 | FOR #5 | 5 | South | YES | 0.077991 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 189 | 0.12249
8156 | FOR #6 | 6 | South | YES | 0.077991 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 190 | 0.12249
8157 | FOR #7 | 7 | South | YES | 0.077991 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 191 | 0.12249
80051 | FOR #8 | 8 | South | YES | 0.077991 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 192 | 0.12249
80052 | FOR #9 | 9 | South | YES | 0.077991 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 193 | 0.12249
80053 | FOR #10 | 10 | South | YES | 0.077991 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 | 0.60981 | 0.7323 |  |  |  |  | 194 | 0.12249
7035 | L_WIRTZ_1G1Y | 1 | South | YES | 0.073215 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.14637 | 0 | 0 | 0 | 0 |  |  | 0.14637 | 0 | 0.60981 | 0.7323 |  |  |  |  | 195 | 0.12249
7036 | L_WIRTZ_1G2Y | 2 | South | YES | 0.073215 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.14637 | 0 | 0 | 0 | 0 |  |  | 0.14637 | 0 | 0.60981 | 0.7323 |  |  |  |  | 196 | 0.12249
7000 | L_FERGUS1_1Y | 1 | South | YES | 0.073077 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.14623 | 423.3 | 423.3 | 30.9335 | 423.3 |  |  | 0.14623 | 61.901 | 0.62412 | 0.74629 |  |  |  |  | 197 | 0.12249
8262 | ELPS | 1 | South | YES | 0.058475 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.13163 | 0 | 0 | 0 | 0 |  |  | 0.13163 | 0 | 0.62412 | 0.74629 |  |  |  |  | 198 | 0.12249
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.057715 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.13087 | 0 | 0 | 0 | 0 |  |  | 0.13087 | 0 | 0.62412 | 0.74629 |  |  |  |  | 199 | 0.12249
5911 | STP_GN1___1 | 1 | Houston | YES | 0.056151 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.12931 | 0 | 0 |  |  |  |  | 0.12931 | 0 | 0.62412 | 0.74629 |  |  |  |  | 200 | 0.12217
5912 | STP_GN2___2 | 2 | Houston | YES | 0.056151 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.12931 | 0 | 0 |  |  |  |  | 0.12931 | 0 | 0.62412 | 0.74629 |  |  |  |  | 201 | 0.12217
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.05598 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0 | 0.62412 | 0.74629 |  |  |  |  | 202 | 0.12217
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.05598 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0 | 0.62412 | 0.74629 |  |  |  |  | 203 | 0.12217
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.05598 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0 | 0.62412 | 0.74629 |  |  |  |  | 204 | 0.12217
48731 | CBE_GT1 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848 | 0.62669 | 0.7485 |  |  |  |  | 205 | 0.12217
48732 | CBE_GT2 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848 | 0.62926 | 0.75071 |  |  |  |  | 206 | 0.12217
48733 | CBE_ST12 | 1 | Houston | YES | 0.05559 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.12875 | 105 | 105 |  |  |  |  | 0.12875 | 13.5185 | 0.63281 | 0.75377 |  |  |  |  | 207 | 0.12217
48734 | CBE_GT3 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848 | 0.63537 | 0.75598 |  |  |  |  | 208 | 0.12181
48735 | CBE_GT4 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848 | 0.63794 | 0.75819 |  |  |  |  | 209 | 0.12145
48736 | CBE_ST34 | 1 | Houston | YES | 0.05559 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.12875 | 105 | 105 |  |  |  |  | 0.12875 | 13.5185 | 0.64149 | 0.76124 |  |  |  |  | 210 | 0.12096
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.052688 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.12585 | 0 | 0 |  |  |  |  | 0.12585 | 0 | 0.64149 | 0.76124 |  |  |  |  | 211 | 0.1206
8032 | AMISTADHYD1 | 1 | South | YES | 0.045618 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0 | 0.64149 | 0.76124 |  |  |  |  | 212 | 0.12024
8033 | AMISTADHYD2 | 2 | South | YES | 0.045618 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0 | 0.64149 | 0.76124 |  |  |  |  | 213 | 0.11975
88253 | HAMILTON | F | South | YES | 0.045618 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0 | 0.64149 | 0.76124 |  |  |  |  | 214 | 0.11975
49851 | DOW17000 | 37 | Houston | YES | 0.044148 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 215 | 0.11975
49858 | DOW38100 | 31 | Houston | YES | 0.044148 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 216 | 0.11975
49859 | DOW38200 | 33 | Houston | YES | 0.044148 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 217 | 0.11975
49860 | DOW38300 | 32 | Houston | YES | 0.044148 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 218 | 0.11975
49862 | DOW39100 | 36 | Houston | YES | 0.044148 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 219 | 0.11975
49863 | DOW39200 | 35 | Houston | YES | 0.044148 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 220 | 0.11975
49865 | DOW41000 | 41 | Houston | YES | 0.044148 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 221 | 0.11975
49866 | DOW42000 | 42 | Houston | YES | 0.044148 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 222 | 0.11975
49869 | DOW49000 | 45 | Houston | YES | 0.044148 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 223 | 0.11975
49870 | DOW61000 | 61 | Houston | YES | 0.044148 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 224 | 0.11975
49871 | DOW62000 | 62 | Houston | YES | 0.044148 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 225 | 0.11975
49872 | DOW63000 | 63 | Houston | YES | 0.044148 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 226 | 0.11975
49873 | DOW64000 | 64 | Houston | YES | 0.044148 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 227 | 0.11975
49876 | DOW65000 | 65 | Houston | YES | 0.044148 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 228 | 0.11975
49877 | DOW66000 | 66 | Houston | YES | 0.044148 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 229 | 0.11975
49878 | DOW67000 | 67 | Houston | YES | 0.044148 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 230 | 0.11975
49882 | DOW81000 | 81 | Houston | YES | 0.044148 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 231 | 0.11975
49884 | DOW82000 | 82 | Houston | YES | 0.044148 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 232 | 0.11975
49885 | DOW83000 | 83 | Houston | YES | 0.044148 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 233 | 0.11975
49886 | DOW84000 | 84 | Houston | YES | 0.044148 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 | 0.64149 | 0.76124 |  |  |  |  | 234 | 0.11975
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.041916 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.11507 | 0 | 0 |  |  |  |  | 0.11507 | 0 | 0.64149 | 0.76124 |  |  |  |  | 235 | 0.11975
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.041916 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.11507 | 0 | 0 |  |  |  |  | 0.11507 | 0 | 0.64149 | 0.76124 |  |  |  |  | 236 | 0.11975
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.04015 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0 | 0.64149 | 0.76124 |  |  |  |  | 237 | 0.11975
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.04015 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0 | 0.64149 | 0.76124 |  |  |  |  | 238 | 0.11975
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.04015 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0 | 0.64149 | 0.76124 |  |  |  |  | 239 | 0.11975
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.04015 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0 | 0.64149 | 0.76124 |  |  |  |  | 240 | 0.11975
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.033903 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 651 |  |  |  |  | 0.10706 | 69.6963 | 0.6635 | 0.77699 |  |  |  |  | 241 | 0.11975
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.033903 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 564 |  |  |  |  | 0.10706 | 60.3821 | 0.68257 | 0.79064 |  |  |  |  | 242 | 0.11975
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.033903 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 603 |  |  |  |  | 0.10706 | 64.5574 | 0.70295 | 0.80522 |  |  |  |  | 243 | 0.11975
48730 | MNS_GT | 1 | Houston | YES | 0.033879 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.10704 | 0 | 0 |  |  |  |  | 0.10704 | 0 | 0.70295 | 0.80522 |  |  |  |  | 244 | 0.11349
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.03385 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.10701 | 167.7 | 167.7 |  |  |  |  | 0.10701 | 17.9451 | 0.70862 | 0.80928 |  |  |  |  | 245 | 0.10807
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.03385 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.10701 | 166.4 | 166.4 |  |  |  |  | 0.10701 | 17.806 | 0.71425 | 0.8133 |  |  |  |  | 246 | 0.10227
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.03385 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.10701 | 252.4 | 252.4 |  |  |  |  | 0.10701 | 27.0087 | 0.72278 | 0.81941 |  |  |  |  | 247 | 0.10227
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.032933 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.10609 | 0 | 0 |  |  |  |  | 0.10609 | 0 | 0.72278 | 0.81941 |  |  |  |  | 248 | 0.10066
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.032833 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.10599 | 166 | 166 |  |  |  |  | 0.10599 | 17.5944 | 0.72839 | 0.82338 |  |  |  |  | 249 | 0.099055
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.032833 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.10599 | 166 | 166 |  |  |  |  | 0.10599 | 17.5944 | 0.734 | 0.82736 |  |  |  |  | 250 | 0.096625
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.032833 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.10599 | 248 | 248 |  |  |  |  | 0.10599 | 26.2856 | 0.74239 | 0.8333 |  |  |  |  | 251 | 0.096625
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.032833 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.10599 | 546 | 546 |  |  |  |  | 0.10599 | 57.8708 | 0.76085 | 0.84637 |  |  |  |  | 252 | 0.094989
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.032833 | 578.7 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.10599 | 0 | 654 |  |  |  |  | 0.10599 | 69.3177 | 0.78295 | 0.86204 |  |  |  |  | 253 | 0.093353
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.032833 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.10599 | 13 | 13 |  |  |  |  | 0.10599 | 1.3779 | 0.78339 | 0.86235 |  |  |  |  | 254 | 0.090909
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.028729 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 255 | 0.085528
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.028729 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 256 | 0.079082
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.028729 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 257 | 0.078954
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.028729 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 258 | 0.078954
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.028729 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 259 | 0.078954
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.028729 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 260 | 0.078954
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.028729 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 261 | 0.078954
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.028729 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 262 | 0.078954
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.028729 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 263 | 0.078954
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.028729 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 264 | 0.078954
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.028729 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 265 | 0.078954
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.028729 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 266 | 0.078954
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.028729 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 267 | 0.078954
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.028729 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 268 | 0.078954
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.028729 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | 0.78339 | 0.86235 |  |  |  |  | 269 | 0.078954
48772 | PHR_GN2_2 | MB | Houston | YES | 0.026988 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.10015 | 0 | 0 |  |  |  |  | 0.10015 | 0 | 0.78339 | 0.86235 |  |  |  |  | 270 | 0.078954
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.025774 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | 0.78339 | 0.86235 |  |  |  |  | 271 | 0.078954
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.025774 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | 0.78339 | 0.86235 |  |  |  |  | 272 | 0.078954
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.025774 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | 0.78339 | 0.86235 |  |  |  |  | 273 | 0.078954
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.025774 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | 0.78339 | 0.86235 |  |  |  |  | 274 | 0.078954
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.025774 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | 0.78339 | 0.86235 |  |  |  |  | 275 | 0.078954
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.025309 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 | 0.78339 | 0.86235 |  |  |  |  | 276 | 0.078954
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.025309 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 | 0.78339 | 0.86235 |  |  |  |  | 277 | 0.078954
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.025309 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 | 0.78339 | 0.86235 |  |  |  |  | 278 | 0.078954
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.025309 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 | 0.78339 | 0.86235 |  |  |  |  | 279 | 0.078954
48691 | GBY_73741085 | B | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 | 0.78498 | 0.86339 |  |  |  |  | 280 | 0.078954
48691 | GBY_73741085 | A | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 | 0.78657 | 0.86443 |  |  |  |  | 281 | 0.078954
48692 | GBY_81821075 | D | Houston | YES | 0.024725 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.097882 | 55 | 55 |  |  |  |  | 0.097882 | 5.3835 | 0.78843 | 0.86564 |  |  |  |  | 282 | 0.078954
48692 | GBY_81821075 | C | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 | 0.79002 | 0.86668 |  |  |  |  | 283 | 0.078405
48693 | GBY_83841065 | F | Houston | YES | 0.024725 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.097882 | 54 | 54 |  |  |  |  | 0.097882 | 5.2857 | 0.79185 | 0.86788 |  |  |  |  | 284 | 0.077855
48693 | GBY_83841065 | E | Houston | YES | 0.024725 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.097882 | 57 | 57 |  |  |  |  | 0.097882 | 5.5793 | 0.79377 | 0.86914 |  |  |  |  | 285 | 0.077213
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.024434 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.097591 | 0 | 0 |  |  |  |  | 0.097591 | 0 | 0.79377 | 0.86914 |  |  |  |  | 286 | 0.076663
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.024434 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.097591 | 0 | 0 |  |  |  |  | 0.097591 | 0 | 0.79377 | 0.86914 |  |  |  |  | 287 | 0.076032
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.024207 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.097364 | 163.2 | 163.2 |  |  |  |  | 0.097364 | 15.8899 | 0.79929 | 0.87273 |  |  |  |  | 288 | 0.075366
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.024207 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.097364 | 157.1 | 157.1 |  |  |  |  | 0.097364 | 15.296 | 0.8046 | 0.87619 |  |  |  |  | 289 | 0.075366
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.024207 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.097364 | 157.5 | 157.5 |  |  |  |  | 0.097364 | 15.3349 | 0.80993 | 0.87965 |  |  |  |  | 290 | 0.075366
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.024207 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.097364 | 157 | 157 |  |  |  |  | 0.097364 | 15.2862 | 0.81523 | 0.88311 |  |  |  |  | 291 | 0.073439
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.024207 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.097364 | 282 | 282 |  |  |  |  | 0.097364 | 27.4568 | 0.82477 | 0.88931 |  |  |  |  | 292 | 0.071585
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.023993 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.09715 | 0 | 0 |  |  |  |  | 0.09715 | 0 | 0.82477 | 0.88931 |  |  |  |  | 293 | 0.069726
48855 | SRB_GT211035 | B1 | Houston | YES | 0.023775 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.096932 | 18 | 18 |  |  |  |  | 0.096932 | 1.7448 | 0.82537 | 0.8897 |  |  |  |  | 294 | 0.067872
48855 | SRB_GT211035 | B2 | Houston | YES | 0.023775 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.096932 | 12 | 12 |  |  |  |  | 0.096932 | 1.1632 | 0.82578 | 0.88997 |  |  |  |  | 295 | 0.064543
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.023763 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.09692 | 176 | 176 |  |  |  |  | 0.09692 | 17.058 | 0.83173 | 0.89382 |  |  |  |  | 296 | 0.064543
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.023747 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.096904 | 165 | 165 |  |  |  |  | 0.096904 | 15.9892 | 0.83731 | 0.89743 |  |  |  |  | 297 | 0.064329
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.023742 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.096899 | 0 | 0 |  |  |  |  | 0.096899 | 0 | 0.83731 | 0.89743 |  |  |  |  | 298 | 0.064186
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.023742 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.096899 | 0 | 0 |  |  |  |  | 0.096899 | 0 | 0.83731 | 0.89743 |  |  |  |  | 299 | 0.062091
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.02369 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.096847 | 213 | 213 |  |  |  |  | 0.096847 | 20.6285 | 0.84451 | 0.9021 |  |  |  |  | 300 | 0.060126
48845 | SOL_GT1 | 1 | Houston | YES | 0.023686 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.096843 | 16.2 | 16.2 |  |  |  |  | 0.096843 | 1.5689 | 0.84506 | 0.90245 |  |  |  |  | 301 | 0.060126
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.023683 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 | 0.84506 | 0.90245 |  |  |  |  | 302 | 0.060126
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.023683 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 | 0.84506 | 0.90245 |  |  |  |  | 303 | 0.057587
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.023683 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 | 0.84506 | 0.90245 |  |  |  |  | 304 | 0.057394
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.023683 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 | 0.84506 | 0.90245 |  |  |  |  | 305 | 0.057394
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.023677 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 | 0.84506 | 0.90245 |  |  |  |  | 306 | 0.057394
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.023677 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 | 0.84506 | 0.90245 |  |  |  |  | 307 | 0.057394
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.023677 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 | 0.84506 | 0.90245 |  |  |  |  | 308 | 0.057394
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.023677 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.096834 | 228 | 228 |  |  |  |  | 0.096834 | 22.0783 | 0.85276 | 0.90744 |  |  |  |  | 309 | 0.057394
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.023372 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 | 0.85276 | 0.90744 |  |  |  |  | 310 | 0.057394
48821 | SHELLG2 | 2 | Houston | YES | 0.023372 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 | 0.85276 | 0.90744 |  |  |  |  | 311 | 0.057394
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.023372 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 | 0.85276 | 0.90744 |  |  |  |  | 312 | 0.054675
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.023372 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 | 0.85276 | 0.90744 |  |  |  |  | 313 | 0.054675
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.022953 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.09611 | 0 | 0 |  |  |  |  | 0.09611 | 0 | 0.85276 | 0.90744 |  |  |  |  | 314 | 0.054675
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.022853 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.09601 | 42 | 42 |  |  |  |  | 0.09601 | 4.0324 | 0.85418 | 0.90835 |  |  |  |  | 315 | 0.054675
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.022853 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.09601 | 42 | 42 |  |  |  |  | 0.09601 | 4.0324 | 0.8556 | 0.90926 |  |  |  |  | 316 | 0.054675
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.022853 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.09601 | 39 | 39 |  |  |  |  | 0.09601 | 3.7444 | 0.85692 | 0.91011 |  |  |  |  | 317 | 0.054675
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.022853 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.09601 | 39 | 39 |  |  |  |  | 0.09601 | 3.7444 | 0.85824 | 0.91095 |  |  |  |  | 318 | 0.054166
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.022792 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.095949 | 0 | 0 |  |  |  |  | 0.095949 | 0 | 0.85824 | 0.91095 |  |  |  |  | 319 | 0.053657
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.022792 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.095949 | 0 | 0 |  |  |  |  | 0.095949 | 0 | 0.85824 | 0.91095 |  |  |  |  | 320 | 0.053185
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.022175 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.095332 | 107 | 107 |  |  |  |  | 0.095332 | 10.2006 | 0.86186 | 0.91326 |  |  |  |  | 321 | 0.052713
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.022175 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.095332 | 108 | 108 |  |  |  |  | 0.095332 | 10.2959 | 0.86551 | 0.91559 |  |  |  |  | 322 | 0.052713
48875 | THW_3132 | A | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 | 0.86737 | 0.91677 |  |  |  |  | 323 | 0.052713
48875 | THW_3132 | B | Houston | YES | 0.022175 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.095332 | 53 | 53 |  |  |  |  | 0.095332 | 5.0526 | 0.86916 | 0.91791 |  |  |  |  | 324 | 0.051401
48877 | THW_3334 | C | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 | 0.87102 | 0.9191 |  |  |  |  | 325 | 0.050076
48877 | THW_3334 | D | Houston | YES | 0.022175 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.095332 | 57 | 57 |  |  |  |  | 0.095332 | 5.4339 | 0.87295 | 0.92032 |  |  |  |  | 326 | 0.049402
48879 | THW_4142 | E | Houston | YES | 0.022175 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.095332 | 56 | 56 |  |  |  |  | 0.095332 | 5.3386 | 0.87484 | 0.92153 |  |  |  |  | 327 | 0.048752
48879 | THW_4142 | F | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 | 0.8767 | 0.92272 |  |  |  |  | 328 | 0.048077
48881 | THW_4344 | G | Houston | YES | 0.022175 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.095332 | 58 | 58 |  |  |  |  | 0.095332 | 5.5293 | 0.87866 | 0.92397 |  |  |  |  | 329 | 0.047378
48881 | THW_4344 | H | Houston | YES | 0.022175 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.095332 | 58 | 58 |  |  |  |  | 0.095332 | 5.5293 | 0.88062 | 0.92521 |  |  |  |  | 330 | 0.046691
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.021662 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.094819 | 746 | 746 |  |  |  |  | 0.094819 | 70.7353 | 0.90584 | 0.9412 |  |  |  |  | 331 | 0.046017
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.021417 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.094574 | 12 | 12 |  |  |  |  | 0.094574 | 1.1349 | 0.90625 | 0.94146 |  |  |  |  | 332 | 0.045305
49803 | EXN_15GT | 1 | Houston | YES | 0.021324 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 333 | 0.044594
49804 | EXN_16GT | 2 | Houston | YES | 0.021324 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 334 | 0.035359
49805 | EXN_17GT | 3 | Houston | YES | 0.021324 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 335 | 0.035209
49826 | EXN938GT | 5 | Houston | YES | 0.021324 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 336 | 0.035209
49828 | EXN941GT | 10 | Houston | YES | 0.021324 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 337 | 0.035209
49829 | EXN942GT | 11 | Houston | YES | 0.021324 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 338 | 0.035209
49830 | EXN943GT | 12 | Houston | YES | 0.021324 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 339 | 0.035209
49831 | EXN944GT | 13 | Houston | YES | 0.021324 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 340 | 0.035209
49832 | EXN945GT | 9 | Houston | YES | 0.021324 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 341 | 0.035209
49837 | EXN_GT | 4 | Houston | YES | 0.021324 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 342 | 0.035209
49838 | EXN_14GT | 14 | Houston | YES | 0.021324 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | 0.90625 | 0.94146 |  |  |  |  | 343 | 0.035209
48651 | EP_1_2 | 1 | Houston | YES | 0.020998 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.094155 | 0 | 0 |  |  |  |  | 0.094155 | 0 | 0.90625 | 0.94146 |  |  |  |  | 344 | 0.035209
48651 | EP_1_2 | 2 | Houston | YES | 0.020998 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.094155 | 0 | 0 |  |  |  |  | 0.094155 | 0 | 0.90625 | 0.94146 |  |  |  |  | 345 | 0.035209
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.020987 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.094144 | 0 | 0 |  |  |  |  | 0.094144 | 0 | 0.90625 | 0.94146 |  |  |  |  | 346 | 0.035209
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.020975 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.094132 | 744 | 744 |  |  |  |  | 0.094132 | 70.0345 | 0.9314 | 0.95728 |  |  |  |  | 347 | 0.035209
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.020965 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | 0.9314 | 0.95728 |  |  |  |  | 348 | 0.035209
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.020965 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | 0.9314 | 0.95728 |  |  |  |  | 349 | 0.035209
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.020965 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | 0.9314 | 0.95728 |  |  |  |  | 350 | 0.025883
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.020965 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | 0.9314 | 0.95728 |  |  |  |  | 351 | 0.025883
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.020965 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | 0.9314 | 0.95728 |  |  |  |  | 352 | 0.025883
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.020965 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | 0.9314 | 0.95728 |  |  |  |  | 353 | 0.025883
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.020965 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | 0.9314 | 0.95728 |  |  |  |  | 354 | 0.025883
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.020784 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.093941 | 0 | 0 |  |  |  |  | 0.093941 | 0 | 0.9314 | 0.95728 |  |  |  |  | 355 | 0.025883
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 | 0.93721 | 0.96093 |  |  |  |  | 356 | 0.025883
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 | 0.94303 | 0.96458 |  |  |  |  | 357 | 0.025883
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 | 0.94884 | 0.96822 |  |  |  |  | 358 | 0.025883
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.020115 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.093272 | 162.8 | 162.8 |  |  |  |  | 0.093272 | 15.1848 | 0.95434 | 0.97165 |  |  |  |  | 359 | 0.023716
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.020115 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.093272 | 161.4 | 161.4 |  |  |  |  | 0.093272 | 15.0542 | 0.9598 | 0.97506 |  |  |  |  | 360 | 0.021549
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.020115 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.093272 | 158.9 | 158.9 |  |  |  |  | 0.093272 | 14.821 | 0.96517 | 0.9784 |  |  |  |  | 361 | 0.019381
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.020115 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.093272 | 269.2 | 269.2 |  |  |  |  | 0.093272 | 25.1089 | 0.97427 | 0.98408 |  |  |  |  | 362 | 0.017309
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.019936 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.093093 | 398 | 398 |  |  |  |  | 0.093093 | 37.0512 | 0.98773 | 0.99245 |  |  |  |  | 363 | 0.015254
48885 | THW_5152 | B | Houston | YES | 0.019689 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.092846 | 59 | 59 |  |  |  |  | 0.092846 | 5.4779 | 0.98972 | 0.99369 |  |  |  |  | 364 | 0.013232
48885 | THW_5152 | A | Houston | YES | 0.019689 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.092846 | 58 | 58 |  |  |  |  | 0.092846 | 5.3851 | 0.99168 | 0.99491 |  |  |  |  | 365 | 0.0098049
48886 | THW_5354 | D | Houston | YES | 0.019689 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.092846 | 58 | 58 |  |  |  |  | 0.092846 | 5.3851 | 0.99364 | 0.99612 |  |  |  |  | 366 | 0.0047225
48886 | THW_5354 | C | Houston | YES | 0.019689 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.092846 | 57 | 57 |  |  |  |  | 0.092846 | 5.2922 | 0.99557 | 0.99732 |  |  |  |  | 367 | 0.0039658
48887 | THW_5556 | E | Houston | YES | 0.019689 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.092846 | 59 | 59 |  |  |  |  | 0.092846 | 5.4779 | 0.99757 | 0.99856 |  |  |  |  | 368 | 0.0032219
48887 | THW_5556 | F | Houston | YES | 0.019689 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.092846 | 57 | 57 |  |  |  |  | 0.092846 | 5.2922 | 0.99949 | 0.99975 |  |  |  |  | 369 | 0.002478
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.016213 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | 0.99949 | 0.99975 |  |  |  |  | 370 | 0.0017469
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.016213 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | 0.99949 | 0.99975 |  |  |  |  | 371 | 0.00099019
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.016213 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | 0.99949 | 0.99975 |  |  |  |  | 372 | 0.00025912
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.016213 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | 0.99949 | 0.99975 |  |  |  |  | 373 | 0.00025912
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.016213 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | 0.99949 | 0.99975 |  |  |  |  | 374 | 0.00025912
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.073157 | 15 | 15 | 0 | 15 |  |  | 0.073157 | 1.0974 | 1 | 1 |  |  |  |  | 375 | 0.00025912
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 376 | 0.00025912
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 377 | 0.00025912
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 378 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 379 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 380 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 381 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 382 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 383 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.073157 | 0 | 0 |  |  |  |  | 0.073157 | 0 | 1 | 1 |  |  |  |  | 384 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | -0.014565 | 0 | 2 | 48 |  | 1.015 | GST | -1 | 0.12021 | 48 | 48 |  |  | -0.69912 | 48 | -0.12021 | -5.7702 | [6 empty] | 385 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | -0.014565 | 46 | 2 | 46 | 0 | 1.015 | GST | -1 | 0.12021 | 46 | 46 |  |  | -0.66999 | 46 | -0.12021 | -5.5298 | [6 empty] | 386 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | -0.014565 | 84 | 25 | 105 | 0 | 1.035 | GST | -1 | 0.12021 | 105 | 105 |  |  | -1.5293 | 105 | -0.12021 | -12.6223 | [6 empty] | 387 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | -0.015218 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | -1 | 0.12087 | 154.2 | 154.2 |  |  | -2.3466 | 154.2 | -0.12087 | -18.6375 | [6 empty] | 388 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | -0.015218 | 159 | 0 | 159 | 0 | 1.0319 | CC | -1 | 0.12087 | 159 | 159 |  |  | -2.4197 | 159 | -0.12087 | -19.2176 | [6 empty] | 389 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | -0.015218 | 158 | 0 | 158 | 0 | 1.0319 | CC | -1 | 0.12087 | 158 | 158 |  |  | -2.4044 | 158 | -0.12087 | -19.0968 | [6 empty] | 390 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | -0.015218 | 380 | 0 | 380 | 0 | 1.0319 | CC | -1 | 0.12087 | 380 | 380 |  |  | -5.7828 | 380 | -0.12087 | -45.929
32886 | BRYN_ATKINS3 | MB | North | YES | -0.016796 | 0 | 5 | 12 |  | 1 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | -0.016796 | 0 | 12 | 51 |  | 1.028 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | -0.016796 | 13.6 | 4 | 17 |  | 1.028 | GGT | -1 | 0.12244 | 17 | 17 |  |  | -0.28553 | 17 | -0.12244 | -2.0815
32890 | BRYN_ATKINS4 | MB | North | YES | -0.016796 | 0 | 5 | 22 |  | 1.031 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | -0.016796 | 0 | 5 | 25 |  | 1.031 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | -0.016957 | 32 | 0 | 32 |  | 1.02 | GST | -1 | 0.1226 | 32 | 32 |  |  | -0.54262 | 32 | -0.1226 | -3.9234
990 | GIBN_CREK_G1 | 1 | North | YES | -0.021238 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | -1 | 0.12689 | 0 | 463 |  |  | 0 | 0 | -0.12689 | 0
39960 | TNTNPONE_18 | 1 | North | YES | -0.041618 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | -1 | 0.14727 | 0 | 152.3 |  |  | 0 | 0 | -0.14727 | 0
39970 | TNTNPONE_28 | 1 | North | YES | -0.041618 | 153 | 30 | 153 |  | 1.04 | LIGCO | -1 | 0.14727 | 0 | 153 |  |  | 0 | 0 | -0.14727 | 0
60202 | FRNDDRCS | F | West | YES | -0.042109 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.14776 | 0 | 0 |  |  |  |  | -0.14776 | 0
48721 | LEG_1___1 | 1 | North | YES | -0.050274 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | -1 | 0.15592 | 0 | 827 |  |  | 0 | 0 | -0.15592 | 0
48722 | LEG_2___2 | 2 | North | YES | -0.050274 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | -1 | 0.15592 | 0 | 819 |  |  | 0 | 0 | -0.15592 | 0
60018 | DSKY1 | 1 | West | YES | -0.052795 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.15844 | 0 | 84 |  |  |  |  | -0.15844 | 0
60000 | DSKY2 | 1 | West | YES | -0.052969 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.15862 | 0 | 76.5 |  |  |  |  | -0.15862 | 0
60017 | ORNNWP1 | 1 | West | YES | -0.053485 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.15913 | 0 | 80 |  |  |  |  | -0.15913 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | -0.055531 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.16118 | 0 | 150 |  |  |  |  | -0.16118 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.05559 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.16124 | 0 | 80 |  |  |  |  | -0.16124 | 0
60016 | WOODWRD11A | 1 | West | YES | -0.055604 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.16125 | 0 | 80 |  |  |  |  | -0.16125 | 0
6016 | SWMESA | 1 | West | YES | -0.055675 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.16132 | 0 | 75 |  |  |  |  | -0.16132 | 0
60003 | KING_NE1A | 1 | West | YES | -0.055675 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16132 | 0 | 80 |  |  |  |  | -0.16132 | 0
60005 | KING_SE1A | 1 | West | YES | -0.055675 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.16132 | 0 | 40 |  |  |  |  | -0.16132 | 0
60201 | RIO DRCS | F | West | YES | -0.055786 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.16143 | 0 | 0 |  |  |  |  | -0.16143 | 0
60007 | KING_SW1A | 1 | West | YES | -0.05606 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16171 | 0 | 80 |  |  |  |  | -0.16171 | 0
60019 | KING_NW1A | 1 | West | YES | -0.05606 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16171 | 0 | 80 |  |  |  |  | -0.16171 | 0
1349 | WESTXWIN_1G | 1 | West | YES | -0.061675 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.16732 | 0 | 6.6 |  |  |  |  | -0.16732 | 0
1350 | NWPWRG1_1G | 1 | West | YES | -0.061675 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.16732 | 0 | 34.3 |  |  |  |  | -0.16732 | 0
1002 | PBCTAGE_1G | A | West | YES | -0.062012 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.16766 | 66 | 66 |  |  |  |  | -0.16766 | -11.0655
1003 | PBCTBGE_2G | B | West | YES | -0.062012 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.16766 | 66 | 66 |  |  |  |  | -0.16766 | -11.0655
1004 | PBCTCGE_3G | C | West | YES | -0.062012 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.16766 | 67 | 67 |  |  |  |  | -0.16766 | -11.2332
1005 | PBCTDGE_4G | D | West | YES | -0.062012 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.16766 | 68 | 68 |  |  |  |  | -0.16766 | -11.4009
1006 | PBCTEGE_5G | E | West | YES | -0.062012 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.16766 | 67 | 67 |  |  |  |  | -0.16766 | -11.2332
1007 | PB5GEN_6G | 5 | West | YES | -0.062012 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.16766 | 114 | 114 |  |  |  |  | -0.16766 | -19.1132
1008 | PB6GEN_7G | 6 | West | YES | -0.062012 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.16766 | 515 | 515 |  |  |  |  | -0.16766 | -86.3447
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.062075 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.16772 | 0 | 35 |  |  |  |  | -0.16772 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.062075 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.16772 | 0 | 30 |  |  |  |  | -0.16772 | 0
3381 | BBRN_1G | 1 | North | YES | -0.062158 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | -1 | 0.16781 | 0 | 618 |  |  | 0 | 0 | -0.16781 | 0
3382 | BBRN_2G | 2 | North | YES | -0.062158 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | -1 | 0.16781 | 0 | 589 |  |  | 0 | 0 | -0.16781 | 0
11147 | NOTREES_1G | 1 | West | YES | -0.062197 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.16784 | 0 | 149 |  |  |  |  | -0.16784 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.062293 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.16794 | 0 | 112.5 |  |  |  |  | -0.16794 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.062293 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 149.5 |  |  |  |  | -0.16794 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.062293 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 186 |  |  |  |  | -0.16794 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.062293 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 214.5 |  |  |  |  | -0.16794 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.062487 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | -1 | 0.16813 | 0 | 114 |  |  |  |  | -0.16813 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | -0.062585 | 30 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.16823 | 0 | 150 |  |  |  |  | -0.16823 | 0
1320 | BSP 1 | 1 | West | YES | -0.062814 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.16846 | 0 | 0 |  |  |  |  | -0.16846 | 0
1326 | STANTONW_8 | 1 | West | YES | -0.06289 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.16854 | 0 | 100.5 |  |  |  |  | -0.16854 | 0
11020 | TIEHVSG_1G | 1 | West | YES | -0.062906 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.16855 | 208.2 | 208.2 |  |  |  |  | -0.16855 | -35.0929
11021 | TIEHVCG_1G | 1 | West | YES | -0.062906 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.16855 | 142.1 | 142.1 |  |  |  |  | -0.16855 | -23.9515
11022 | TIEHVCG_2G | 1 | West | YES | -0.062906 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.16855 | 132.4 | 132.4 |  |  |  |  | -0.16855 | -22.3165
11023 | TIEHVCG_3G | 1 | West | YES | -0.062906 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.16855 | 137.4 | 137.4 |  |  |  |  | -0.16855 | -23.1593
11024 | TIEHVCG_4G | 1 | West | YES | -0.062906 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.16855 | 147 | 147 |  |  |  |  | -0.16855 | -24.7774
11025 | TIEHVSG_2G | 1 | West | YES | -0.062906 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.16855 | 213.2 | 213.2 |  |  |  |  | -0.16855 | -35.9356
11001 | NAV1CT | 1 | West | YES | -0.062916 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.16856 | 70.4 | 70.4 |  |  |  |  | -0.16856 | -11.8669
11009 | NAV2CT | 1 | West | YES | -0.062916 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.16856 | 71.4 | 71.4 |  |  |  |  | -0.16856 | -12.0354
11011 | NAV3ST | 1 | West | YES | -0.062916 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.16856 | 92.8 | 92.8 |  |  |  |  | -0.16856 | -15.6427
11012 | NAV4CT | 1 | West | YES | -0.062916 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.16856 | 80 | 80 |  |  |  |  | -0.16856 | -13.4851
11013 | NAV5CT | 1 | West | YES | -0.062916 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.16856 | 80 | 80 |  |  |  |  | -0.16856 | -13.4851
11014 | NAV6ST | 1 | West | YES | -0.062916 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.16856 | 115 | 115 |  |  |  |  | -0.16856 | -19.3848
13131 | CALFREST_1G | 1 | North | YES | -0.062996 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | -1 | 0.16864 | 150.7 | 150.7 |  |  | -9.4935 | 150.7 | -0.16864 | -25.4146
13132 | CALFREST_2G | 2 | North | YES | -0.062996 | 151 | 57 | 151 | 0 | 1.031 | CC | -1 | 0.16864 | 151 | 151 |  |  | -9.5124 | 151 | -0.16864 | -25.4652
13133 | CALFREST_3G | 3 | North | YES | -0.062996 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | -1 | 0.16864 | 177.4 | 177.4 |  |  | -11.1755 | 177.4 | -0.16864 | -29.9174
1328 | OCOTILLO_1G | 1 | West | YES | -0.063008 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.16866 | 0 | 58 |  |  |  |  | -0.16866 | 0
1333 | MCDDONAL_8 | 1 | West | YES | -0.063168 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.16882 | 0 | 214.2 |  |  |  |  | -0.16882 | 0
13134 | CALFREST_4G | 4 | North | YES | -0.063173 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | -1 | 0.16882 | 151.5 | 151.5 |  |  | -9.5707 | 151.5 | -0.16882 | -25.5763
13135 | CALFREST_5G | 5 | North | YES | -0.063173 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | -1 | 0.16882 | 152.3 | 152.3 |  |  | -9.6212 | 152.3 | -0.16882 | -25.7114
13136 | CALFREST_6G | 6 | North | YES | -0.063173 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | -1 | 0.16882 | 177.5 | 177.5 |  |  | -11.2132 | 177.5 | -0.16882 | -29.9657
1327 | WILDHRSE_1G | 1 | West | YES | -0.063374 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.16902 | 0 | 120 |  |  |  |  | -0.16902 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.06341 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.16906 | 0 | 120 |  |  |  |  | -0.16906 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.063659 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.16931 | 0 | 225 |  |  |  |  | -0.16931 | 0
1045 | CALENG1G_1G | 1 | West | YES | -0.063663 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0
1046 | CALENG2G_2G | 2 | West | YES | -0.063663 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0
1047 | CALENG3G_3G | 3 | West | YES | -0.063663 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.063719 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.16937 | 0 | 180 |  |  |  |  | -0.16937 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.063719 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.16937 | 0 | 180 |  |  |  |  | -0.16937 | 0
1058 | LONGSHORE_5 | 1 | West | YES | -0.063837 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.16948 | 0 | 150 |  |  |  |  | -0.16948 | 0
1058 | LONGSHORE_5 | 2 | West | YES | -0.063837 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.16948 | 0 | 220 |  |  |  |  | -0.16948 | 0
11065 | ELBOWCK_1G | 1 | West | YES | -0.063837 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.16948 | 0 | 121.9 |  |  |  |  | -0.16948 | 0
60058 | BUFF_GAP1A | 1 | West | YES | -0.063992 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.16964 | 0 | 120 |  |  |  |  | -0.16964 | 0
60060 | CIRELLO | 1 | West | YES | -0.063992 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.16964 | 0 | 233 |  |  |  |  | -0.16964 | 0
60063 | BUFF_GAP1B | 1 | West | YES | -0.063992 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.16964 | 0 | 170.2 |  |  |  |  | -0.16964 | 0
60066 | H_HOLLOW1A | 1 | West | YES | -0.063992 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.16964 | 0 | 222 |  |  |  |  | -0.16964 | 0
60068 | HHOLLOW21A | 1 | West | YES | -0.063992 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 184 |  |  |  |  | -0.16964 | 0
60070 | HHOLLOW31A | 1 | West | YES | -0.063992 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 224 |  |  |  |  | -0.16964 | 0
60072 | HHOLLOW41A | 1 | West | YES | -0.063992 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 115 |  |  |  |  | -0.16964 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.063995 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.16964 | 137 | 137 |  |  |  |  | -0.16964 | -23.241
1039 | MRGNAG_1G | A | West | YES | -0.063995 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.16964 | 69 | 69 |  |  |  |  | -0.16964 | -11.7053
1040 | MRGNBG_2G | B | West | YES | -0.063995 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.16964 | 71 | 71 |  |  |  |  | -0.16964 | -12.0446
1041 | MRGNCG_3G | C | West | YES | -0.063995 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.16964 | 70 | 70 |  |  |  |  | -0.16964 | -11.875
1042 | MRGNDG_4G | D | West | YES | -0.063995 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.16964 | 68 | 68 |  |  |  |  | -0.16964 | -11.5357
1043 | MRGNEG_5G | E | West | YES | -0.063995 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.16964 | 70 | 70 |  |  |  |  | -0.16964 | -11.875
1044 | MRGNFG_6G | F | West | YES | -0.063995 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.16964 | 66 | 66 |  |  |  |  | -0.16964 | -11.1964
6637 | SNYDERW1A | 1 | West | YES | -0.064071 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.16972 | 0 | 63 |  |  |  |  | -0.16972 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.064132 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.16978 | 0 | 141 |  |  |  |  | -0.16978 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.064132 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.16978 | 0 | 120 |  |  |  |  | -0.16978 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.064142 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.16979 | 0 | 99 |  |  |  |  | -0.16979 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.064142 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.16979 | 0 | 61 |  |  |  |  | -0.16979 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.064142 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.064142 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.064142 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0
36998 | RDCNYNG1 | 1 | West | YES | -0.064322 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.16997 | 0 | 84 |  |  |  |  | -0.16997 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.064746 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.17039 | 0 | 150 |  |  |  |  | -0.17039 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.064746 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.17039 | 0 | 101 |  |  |  |  | -0.17039 | 0
11056 | ROSCOE_1G | 1 | West | YES | -0.064846 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.17049 | 0 | 209 |  |  |  |  | -0.17049 | 0
11057 | CHAMPION_1G | 1 | West | YES | -0.064846 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.17049 | 0 | 126.5 |  |  |  |  | -0.17049 | 0
11058 | PYRON_1G | 1 | West | YES | -0.064846 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.17049 | 0 | 249 |  |  |  |  | -0.17049 | 0
11059 | INADALE_1G | 1 | West | YES | -0.064846 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.17049 | 0 | 197 |  |  |  |  | -0.17049 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | -0.064849 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 37.5 |  |  |  |  | -0.1705 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | -0.064849 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 107.5 |  |  |  |  | -0.1705 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | -0.064849 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 135 |  |  |  |  | -0.1705 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | -0.064849 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 119 |  |  |  |  | -0.1705 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | -0.064849 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 105 |  |  |  |  | -0.1705 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | -0.064849 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 80.5 |  |  |  |  | -0.1705 | 0
6144 | MCADOO1A | 1 | West | YES | -0.065112 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.17076 | 0 | 150 |  |  |  |  | -0.17076 | 0
6407 | TURKTRAK1A | 1 | West | YES | -0.065221 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.17087 | 0 | 169.5 |  |  |  |  | -0.17087 | 0
1416 | SWETWATR_1G | 1 | West | YES | -0.065247 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.17089 | 30 | 30 |  |  |  |  | -0.17089 | -5.1268
1417 | SWETWATR_2G | 2 | West | YES | -0.065247 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.17089 | 72 | 72 |  |  |  |  | -0.17089 | -12.3044
1418 | SWETWATR_3G | 3 | West | YES | -0.065247 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.17089 | 68 | 68 |  |  |  |  | -0.17089 | -11.6208
1419 | SWETWATR_4G | 4 | West | YES | -0.065247 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.17089 | 61 | 61 |  |  |  |  | -0.17089 | -10.4246
60081 | WHRLWIND1A | 1 | West | YES | -0.066019 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.17167 | 0 | 60 |  |  |  |  | -0.17167 | 0
3107 | STRYKER_1G | 1 | North | YES | -0.066332 | 145.6 | 45 | 182 | 0 | 1.029 | GST | -1 | 0.17198 | 182 | 182 |  |  | -12.0724 | 182 | -0.17198 | -31.3003
3108 | STRYKER_2G | 2 | North | YES | -0.066332 | 484 | 75 | 484 | 0 | 1.029 | GST | -1 | 0.17198 | 484 | 484 |  |  | -32.1047 | 484 | -0.17198 | -83.2382
3309 | ASPN_G | 1 | North | YES | -0.066592 | 50 | 0 | 50 |  | 1 | Bio | -1 | 0.17224 | 50 | 50 |  |  | -3.3296 | 50 | -0.17224 | -8.612
3348 | CHAMPION_1G | MB | North | YES | -0.066625 | 0 | 42 | 42 |  | 1 | Cogen | -1 | 0.17227 | 0 | 0 |  |  | 0 | 0 | -0.17227 | 0
13116 | TGATEWAY_1G | 1 | North | YES | -0.067045 | 151 | 30 | 151 | 0 | 1.0232 | CC | -1 | 0.17269 | 151 | 151 |  |  | -10.1238 | 151 | -0.17269 | -26.0766
13117 | TGATEWAY_2G | 2 | North | YES | -0.067045 | 130 | 30 | 130 | 0 | 1.0232 | CC | -1 | 0.17269 | 130 | 130 |  |  | -8.7158 | 130 | -0.17269 | -22.4501
13118 | TGATEWAY_3G | 3 | North | YES | -0.067045 | 148 | 30 | 148 | 0 | 1.0232 | CC | -1 | 0.17269 | 148 | 148 |  |  | -9.9227 | 148 | -0.17269 | -25.5585
13119 | TGATEWAY_4G | 4 | North | YES | -0.067045 | 399 | 65 | 399 | 0 | 1.0232 | CC | -1 | 0.17269 | 399 | 399 |  |  | -26.751 | 399 | -0.17269 | -68.9044
1437 | MESQUITW_1G | 1 | North | YES | -0.067055 | 40 | 0 | 400 | 0 | 1.023 | Wind | -1 | 0.1727 | 0 | 400 |  |  | 0 | 0 | -0.1727 | 0
1438 | MESQUITW_2G | 1 | North | YES | -0.067058 | 23.6 | 0 | 236 |  | 1.017 | Wind | -1 | 0.17271 | 0 | 236 |  |  | 0 | 0 | -0.17271 | 0
3097 | MARTLAKE_1G | 1 | North | YES | -0.067389 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 790 |  |  | 0 | 0 | -0.17304 | 0
3098 | MARTLAKE_2G | 2 | North | YES | -0.067389 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 795 |  |  | 0 | 0 | -0.17304 | 0
3099 | MARTLAKE_3G | 3 | North | YES | -0.067389 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 804 |  |  | 0 | 0 | -0.17304 | 0
1442 | COKFIELD_5 | 1 | North | YES | -0.067751 | 16.5 | 0 | 165 |  | 1.029 | Wind | -1 | 0.1734 | 0 | 165 |  |  | 0 | 0 | -0.1734 | 0
6100 | OKLA7A | EQ | West | YES | -0.068286 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.17393 | 0 | 0 |  |  |  |  | -0.17393 | 0
6752 | OKLA0A | 1 | West | YES | -0.068286 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.17393 | 0 | 649.7 |  |  |  |  | -0.17393 | 0
1432 | GRHAMSES_2G | 2 | North | YES | -0.069944 | 294.9 | 90 | 366 | 0 | 1.014 | GST | -1 | 0.17559 | 366 | 366 |  |  | -25.5995 | 366 | -0.17559 | -64.2666
12411 | FPLEFR1A_G | 1 | North | YES | -0.070029 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.17568 | 161 | 161 |  |  | -11.2747 | 161 | -0.17568 | -28.2839
12412 | FPLEFR1B_G | 2 | North | YES | -0.070029 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.17568 | 164 | 164 |  |  | -11.4848 | 164 | -0.17568 | -28.811
12413 | FPLEFR1C_G | 3 | North | YES | -0.070029 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.17568 | 164 | 164 |  |  | -11.4848 | 164 | -0.17568 | -28.811
12414 | FPLEFR1S_G | 4 | North | YES | -0.070029 | 414 | 191 | 414 | 0 | 1 | CC | -1 | 0.17568 | 414 | 414 |  |  | -28.992 | 414 | -0.17568 | -72.7302
12421 | FPLEFR2A_G | 1 | North | YES | -0.070029 | 162 | 72 | 162 | 0 | 1 | CC | -1 | 0.17568 | 162 | 162 |  |  | -11.3447 | 162 | -0.17568 | -28.4596
12422 | FPLEFR2B_G | 2 | North | YES | -0.070029 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.17568 | 161 | 161 |  |  | -11.2747 | 161 | -0.17568 | -28.2839
12423 | FPLEFR2C_G | 3 | North | YES | -0.070029 | 163 | 72 | 163 | 0 | 1 | CC | -1 | 0.17568 | 163 | 163 |  |  | -11.4147 | 163 | -0.17568 | -28.6353
12424 | FPLEFR2S_G | 4 | North | YES | -0.070029 | 415 | 191 | 415 | 0 | 1 | CC | -1 | 0.17568 | 415 | 415 |  |  | -29.062 | 415 | -0.17568 | -72.9058
1479 | WFCOGEN_1G | 1 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0
1479 | WFCOGEN_1G | 2 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0
1482 | WFCOGEN_2G | 2 | North | YES | -0.070041 | 13.6 | 12 | 17 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0
1482 | WFCOGEN_2G | 1 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0
1433 | GRHAMSES_1G | 1 | North | YES | -0.070142 | 242 | 60 | 242 | 0 | 1.038 | GST | -1 | 0.17579 | 242 | 242 |  |  | -16.9744 | 242 | -0.17579 | -42.5411
3126 | TRINIDAD_6G | 1 | North | YES | -0.070556 | 179.2 | 46 | 224 | 0 | 1 | GST | -1 | 0.1762 | 224 | 224 |  |  | -15.8045 | 224 | -0.1762 | -39.4696
2451 | LKHB1_G | 1 | North | YES | -0.070564 | 0 | 80 | 391 |  | 1.022 | GST | -1 | 0.17621 | 391 | 391 |  |  | -27.5905 | 391 | -0.17621 | -68.8988
2452 | LKHB2_G | 2 | North | YES | -0.070564 | 516 | 80 | 516 | 0 | 1.022 | GST | -1 | 0.17621 | 516 | 516 |  |  | -36.411 | 516 | -0.17621 | -90.9252
12440 | PARKD_1SVC8 | 1 | North | YES | -0.070682 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.17633 | 0 | 0 |  |  | 0 | 0 | -0.17633 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | -0.070682 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.17633 | 0 | 0 |  |  | 0 | 0 | -0.17633 | 0
948 | STEAM1 | 1 | North | YES | -0.070707 | 0 | 12 | 20 |  | 1.02 | GST | -1 | 0.17635 | 20 | 20 |  |  | -1.4141 | 20 | -0.17635 | -3.5271
949 | STEAM2 | 1 | North | YES | -0.070707 | 26 | 8 | 26 | 0 | 0.99 | GST | -1 | 0.17635 | 26 | 26 |  |  | -1.8384 | 26 | -0.17635 | -4.5852
950 | STEAM3 | 1 | North | YES | -0.070707 | 41 | 13 | 42 | 0 | 1.02 | GST | -1 | 0.17635 | 42 | 42 |  |  | -2.9697 | 42 | -0.17635 | -7.4069
842 | OLINGER_G1 | 1 | North | YES | -0.070819 | 55.4 | 20 | 79 | 0 | 1.03 | GST | -1 | 0.17647 | 79 | 79 |  |  | -5.5947 | 79 | -0.17647 | -13.9409
843 | OLINGER_G2 | 1 | North | YES | -0.070819 | 76.2 | 25 | 110 | 0 | 1.03 | GST | -1 | 0.17647 | 110 | 110 |  |  | -7.7901 | 110 | -0.17647 | -19.4113
844 | OLINGER_G3 | 1 | North | YES | -0.070819 | 103.9 | 45 | 150 | 0 | 1.03 | GST | -1 | 0.17647 | 150 | 150 |  |  | -10.6228 | 150 | -0.17647 | -26.47
845 | OLINGER_G4 | 1 | North | YES | -0.070819 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | -1 | 0.17647 | 76 | 76 |  |  | -5.3822 | 76 | -0.17647 | -13.4115
837 | NEWMAN_G5 | 1 | North | YES | -0.070826 | 0 | 15 | 40 |  | 1.01 | GST | -1 | 0.17647 | 40 | 40 |  |  | -2.833 | 40 | -0.17647 | -7.0589
1701 | MOSES_1G | 1 | North | YES | -0.070891 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 558 |  |  | 0 | 0 | -0.17654 | 0
1702 | MOSES_2G | 2 | North | YES | -0.070891 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 579 |  |  | 0 | 0 | -0.17654 | 0
1703 | MOSES_3G | 3 | North | YES | -0.070891 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 808 |  |  | 0 | 0 | -0.17654 | 0
5925 | DCEAST | EQ | North | YES | -0.070891 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | -1 | 0.17654 | 0 | 0 |  |  | 0 | 0 | -0.17654 | 0
1675 | PEC_1G | 1 | North | YES | -0.070943 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0
1676 | PEC_2G | 2 | North | YES | -0.070943 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0
1677 | PEC_3G | 3 | North | YES | -0.070943 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0
1678 | LAMARPWR_1G | 1 | North | YES | -0.071002 | 160 | 67.7 | 160 | 0 | 1.038 | CC | -1 | 0.17665 | 160 | 160 |  |  | -11.3603 | 160 | -0.17665 | -28.264
1679 | LAMARPWR_2G | 2 | North | YES | -0.071002 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.17665 | 156 | 156 |  |  | -11.0763 | 156 | -0.17665 | -27.5574
1680 | LAMARPWR_3G | 3 | North | YES | -0.071002 | 196 | 129.1 | 196 | 0 | 1.038 | CC | -1 | 0.17665 | 196 | 196 |  |  | -13.9164 | 196 | -0.17665 | -34.6233
1681 | LAMARPWR_4G | 4 | North | YES | -0.071002 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.17665 | 156 | 156 |  |  | -11.0763 | 156 | -0.17665 | -27.5574
1682 | LAMARPWR_5G | 5 | North | YES | -0.071002 | 157 | 67.7 | 157 | 0 | 1.038 | CC | -1 | 0.17665 | 157 | 157 |  |  | -11.1473 | 157 | -0.17665 | -27.734
1683 | LAMARPWR_6G | 6 | North | YES | -0.071002 | 198 | 129.1 | 198 | 0 | 1.038 | CC | -1 | 0.17665 | 198 | 198 |  |  | -14.0584 | 198 | -0.17665 | -34.9766
1689 | VALLEY_3G | 3 | North | YES | -0.07107 | 0 | 25 | 375 |  | 1.003 | GST | -1 | 0.17672 | 375 | 375 |  |  | -26.6513 | 375 | -0.17672 | -66.2691
11691 | KMICHICT1_G | 1 | North | YES | -0.07107 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.17672 | 144 | 144 |  |  | -10.2341 | 144 | -0.17672 | -25.4473
11692 | KMICHICT2_G | 2 | North | YES | -0.07107 | 146 | 80 | 146 | 0 | 1.026 | CC | -1 | 0.17672 | 146 | 146 |  |  | -10.3762 | 146 | -0.17672 | -25.8008
11693 | KMICHIST3_G | 3 | North | YES | -0.07107 | 312 | 60 | 312 | 0 | 1.026 | CC | -1 | 0.17672 | 312 | 312 |  |  | -22.1738 | 312 | -0.17672 | -55.1359
11694 | KMICHICT4_G | 4 | North | YES | -0.07107 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.17672 | 144 | 144 |  |  | -10.2341 | 144 | -0.17672 | -25.4473
11695 | KMICHICT5_G | 5 | North | YES | -0.07107 | 148 | 80 | 148 | 0 | 1.026 | CC | -1 | 0.17672 | 148 | 148 |  |  | -10.5184 | 148 | -0.17672 | -26.1542
11696 | KMICHIST6_G | 6 | North | YES | -0.07107 | 310 | 60 | 310 | 0 | 1.026 | CC | -1 | 0.17672 | 310 | 310 |  |  | -22.0317 | 310 | -0.17672 | -54.7825
1687 | VALLEY_1G | 1 | North | YES | -0.071166 | 136 | 15 | 170 | 0 | 1.029 | GST | -1 | 0.17681 | 170 | 170 |  |  | -12.0982 | 170 | -0.17681 | -30.0583
1688 | VALLEY_2G | 2 | North | YES | -0.071166 | 527 | 90 | 527 | 0 | 1.029 | GSC | -1 | 0.17681 | 527 | 527 |  |  | -37.5045 | 527 | -0.17681 | -93.1808
6948 | DENISNDM | 1 | North | YES | -0.071253 | 40 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.1769 | 0 | 0 |  |  | 0 | 0 | -0.1769 | 0
6948 | DENISNDM | 2 | North | YES | -0.071253 | 31 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.1769 | 0 | 0 |  |  | 0 | 0 | -0.1769 | 0
2371 | COLLIN_1G | MB | North | YES | -0.071683 | 0 | 40 | 138 |  | 1.022 | GST | -1 | 0.17733 | 0 | 0 |  |  | 0 | 0 | -0.17733 | 0
1453 | WCPWRCO_1G | 1 | North | YES | -0.071787 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.17743 | 204 | 204 |  |  | -14.6445 | 204 | -0.17743 | -36.1967
1454 | WCPWRCO_2G | 2 | North | YES | -0.071787 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.17743 | 204 | 204 |  |  | -14.6445 | 204 | -0.17743 | -36.1967
1455 | WCPWRCO_3G | 3 | North | YES | -0.071787 | 242 | 50 | 242 |  | 1.02 | CC | -1 | 0.17743 | 242 | 242 |  |  | -17.3725 | 242 | -0.17743 | -42.9392
2413 | MTCK6_G | 6 | North | YES | -0.071897 | 0 | 30 | 118 |  | 1.022 | GST | -1 | 0.17754 | 118 | 118 |  |  | -8.4838 | 118 | -0.17754 | -20.9503
2414 | MTCK7_G | 7 | North | YES | -0.071897 | 0 | 30 | 115 |  | 1.022 | GST | -1 | 0.17754 | 115 | 115 |  |  | -8.2682 | 115 | -0.17754 | -20.4176
2417 | MTCK8_G | 8 | North | YES | -0.071897 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | -1 | 0.17754 | 556 | 556 |  |  | -39.9747 | 556 | -0.17754 | -98.7149
1600 | BARTNWND_1G | 1 | North | YES | -0.071906 | 12 | 0 | 120 | 0 | 1.022 | Wind | -1 | 0.17755 | 0 | 120 |  |  | 0 | 0 | -0.17755 | 0
344 | MRSSHPRD | 1 | North | YES | -0.071924 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.17757 | 0 | 0 |  |  | 0 | 0 | -0.17757 | 0
345 | MRSSHPRD01 | 2 | North | YES | -0.071924 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.17757 | 0 | 0 |  |  | 0 | 0 | -0.17757 | 0
728 | WOLFRIDGE801 | 1 | North | YES | -0.072064 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | -1 | 0.17771 | 0 | 112.5 |  |  | 0 | 0 | -0.17771 | 0
923 | SPENCER_G4 | 1 | North | YES | -0.072141 | 48 | 20 | 61 | 0 | 1.03 | GST | -1 | 0.17779 | 61 | 61 |  |  | -4.4006 | 61 | -0.17779 | -10.8451
924 | SPENCER_G5 | 1 | North | YES | -0.072141 | 52 | 20 | 66 | 0 | 1.03 | GST | -1 | 0.17779 | 66 | 66 |  |  | -4.7613 | 66 | -0.17779 | -11.7341
2381 | NTHLK1_G | 1 | North | YES | -0.072188 | 0 | 35 | 156 |  | 1.022 | GST | -1 | 0.17784 | 156 | 156 |  |  | -11.2613 | 156 | -0.17784 | -27.7424
2382 | NTHLK2_G | 2 | North | YES | -0.072188 | 0 | 35 | 181 |  | 1.022 | GST | -1 | 0.17784 | 181 | 181 |  |  | -13.066 | 181 | -0.17784 | -32.1883
2383 | NTHLK3_G | 3 | North | YES | -0.072188 | 0 | 50 | 329 |  | 1.022 | GST | -1 | 0.17784 | 329 | 329 |  |  | -23.7499 | 329 | -0.17784 | -58.5079
580 | JCKCNTY801 | 1 | North | YES | -0.072706 | 288 | 0 | 288 | 0 | 1.022 | CC | -1 | 0.17835 | 288 | 288 |  |  | -20.9393 | 288 | -0.17835 | -51.3659
581 | JCKCNTY802 | 2 | North | YES | -0.072706 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.17835 | 147 | 147 |  |  | -10.6878 | 147 | -0.17835 | -26.218
582 | JCKCNTY803 | 3 | North | YES | -0.072706 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.17835 | 147 | 147 |  |  | -10.6878 | 147 | -0.17835 | -26.218
12322 | ENNSTRAC_1G | 1 | North | YES | -0.073342 | 196 | 130 | 196 | 0 | 1.036 | CC | -1 | 0.17899 | 196 | 196 |  |  | -14.375 | 196 | -0.17899 | -35.082
12323 | ENNSTRAC_2G | 2 | North | YES | -0.073342 | 116 | 100 | 116 | 0 | 1.036 | CC | -1 | 0.17899 | 116 | 116 |  |  | -8.5077 | 116 | -0.17899 | -20.7628
1861 | EAGLEMNT_1G | MB | North | YES | -0.073375 | 0 | 30 | 112 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0
1862 | EAGLEMNT_2G | MB | North | YES | -0.073375 | 0 | 40 | 100 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0
1863 | EAGLEMNT_3G | MB | North | YES | -0.073375 | 0 | 50 | 378 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0
503 | NTHTEXAS01 | 1 | North | YES | -0.07364 | 0 | 5 | 18 |  | 1.015 | GST | -1 | 0.17929 | 18 | 18 |  |  | -1.3255 | 18 | -0.17929 | -3.2272
504 | NTHTEXAS02 | 2 | North | YES | -0.07364 | 14.4 | 5 | 18 |  | 1.015 | GST | -1 | 0.17929 | 18 | 18 |  |  | -1.3255 | 18 | -0.17929 | -3.2272
505 | NTHTEXAS03 | 3 | North | YES | -0.07364 | 30.4 | 15 | 38 |  | 1.015 | GST | -1 | 0.17929 | 38 | 38 |  |  | -2.7983 | 38 | -0.17929 | -6.8129
1643 | SLSTR1PP_1G | 1 | North | YES | -0.073825 | 6 | 0 | 60 | 0 | 1.022 | Wind | -1 | 0.17947 | 0 | 60 |  |  | 0 | 0 | -0.17947 | 0
1898 | COMCHEPK_1G | 1 | North | YES | -0.074064 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | -1 | 0.17971 | 0 | 0 |  |  | 0 | 0 | -0.17971 | 0
1899 | COMCHEPK_2G | 2 | North | YES | -0.074064 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | -1 | 0.17971 | 0 | 0 |  |  | 0 | 0 | -0.17971 | 0
1877 | WLFHOLW_1G | 1 | North | YES | -0.074234 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | -1 | 0.17988 | 217.3 | 217.3 |  |  | -16.131 | 217.3 | -0.17988 | -39.0883
1878 | WLFHOLW_2G | 2 | North | YES | -0.074234 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | -1 | 0.17988 | 215.7 | 215.7 |  |  | -16.0123 | 215.7 | -0.17988 | -38.8005
1879 | WLFHOLW_3G | 3 | North | YES | -0.074234 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | -1 | 0.17988 | 272.4 | 272.4 |  |  | -20.2213 | 272.4 | -0.17988 | -48.9998
332 | RWMILLER01 | 1 | North | YES | -0.074418 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | -1 | 0.18007 | 73 | 73 |  |  | -5.4325 | 73 | -0.18007 | -13.1448
333 | RWMILLER02 | 2 | North | YES | -0.074418 | 95.2 | 37 | 119 | 0 | 1.04 | GST | -1 | 0.18007 | 119 | 119 |  |  | -8.8557 | 119 | -0.18007 | -21.4278
334 | RWMILLER03 | 3 | North | YES | -0.074418 | 166.4 | 65 | 208 | 0 | 1.04 | GST | -1 | 0.18007 | 208 | 208 |  |  | -15.4789 | 208 | -0.18007 | -37.4537
335 | RWMILLER04 | 4 | North | YES | -0.074418 | 81.6 | 0 | 102 | 0 | 1.04 | GST | -1 | 0.18007 | 102 | 102 |  |  | -7.5906 | 102 | -0.18007 | -18.3667
336 | RWMILLER05 | 5 | North | YES | -0.074418 | 80.8 | 0 | 101 | 0 | 1.04 | GST | -1 | 0.18007 | 101 | 101 |  |  | -7.5162 | 101 | -0.18007 | -18.1866
1889 | DECRDOVA_1G | 1 | North | YES | -0.074446 | 779 | 255 | 779 | 0 | 1.02 | GSC | -1 | 0.18009 | 779 | 779 |  |  | -57.9934 | 779 | -0.18009 | -140.293
1948 | HANDLEY_4G | 4 | North | YES | -0.074468 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.18012 | 435 | 435 |  |  | -32.3936 | 435 | -0.18012 | -78.3503
1947 | HANDLEY_3G | 3 | North | YES | -0.07457 | 316 | 100 | 395 | 0 | 1.022 | GST | -1 | 0.18022 | 395 | 395 |  |  | -29.4551 | 395 | -0.18022 | -71.186
1949 | HANDLEY_5G | 5 | North | YES | -0.07457 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.18022 | 435 | 435 |  |  | -32.438 | 435 | -0.18022 | -78.3947
1892 | DECRDOVA_2G | A | North | YES | -0.075535 | 65 | 65 | 70 | 0 | 1.025 | GGT | -1 | 0.18118 | 70 | 70 |  |  | -5.2874 | 70 | -0.18118 | -12.6828
1893 | DECRDOVA_3G | B | North | YES | -0.075535 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.18118 | 69 | 69 |  |  | -5.2119 | 69 | -0.18118 | -12.5016
1894 | DECRDOVA_4G | C | North | YES | -0.075535 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.18118 | 69 | 69 |  |  | -5.2119 | 69 | -0.18118 | -12.5016
1895 | DECRDOVA_5G | D | North | YES | -0.075535 | 65 | 65 | 68 | 0 | 1.025 | GGT | -1 | 0.18118 | 68 | 68 |  |  | -5.1364 | 68 | -0.18118 | -12.3204
1941 | MDLTHELP_1G | 1 | North | YES | -0.077237 | 216.4 | 74 | 216.4 | 0 | 1 | CC | -1 | 0.18288 | 216.4 | 216.4 |  |  | -16.7141 | 216.4 | -0.18288 | -39.5762
1942 | MDLTHELP_2G | 2 | North | YES | -0.077237 | 216.1 | 74 | 216.1 | 0 | 1 | CC | -1 | 0.18288 | 216.1 | 216.1 |  |  | -16.6909 | 216.1 | -0.18288 | -39.5214
1937 | MDLTHELP_5G | 5 | North | YES | -0.077577 | 224 | 74 | 224 | 0 | 1 | CC | -1 | 0.18322 | 224 | 224 |  |  | -17.3772 | 224 | -0.18322 | -41.0423
1938 | MDLTHELP_6G | 6 | North | YES | -0.077577 | 226 | 74 | 226 | 0 | 1 | CC | -1 | 0.18322 | 226 | 226 |  |  | -17.5324 | 226 | -0.18322 | -41.4088
1943 | MDLTHELP_3G | 3 | North | YES | -0.077577 | 212 | 74 | 212 | 0 | 1 | CC | -1 | 0.18322 | 212 | 212 |  |  | -16.4463 | 212 | -0.18322 | -38.8436
1944 | MDLTHELP_4G | 4 | North | YES | -0.077577 | 211 | 74 | 211 | 0 | 1 | CC | -1 | 0.18322 | 211 | 211 |  |  | -16.3687 | 211 | -0.18322 | -38.6604
366 | JNSNCNTY802 | 1 | North | YES | -0.078006 | 168 | 20 | 168 | 0 | 1.02 | Cogen | -1 | 0.18365 | 0 | 0 |  |  | 0 | 0 | -0.18365 | 0
367 | JNSNCNTY802 | 2 | North | YES | -0.078006 | 90 | 20 | 90 | 0 | 1.02 | Cogen | -1 | 0.18365 | 0 | 0 |  |  | 0 | 0 | -0.18365 | 0
244 | WHITNYDM01 | 1 | North | YES | -0.096791 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.20244 | 0 | 0 |  |  | 0 | 0 | -0.20244 | 0
245 | WHITNYDM02 | 2 | North | YES | -0.096791 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.20244 | 0 | 0 |  |  | 0 | 0 | -0.20244 | 0
251 | BOSQUESW803 | 2 | North | YES | -0.10187 | 150 | 0 | 150 | 0 | 1.032 | CC | -1 | 0.20751 | 150 | 150 |  |  | -15.2799 | 150 | -0.20751 | -31.1271
253 | BOSQUESW804 | 2 | North | YES | -0.10187 | 80 | 0 | 80 | 0 | 1.032 | CC | -1 | 0.20751 | 80 | 80 |  |  | -8.1493 | 80 | -0.20751 | -16.6011
238 | BOSQUESW505 | 1 | North | YES | -0.10901 | 255 | 0 | 255 | 0 | 1.02 | CC | -1 | 0.21466 | 255 | 255 |  |  | -27.7983 | 255 | -0.21466 | -54.7385
239 | BOSQUESW502 | 1 | North | YES | -0.10901 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | -1 | 0.21466 | 149 | 149 |  |  | -16.2429 | 149 | -0.21466 | -31.9844
247 | BOSQUESW501 | 2 | North | YES | -0.10901 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | -1 | 0.21466 | 156 | 156 |  |  | -17.006 | 156 | -0.21466 | -33.4871
3416 | LAKE_CRK1_G | 1 | North | YES | -0.11345 | 60 | 33 | 75 |  | 1.029 | GST | -1 | 0.2191 | 75 | 75 |  |  | -8.5087 | 75 | -0.2191 | -16.4323
3417 | LAKE_CRK2_G | 2 | North | YES | -0.11345 | 177.6 | 40 | 222 | 0 | 1.029 | GST | -1 | 0.2191 | 222 | 222 |  |  | -25.1857 | 222 | -0.2191 | -48.6395
3403 | THOUSE_1G | 1 | North | YES | -0.11377 | 563 | 200 | 563 | 0 | 1.012 | GSC | -1 | 0.21941 | 563 | 563 |  |  | -64.0497 | 563 | -0.21941 | -123.5293
3404 | THOUSE_2G | 2 | North | YES | -0.11377 | 807 | 250 | 807 | 0 | 1.012 | GSC | -1 | 0.21941 | 807 | 807 |  |  | -91.8084 | 807 | -0.21941 | -177.066
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ TempleSS to TemplePEC OL_ TempleSS to Sandow |  | i_PTDF_INC_pt | 258 |  | SPENCER_G5 | Unit at max
3403 | THOUSE_1G | 1 | North | YES | -0.11377 | 563 | 200 | 563 | 0 | 1.012 | GSC | -1 | 0.21941 | 563 | 563 |  |  | -64.0497 | 563 | -0.21941 | -123.5293 | 0.022785 | 0.02813 |  |  | i_10pctunit | 14 |  | 54 | # units @ max
3404 | THOUSE_2G | 2 | North | YES | -0.11377 | 807 | 250 | 807 | 0 | 1.012 | GSC | -1 | 0.21941 | 807 | 807 |  |  | -91.8084 | 807 | -0.21941 | -177.066 | 0.055444 | 0.06845 | [5 empty] | 0.02591 | delta max
3416 | LAKE_CRK1_G | 1 | North | YES | -0.11345 | 60 | 33 | 75 |  | 1.029 | GST | -1 | 0.2191 | 75 | 75 |  |  | -8.5087 | 75 | -0.2191 | -16.4323 | 0.05848 | 0.072192 | [5 empty] | Delta
3417 | LAKE_CRK2_G | 2 | North | YES | -0.11345 | 177.6 | 40 | 222 | 0 | 1.029 | GST | -1 | 0.2191 | 222 | 222 |  |  | -25.1857 | 222 | -0.2191 | -48.6395 | 0.067464 | 0.083268 | Weighted Shift Factors |  |  |  | 1 | 0.0053447
238 | BOSQUESW505 | 1 | North | YES | -0.10901 | 255 | 0 | 255 | 0 | 1.02 | CC | -1 | 0.21466 | 255 | 255 |  |  | -27.7983 | 255 | -0.21466 | -54.7385 | 0.077784 | 0.095733 | South | 0.10565 |  |  | 2 | 0.013006
239 | BOSQUESW502 | 1 | North | YES | -0.10901 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | -1 | 0.21466 | 149 | 149 |  |  | -16.2429 | 149 | -0.21466 | -31.9844 | 0.083814 | 0.10302 | North | -0.073157 |  |  | 3 | 0.013712
247 | BOSQUESW501 | 2 | North | YES | -0.10901 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | -1 | 0.21466 | 156 | 156 |  |  | -17.006 | 156 | -0.21466 | -33.4871 | 0.090128 | 0.11064 |  |  |  |  | 4 | 0.015804
251 | BOSQUESW803 | 2 | North | YES | -0.10187 | 150 | 0 | 150 | 0 | 1.032 | CC | -1 | 0.20751 | 150 | 150 |  |  | -15.2799 | 150 | -0.20751 | -31.1271 | 0.096198 | 0.11773 |  |  |  |  | 5 | 0.017949
253 | BOSQUESW804 | 2 | North | YES | -0.10187 | 80 | 0 | 80 | 0 | 1.032 | CC | -1 | 0.20751 | 80 | 80 |  |  | -8.1493 | 80 | -0.20751 | -16.6011 | 0.099436 | 0.12151 |  |  |  |  | 6 | 0.019202
244 | WHITNYDM01 | 1 | North | YES | -0.096791 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.20244 | 0 | 0 |  |  | 0 | 0 | -0.20244 | 0 | 0.099436 | 0.12151 |  |  |  |  | 7 | 0.020514
245 | WHITNYDM02 | 2 | North | YES | -0.096791 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.20244 | 0 | 0 |  |  | 0 | 0 | -0.20244 | 0 | 0.099436 | 0.12151 |  |  |  |  | 8 | 0.021532
366 | JNSNCNTY802 | 1 | North | YES | -0.078006 | 168 | 20 | 168 | 0 | 1.02 | Cogen | -1 | 0.18365 | 0 | 0 |  |  | 0 | 0 | -0.18365 | 0 | 0.099436 | 0.12151 |  |  |  |  | 9 | 0.022074
367 | JNSNCNTY802 | 2 | North | YES | -0.078006 | 90 | 20 | 90 | 0 | 1.02 | Cogen | -1 | 0.18365 | 0 | 0 |  |  | 0 | 0 | -0.18365 | 0 | 0.099436 | 0.12151 |  |  |  |  | 10 | 0.022074
1937 | MDLTHELP_5G | 5 | North | YES | -0.077577 | 224 | 74 | 224 | 0 | 1 | CC | -1 | 0.18322 | 224 | 224 |  |  | -17.3772 | 224 | -0.18322 | -41.0423 | 0.1085 | 0.13086 |  |  |  |  | 11 | 0.022074
1938 | MDLTHELP_6G | 6 | North | YES | -0.077577 | 226 | 74 | 226 | 0 | 1 | CC | -1 | 0.18322 | 226 | 226 |  |  | -17.5324 | 226 | -0.18322 | -41.4088 | 0.11765 | 0.14029 |  |  |  |  | 12 | 0.022074
1943 | MDLTHELP_3G | 3 | North | YES | -0.077577 | 212 | 74 | 212 | 0 | 1 | CC | -1 | 0.18322 | 212 | 212 |  |  | -16.4463 | 212 | -0.18322 | -38.8436 | 0.12623 | 0.14913 |  |  |  |  | 13 | 0.022074
1944 | MDLTHELP_4G | 4 | North | YES | -0.077577 | 211 | 74 | 211 | 0 | 1 | CC | -1 | 0.18322 | 211 | 211 |  |  | -16.3687 | 211 | -0.18322 | -38.6604 | 0.13477 | 0.15793 |  |  |  |  | 14 | 0.022355
1941 | MDLTHELP_1G | 1 | North | YES | -0.077237 | 216.4 | 74 | 216.4 | 0 | 1 | CC | -1 | 0.18288 | 216.4 | 216.4 |  |  | -16.7141 | 216.4 | -0.18288 | -39.5762 | 0.14352 | 0.16695 |  |  |  |  | 15 | 0.022638
1942 | MDLTHELP_2G | 2 | North | YES | -0.077237 | 216.1 | 74 | 216.1 | 0 | 1 | CC | -1 | 0.18288 | 216.1 | 216.1 |  |  | -16.6909 | 216.1 | -0.18288 | -39.5214 | 0.15227 | 0.17595 |  |  |  |  | 16 | 0.022904
1892 | DECRDOVA_2G | A | North | YES | -0.075535 | 65 | 65 | 70 | 0 | 1.025 | GGT | -1 | 0.18118 | 70 | 70 |  |  | -5.2874 | 70 | -0.18118 | -12.6828 | 0.1551 | 0.17883 |  |  |  |  | 17 | 0.023168
1893 | DECRDOVA_3G | B | North | YES | -0.075535 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.18118 | 69 | 69 |  |  | -5.2119 | 69 | -0.18118 | -12.5016 | 0.1579 | 0.18168 |  |  |  |  | 18 | 0.023422
1894 | DECRDOVA_4G | C | North | YES | -0.075535 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.18118 | 69 | 69 |  |  | -5.2119 | 69 | -0.18118 | -12.5016 | 0.16069 | 0.18453 |  |  |  |  | 19 | 0.023676
1895 | DECRDOVA_5G | D | North | YES | -0.075535 | 65 | 65 | 68 | 0 | 1.025 | GGT | -1 | 0.18118 | 68 | 68 |  |  | -5.1364 | 68 | -0.18118 | -12.3204 | 0.16344 | 0.18733 |  |  |  |  | 20 | 0.023731
1947 | HANDLEY_3G | 3 | North | YES | -0.07457 | 316 | 100 | 395 | 0 | 1.022 | GST | -1 | 0.18022 | 395 | 395 |  |  | -29.4551 | 395 | -0.18022 | -71.186 | 0.17943 | 0.20354 |  |  |  |  | 21 | 0.023786
1949 | HANDLEY_5G | 5 | North | YES | -0.07457 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.18022 | 435 | 435 |  |  | -32.438 | 435 | -0.18022 | -78.3947 | 0.19703 | 0.2214 |  |  |  |  | 22 | 0.02384
1948 | HANDLEY_4G | 4 | North | YES | -0.074468 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.18012 | 435 | 435 |  |  | -32.3936 | 435 | -0.18012 | -78.3503 | 0.21463 | 0.23924 |  |  |  |  | 23 | 0.023894
1889 | DECRDOVA_1G | 1 | North | YES | -0.074446 | 779 | 255 | 779 | 0 | 1.02 | GSC | -1 | 0.18009 | 779 | 779 |  |  | -57.9934 | 779 | -0.18009 | -140.293 | 0.24616 | 0.27118 |  |  |  |  | 24 | 0.024118
332 | RWMILLER01 | 1 | North | YES | -0.074418 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | -1 | 0.18007 | 73 | 73 |  |  | -5.4325 | 73 | -0.18007 | -13.1448 | 0.24912 | 0.27418 |  |  |  |  | 25 | 0.024365
333 | RWMILLER02 | 2 | North | YES | -0.074418 | 95.2 | 37 | 119 | 0 | 1.04 | GST | -1 | 0.18007 | 119 | 119 |  |  | -8.8557 | 119 | -0.18007 | -21.4278 | 0.25393 | 0.27906 |  |  |  |  | 26 | 0.024602
334 | RWMILLER03 | 3 | North | YES | -0.074418 | 166.4 | 65 | 208 | 0 | 1.04 | GST | -1 | 0.18007 | 208 | 208 |  |  | -15.4789 | 208 | -0.18007 | -37.4537 | 0.26235 | 0.28759 |  |  |  |  | 27 | 0.025023
335 | RWMILLER04 | 4 | North | YES | -0.074418 | 81.6 | 0 | 102 | 0 | 1.04 | GST | -1 | 0.18007 | 102 | 102 |  |  | -7.5906 | 102 | -0.18007 | -18.3667 | 0.26648 | 0.29177 |  |  |  |  | 28 | 0.025061
336 | RWMILLER05 | 5 | North | YES | -0.074418 | 80.8 | 0 | 101 | 0 | 1.04 | GST | -1 | 0.18007 | 101 | 101 |  |  | -7.5162 | 101 | -0.18007 | -18.1866 | 0.27057 | 0.29591 |  |  |  |  | 29 | 0.025125
1877 | WLFHOLW_1G | 1 | North | YES | -0.074234 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | -1 | 0.17988 | 217.3 | 217.3 |  |  | -16.131 | 217.3 | -0.17988 | -39.0883 | 0.27936 | 0.30481 |  |  |  |  | 30 | 0.025236
1878 | WLFHOLW_2G | 2 | North | YES | -0.074234 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | -1 | 0.17988 | 215.7 | 215.7 |  |  | -16.0123 | 215.7 | -0.17988 | -38.8005 | 0.28809 | 0.31365 |  |  |  |  | 31 | 0.02529
1879 | WLFHOLW_3G | 3 | North | YES | -0.074234 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | -1 | 0.17988 | 272.4 | 272.4 |  |  | -20.2213 | 272.4 | -0.17988 | -48.9998 | 0.29911 | 0.3248 |  |  |  |  | 32 | 0.025344
1898 | COMCHEPK_1G | 1 | North | YES | -0.074064 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | -1 | 0.17971 | 0 | 0 |  |  | 0 | 0 | -0.17971 | 0 | 0.29911 | 0.3248 |  |  |  |  | 33 | 0.025451
1899 | COMCHEPK_2G | 2 | North | YES | -0.074064 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | -1 | 0.17971 | 0 | 0 |  |  | 0 | 0 | -0.17971 | 0 | 0.29911 | 0.3248 |  |  |  |  | 34 | 0.025557
1643 | SLSTR1PP_1G | 1 | North | YES | -0.073825 | 6 | 0 | 60 | 0 | 1.022 | Wind | -1 | 0.17947 | 0 | 60 |  |  | 0 | 0 | -0.17947 | 0 | 0.29911 | 0.3248 |  |  |  |  | 35 | 0.025691
503 | NTHTEXAS01 | 1 | North | YES | -0.07364 | 0 | 5 | 18 |  | 1.015 | GST | -1 | 0.17929 | 18 | 18 |  |  | -1.3255 | 18 | -0.17929 | -3.2272 | 0.29984 | 0.32554 |  |  |  |  | 36 | 0.025691
504 | NTHTEXAS02 | 2 | North | YES | -0.07364 | 14.4 | 5 | 18 |  | 1.015 | GST | -1 | 0.17929 | 18 | 18 |  |  | -1.3255 | 18 | -0.17929 | -3.2272 | 0.30057 | 0.32627 |  |  |  |  | 37 | 0.025691
505 | NTHTEXAS03 | 3 | North | YES | -0.07364 | 30.4 | 15 | 38 |  | 1.015 | GST | -1 | 0.17929 | 38 | 38 |  |  | -2.7983 | 38 | -0.17929 | -6.8129 | 0.30211 | 0.32782 |  |  |  |  | 38 | 0.025691
1861 | EAGLEMNT_1G | MB | North | YES | -0.073375 | 0 | 30 | 112 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0 | 0.30211 | 0.32782 |  |  |  |  | 39 | 0.025697
1862 | EAGLEMNT_2G | MB | North | YES | -0.073375 | 0 | 40 | 100 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0 | 0.30211 | 0.32782 |  |  |  |  | 40 | 0.025704
1863 | EAGLEMNT_3G | MB | North | YES | -0.073375 | 0 | 50 | 378 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0 | 0.30211 | 0.32782 |  |  |  |  | 41 | 0.025717
12322 | ENNSTRAC_1G | 1 | North | YES | -0.073342 | 196 | 130 | 196 | 0 | 1.036 | CC | -1 | 0.17899 | 196 | 196 |  |  | -14.375 | 196 | -0.17899 | -35.082 | 0.31004 | 0.33581 |  |  |  |  | 42 | 0.025717
12323 | ENNSTRAC_2G | 2 | North | YES | -0.073342 | 116 | 100 | 116 | 0 | 1.036 | CC | -1 | 0.17899 | 116 | 116 |  |  | -8.5077 | 116 | -0.17899 | -20.7628 | 0.31473 | 0.34054 |  |  |  |  | 43 | 0.025717
580 | JCKCNTY801 | 1 | North | YES | -0.072706 | 288 | 0 | 288 | 0 | 1.022 | CC | -1 | 0.17835 | 288 | 288 |  |  | -20.9393 | 288 | -0.17835 | -51.3659 | 0.32639 | 0.35224 |  |  |  |  | 44 | 0.025717
581 | JCKCNTY802 | 2 | North | YES | -0.072706 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.17835 | 147 | 147 |  |  | -10.6878 | 147 | -0.17835 | -26.218 | 0.33234 | 0.35821 |  |  |  |  | 45 | 0.025774
582 | JCKCNTY803 | 3 | North | YES | -0.072706 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.17835 | 147 | 147 |  |  | -10.6878 | 147 | -0.17835 | -26.218 | 0.33829 | 0.36418 |  |  |  |  | 46 | 0.025807
2381 | NTHLK1_G | 1 | North | YES | -0.072188 | 0 | 35 | 156 |  | 1.022 | GST | -1 | 0.17784 | 156 | 156 |  |  | -11.2613 | 156 | -0.17784 | -27.7424 | 0.3446 | 0.3705 |  |  |  |  | 47 | 0.025848
2382 | NTHLK2_G | 2 | North | YES | -0.072188 | 0 | 35 | 181 |  | 1.022 | GST | -1 | 0.17784 | 181 | 181 |  |  | -13.066 | 181 | -0.17784 | -32.1883 | 0.35193 | 0.37783 |  |  |  |  | 48 | 0.02587
2383 | NTHLK3_G | 3 | North | YES | -0.072188 | 0 | 50 | 329 |  | 1.022 | GST | -1 | 0.17784 | 329 | 329 |  |  | -23.7499 | 329 | -0.17784 | -58.5079 | 0.36524 | 0.39115 |  |  |  |  | 49 | 0.025891
923 | SPENCER_G4 | 1 | North | YES | -0.072141 | 48 | 20 | 61 | 0 | 1.03 | GST | -1 | 0.17779 | 61 | 61 |  |  | -4.4006 | 61 | -0.17779 | -10.8451 | 0.36771 | 0.39362 |  |  |  |  | 50 | 0.025895
924 | SPENCER_G5 | 1 | North | YES | -0.072141 | 52 | 20 | 66 | 0 | 1.03 | GST | -1 | 0.17779 | 66 | 66 |  |  | -4.7613 | 66 | -0.17779 | -11.7341 | 0.37038 | 0.39629 |  |  |  |  | 51 | 0.025899
728 | WOLFRIDGE801 | 1 | North | YES | -0.072064 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | -1 | 0.17771 | 0 | 112.5 |  |  | 0 | 0 | -0.17771 | 0 | 0.37038 | 0.39629 |  |  |  |  | 52 | 0.025908
344 | MRSSHPRD | 1 | North | YES | -0.071924 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.17757 | 0 | 0 |  |  | 0 | 0 | -0.17757 | 0 | 0.37038 | 0.39629 |  |  |  |  | 53 | 0.025909
345 | MRSSHPRD01 | 2 | North | YES | -0.071924 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.17757 | 0 | 0 |  |  | 0 | 0 | -0.17757 | 0 | 0.37038 | 0.39629 |  |  |  |  | 54 | 0.02591
1600 | BARTNWND_1G | 1 | North | YES | -0.071906 | 12 | 0 | 120 | 0 | 1.022 | Wind | -1 | 0.17755 | 0 | 120 |  |  | 0 | 0 | -0.17755 | 0 | 0.37038 | 0.39629 |  |  |  |  | 55 | 0.02591
2413 | MTCK6_G | 6 | North | YES | -0.071897 | 0 | 30 | 118 |  | 1.022 | GST | -1 | 0.17754 | 118 | 118 |  |  | -8.4838 | 118 | -0.17754 | -20.9503 | 0.37516 | 0.40106 |  |  |  |  | 56 | 0.02591
2414 | MTCK7_G | 7 | North | YES | -0.071897 | 0 | 30 | 115 |  | 1.022 | GST | -1 | 0.17754 | 115 | 115 |  |  | -8.2682 | 115 | -0.17754 | -20.4176 | 0.37981 | 0.40571 |  |  |  |  | 57 | 0.02591
2417 | MTCK8_G | 8 | North | YES | -0.071897 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | -1 | 0.17754 | 556 | 556 |  |  | -39.9747 | 556 | -0.17754 | -98.7149 | 0.40231 | 0.42819 |  |  |  |  | 58 | 0.02591
1453 | WCPWRCO_1G | 1 | North | YES | -0.071787 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.17743 | 204 | 204 |  |  | -14.6445 | 204 | -0.17743 | -36.1967 | 0.41057 | 0.43643 |  |  |  |  | 59 | 0.025905
1454 | WCPWRCO_2G | 2 | North | YES | -0.071787 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.17743 | 204 | 204 |  |  | -14.6445 | 204 | -0.17743 | -36.1967 | 0.41882 | 0.44467 |  |  |  |  | 60 | 0.0259
1455 | WCPWRCO_3G | 3 | North | YES | -0.071787 | 242 | 50 | 242 |  | 1.02 | CC | -1 | 0.17743 | 242 | 242 |  |  | -17.3725 | 242 | -0.17743 | -42.9392 | 0.42862 | 0.45445 |  |  |  |  | 61 | 0.025877
2371 | COLLIN_1G | MB | North | YES | -0.071683 | 0 | 40 | 138 |  | 1.022 | GST | -1 | 0.17733 | 0 | 0 |  |  | 0 | 0 | -0.17733 | 0 | 0.42862 | 0.45445 |  |  |  |  | 62 | 0.025864
6948 | DENISNDM | 1 | North | YES | -0.071253 | 40 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.1769 | 0 | 0 |  |  | 0 | 0 | -0.1769 | 0 | 0.42862 | 0.45445 |  |  |  |  | 63 | 0.025851
6948 | DENISNDM | 2 | North | YES | -0.071253 | 31 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.1769 | 0 | 0 |  |  | 0 | 0 | -0.1769 | 0 | 0.42862 | 0.45445 |  |  |  |  | 64 | 0.025835
1687 | VALLEY_1G | 1 | North | YES | -0.071166 | 136 | 15 | 170 | 0 | 1.029 | GST | -1 | 0.17681 | 170 | 170 |  |  | -12.0982 | 170 | -0.17681 | -30.0583 | 0.4355 | 0.4613 |  |  |  |  | 65 | 0.025835
1688 | VALLEY_2G | 2 | North | YES | -0.071166 | 527 | 90 | 527 | 0 | 1.029 | GSC | -1 | 0.17681 | 527 | 527 |  |  | -37.5045 | 527 | -0.17681 | -93.1808 | 0.45683 | 0.48252 |  |  |  |  | 66 | 0.025835
1689 | VALLEY_3G | 3 | North | YES | -0.07107 | 0 | 25 | 375 |  | 1.003 | GST | -1 | 0.17672 | 375 | 375 |  |  | -26.6513 | 375 | -0.17672 | -66.2691 | 0.472 | 0.49761 |  |  |  |  | 67 | 0.025835
11691 | KMICHICT1_G | 1 | North | YES | -0.07107 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.17672 | 144 | 144 |  |  | -10.2341 | 144 | -0.17672 | -25.4473 | 0.47783 | 0.5034 |  |  |  |  | 68 | 0.025799
11692 | KMICHICT2_G | 2 | North | YES | -0.07107 | 146 | 80 | 146 | 0 | 1.026 | CC | -1 | 0.17672 | 146 | 146 |  |  | -10.3762 | 146 | -0.17672 | -25.8008 | 0.48374 | 0.50928 |  |  |  |  | 69 | 0.02569
11693 | KMICHIST3_G | 3 | North | YES | -0.07107 | 312 | 60 | 312 | 0 | 1.026 | CC | -1 | 0.17672 | 312 | 312 |  |  | -22.1738 | 312 | -0.17672 | -55.1359 | 0.49637 | 0.52183 |  |  |  |  | 70 | 0.025604
11694 | KMICHICT4_G | 4 | North | YES | -0.07107 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.17672 | 144 | 144 |  |  | -10.2341 | 144 | -0.17672 | -25.4473 | 0.50219 | 0.52763 |  |  |  |  | 71 | 0.025571
11695 | KMICHICT5_G | 5 | North | YES | -0.07107 | 148 | 80 | 148 | 0 | 1.026 | CC | -1 | 0.17672 | 148 | 148 |  |  | -10.5184 | 148 | -0.17672 | -26.1542 | 0.50818 | 0.53358 |  |  |  |  | 72 | 0.025538
11696 | KMICHIST6_G | 6 | North | YES | -0.07107 | 310 | 60 | 310 | 0 | 1.026 | CC | -1 | 0.17672 | 310 | 310 |  |  | -22.0317 | 310 | -0.17672 | -54.7825 | 0.52073 | 0.54606 |  |  |  |  | 73 | 0.025466
1678 | LAMARPWR_1G | 1 | North | YES | -0.071002 | 160 | 67.7 | 160 | 0 | 1.038 | CC | -1 | 0.17665 | 160 | 160 |  |  | -11.3603 | 160 | -0.17665 | -28.264 | 0.5272 | 0.55249 |  |  |  |  | 74 | 0.025433
1679 | LAMARPWR_2G | 2 | North | YES | -0.071002 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.17665 | 156 | 156 |  |  | -11.0763 | 156 | -0.17665 | -27.5574 | 0.53352 | 0.55877 |  |  |  |  | 75 | 0.0254
1680 | LAMARPWR_3G | 3 | North | YES | -0.071002 | 196 | 129.1 | 196 | 0 | 1.038 | CC | -1 | 0.17665 | 196 | 196 |  |  | -13.9164 | 196 | -0.17665 | -34.6233 | 0.54145 | 0.56665 |  |  |  |  | 76 | 0.025329
1681 | LAMARPWR_4G | 4 | North | YES | -0.071002 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.17665 | 156 | 156 |  |  | -11.0763 | 156 | -0.17665 | -27.5574 | 0.54776 | 0.57293 |  |  |  |  | 77 | 0.025289
1682 | LAMARPWR_5G | 5 | North | YES | -0.071002 | 157 | 67.7 | 157 | 0 | 1.038 | CC | -1 | 0.17665 | 157 | 157 |  |  | -11.1473 | 157 | -0.17665 | -27.734 | 0.55412 | 0.57924 |  |  |  |  | 78 | 0.025251
1683 | LAMARPWR_6G | 6 | North | YES | -0.071002 | 198 | 129.1 | 198 | 0 | 1.038 | CC | -1 | 0.17665 | 198 | 198 |  |  | -14.0584 | 198 | -0.17665 | -34.9766 | 0.56213 | 0.58721 |  |  |  |  | 79 | 0.025203
1675 | PEC_1G | 1 | North | YES | -0.070943 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0 | 0.56213 | 0.58721 |  |  |  |  | 80 | 0.025165
1676 | PEC_2G | 2 | North | YES | -0.070943 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0 | 0.56213 | 0.58721 |  |  |  |  | 81 | 0.025127
1677 | PEC_3G | 3 | North | YES | -0.070943 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0 | 0.56213 | 0.58721 |  |  |  |  | 82 | 0.025078
1701 | MOSES_1G | 1 | North | YES | -0.070891 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 558 |  |  | 0 | 0 | -0.17654 | 0 | 0.56213 | 0.58721 |  |  |  |  | 83 | 0.025078
1702 | MOSES_2G | 2 | North | YES | -0.070891 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 579 |  |  | 0 | 0 | -0.17654 | 0 | 0.56213 | 0.58721 |  |  |  |  | 84 | 0.025078
1703 | MOSES_3G | 3 | North | YES | -0.070891 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 808 |  |  | 0 | 0 | -0.17654 | 0 | 0.56213 | 0.58721 |  |  |  |  | 85 | 0.025078
5925 | DCEAST | EQ | North | YES | -0.070891 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | -1 | 0.17654 | 0 | 0 |  |  | 0 | 0 | -0.17654 | 0 | 0.56213 | 0.58721 |  |  |  |  | 86 | 0.025078
837 | NEWMAN_G5 | 1 | North | YES | -0.070826 | 0 | 15 | 40 |  | 1.01 | GST | -1 | 0.17647 | 40 | 40 |  |  | -2.833 | 40 | -0.17647 | -7.0589 | 0.56375 | 0.58882 |  |  |  |  | 87 | 0.025078
842 | OLINGER_G1 | 1 | North | YES | -0.070819 | 55.4 | 20 | 79 | 0 | 1.03 | GST | -1 | 0.17647 | 79 | 79 |  |  | -5.5947 | 79 | -0.17647 | -13.9409 | 0.56695 | 0.59199 |  |  |  |  | 88 | 0.025078
843 | OLINGER_G2 | 1 | North | YES | -0.070819 | 76.2 | 25 | 110 | 0 | 1.03 | GST | -1 | 0.17647 | 110 | 110 |  |  | -7.7901 | 110 | -0.17647 | -19.4113 | 0.5714 | 0.59641 |  |  |  |  | 89 | 0.025078
844 | OLINGER_G3 | 1 | North | YES | -0.070819 | 103.9 | 45 | 150 | 0 | 1.03 | GST | -1 | 0.17647 | 150 | 150 |  |  | -10.6228 | 150 | -0.17647 | -26.47 | 0.57747 | 0.60244 |  |  |  |  | 90 | 0.025067
845 | OLINGER_G4 | 1 | North | YES | -0.070819 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | -1 | 0.17647 | 76 | 76 |  |  | -5.3822 | 76 | -0.17647 | -13.4115 | 0.58054 | 0.60549 |  |  |  |  | 91 | 0.025044
948 | STEAM1 | 1 | North | YES | -0.070707 | 0 | 12 | 20 |  | 1.02 | GST | -1 | 0.17635 | 20 | 20 |  |  | -1.4141 | 20 | -0.17635 | -3.5271 | 0.58135 | 0.6063 |  |  |  |  | 92 | 0.025013
949 | STEAM2 | 1 | North | YES | -0.070707 | 26 | 8 | 26 | 0 | 0.99 | GST | -1 | 0.17635 | 26 | 26 |  |  | -1.8384 | 26 | -0.17635 | -4.5852 | 0.58241 | 0.60734 |  |  |  |  | 93 | 0.02497
950 | STEAM3 | 1 | North | YES | -0.070707 | 41 | 13 | 42 | 0 | 1.02 | GST | -1 | 0.17635 | 42 | 42 |  |  | -2.9697 | 42 | -0.17635 | -7.4069 | 0.58411 | 0.60903 |  |  |  |  | 94 | 0.024948
12440 | PARKD_1SVC8 | 1 | North | YES | -0.070682 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.17633 | 0 | 0 |  |  | 0 | 0 | -0.17633 | 0 | 0.58411 | 0.60903 |  |  |  |  | 95 | 0.024942
12449 | PARKD_2SVC8 | 1 | North | YES | -0.070682 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.17633 | 0 | 0 |  |  | 0 | 0 | -0.17633 | 0 | 0.58411 | 0.60903 |  |  |  |  | 96 | 0.024934
2451 | LKHB1_G | 1 | North | YES | -0.070564 | 0 | 80 | 391 |  | 1.022 | GST | -1 | 0.17621 | 391 | 391 |  |  | -27.5905 | 391 | -0.17621 | -68.8988 | 0.59993 | 0.62472 |  |  |  |  | 97 | 0.024921
2452 | LKHB2_G | 2 | North | YES | -0.070564 | 516 | 80 | 516 | 0 | 1.022 | GST | -1 | 0.17621 | 516 | 516 |  |  | -36.411 | 516 | -0.17621 | -90.9252 | 0.62081 | 0.64542 |  |  |  |  | 98 | 0.024921
3126 | TRINIDAD_6G | 1 | North | YES | -0.070556 | 179.2 | 46 | 224 | 0 | 1 | GST | -1 | 0.1762 | 224 | 224 |  |  | -15.8045 | 224 | -0.1762 | -39.4696 | 0.62988 | 0.65441 |  |  |  |  | 99 | 0.024921
1433 | GRHAMSES_1G | 1 | North | YES | -0.070142 | 242 | 60 | 242 | 0 | 1.038 | GST | -1 | 0.17579 | 242 | 242 |  |  | -16.9744 | 242 | -0.17579 | -42.5411 | 0.63967 | 0.6641 |  |  |  |  | 100 | 0.024786
1479 | WFCOGEN_1G | 1 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0 | 0.63967 | 0.6641 |  |  |  |  | 101 | 0.024609
1479 | WFCOGEN_1G | 2 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0 | 0.63967 | 0.6641 |  |  |  |  | 102 | 0.024531
1482 | WFCOGEN_2G | 2 | North | YES | -0.070041 | 13.6 | 12 | 17 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0 | 0.63967 | 0.6641 |  |  |  |  | 103 | 0.024424
1482 | WFCOGEN_2G | 1 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0 | 0.63967 | 0.6641 |  |  |  |  | 104 | 0.024424
12411 | FPLEFR1A_G | 1 | North | YES | -0.070029 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.17568 | 161 | 161 |  |  | -11.2747 | 161 | -0.17568 | -28.2839 | 0.64619 | 0.67054 |  |  |  |  | 105 | 0.024424
12412 | FPLEFR1B_G | 2 | North | YES | -0.070029 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.17568 | 164 | 164 |  |  | -11.4848 | 164 | -0.17568 | -28.811 | 0.65282 | 0.6771 |  |  |  |  | 106 | 0.024424
12413 | FPLEFR1C_G | 3 | North | YES | -0.070029 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.17568 | 164 | 164 |  |  | -11.4848 | 164 | -0.17568 | -28.811 | 0.65946 | 0.68366 |  |  |  |  | 107 | 0.024424
12414 | FPLEFR1S_G | 4 | North | YES | -0.070029 | 414 | 191 | 414 | 0 | 1 | CC | -1 | 0.17568 | 414 | 414 |  |  | -28.992 | 414 | -0.17568 | -72.7302 | 0.67622 | 0.70022 |  |  |  |  | 108 | 0.024349
12421 | FPLEFR2A_G | 1 | North | YES | -0.070029 | 162 | 72 | 162 | 0 | 1 | CC | -1 | 0.17568 | 162 | 162 |  |  | -11.3447 | 162 | -0.17568 | -28.4596 | 0.68277 | 0.7067 |  |  |  |  | 109 | 0.024273
12422 | FPLEFR2B_G | 2 | North | YES | -0.070029 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.17568 | 161 | 161 |  |  | -11.2747 | 161 | -0.17568 | -28.2839 | 0.68929 | 0.71314 |  |  |  |  | 110 | 0.024197
12423 | FPLEFR2C_G | 3 | North | YES | -0.070029 | 163 | 72 | 163 | 0 | 1 | CC | -1 | 0.17568 | 163 | 163 |  |  | -11.4147 | 163 | -0.17568 | -28.6353 | 0.69588 | 0.71966 |  |  |  |  | 111 | 0.024004
12424 | FPLEFR2S_G | 4 | North | YES | -0.070029 | 415 | 191 | 415 | 0 | 1 | CC | -1 | 0.17568 | 415 | 415 |  |  | -29.062 | 415 | -0.17568 | -72.9058 | 0.71268 | 0.73626 |  |  |  |  | 112 | 0.023928
1432 | GRHAMSES_2G | 2 | North | YES | -0.069944 | 294.9 | 90 | 366 | 0 | 1.014 | GST | -1 | 0.17559 | 366 | 366 |  |  | -25.5995 | 366 | -0.17559 | -64.2666 | 0.72749 | 0.7509 |  |  |  |  | 113 | 0.023853
6100 | OKLA7A | EQ | West | YES | -0.068286 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.17393 | 0 | 0 |  |  |  |  | -0.17393 | 0 | 0.72749 | 0.7509 |  |  |  |  | 114 | 0.023777
6752 | OKLA0A | 1 | West | YES | -0.068286 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.17393 | 0 | 649.7 |  |  |  |  | -0.17393 | 0 | 0.72749 | 0.7509 |  |  |  |  | 115 | 0.023584
1442 | COKFIELD_5 | 1 | North | YES | -0.067751 | 16.5 | 0 | 165 |  | 1.029 | Wind | -1 | 0.1734 | 0 | 165 |  |  | 0 | 0 | -0.1734 | 0 | 0.72749 | 0.7509 |  |  |  |  | 116 | 0.023406
3097 | MARTLAKE_1G | 1 | North | YES | -0.067389 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 790 |  |  | 0 | 0 | -0.17304 | 0 | 0.72749 | 0.7509 |  |  |  |  | 117 | 0.023406
3098 | MARTLAKE_2G | 2 | North | YES | -0.067389 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 795 |  |  | 0 | 0 | -0.17304 | 0 | 0.72749 | 0.7509 |  |  |  |  | 118 | 0.023406
3099 | MARTLAKE_3G | 3 | North | YES | -0.067389 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 804 |  |  | 0 | 0 | -0.17304 | 0 | 0.72749 | 0.7509 |  |  |  |  | 119 | 0.023406
1438 | MESQUITW_2G | 1 | North | YES | -0.067058 | 23.6 | 0 | 236 |  | 1.017 | Wind | -1 | 0.17271 | 0 | 236 |  |  | 0 | 0 | -0.17271 | 0 | 0.72749 | 0.7509 |  |  |  |  | 120 | 0.023406
1437 | MESQUITW_1G | 1 | North | YES | -0.067055 | 40 | 0 | 400 | 0 | 1.023 | Wind | -1 | 0.1727 | 0 | 400 |  |  | 0 | 0 | -0.1727 | 0 | 0.72749 | 0.7509 |  |  |  |  | 121 | 0.023406
13116 | TGATEWAY_1G | 1 | North | YES | -0.067045 | 151 | 30 | 151 | 0 | 1.0232 | CC | -1 | 0.17269 | 151 | 151 |  |  | -10.1238 | 151 | -0.17269 | -26.0766 | 0.7336 | 0.75684 |  |  |  |  | 122 | 0.023406
13117 | TGATEWAY_2G | 2 | North | YES | -0.067045 | 130 | 30 | 130 | 0 | 1.0232 | CC | -1 | 0.17269 | 130 | 130 |  |  | -8.7158 | 130 | -0.17269 | -22.4501 | 0.73886 | 0.76195 |  |  |  |  | 123 | 0.023406
13118 | TGATEWAY_3G | 3 | North | YES | -0.067045 | 148 | 30 | 148 | 0 | 1.0232 | CC | -1 | 0.17269 | 148 | 148 |  |  | -9.9227 | 148 | -0.17269 | -25.5585 | 0.74485 | 0.76777 |  |  |  |  | 124 | 0.023406
13119 | TGATEWAY_4G | 4 | North | YES | -0.067045 | 399 | 65 | 399 | 0 | 1.0232 | CC | -1 | 0.17269 | 399 | 399 |  |  | -26.751 | 399 | -0.17269 | -68.9044 | 0.761 | 0.78346 |  |  |  |  | 125 | 0.023233
3348 | CHAMPION_1G | MB | North | YES | -0.066625 | 0 | 42 | 42 |  | 1 | Cogen | -1 | 0.17227 | 0 | 0 |  |  | 0 | 0 | -0.17227 | 0 | 0.761 | 0.78346 |  |  |  |  | 126 | 0.023084
3309 | ASPN_G | 1 | North | YES | -0.066592 | 50 | 0 | 50 |  | 1 | Bio | -1 | 0.17224 | 50 | 50 |  |  | -3.3296 | 50 | -0.17224 | -8.612 | 0.76303 | 0.78542 |  |  |  |  | 127 | 0.022914
3107 | STRYKER_1G | 1 | North | YES | -0.066332 | 145.6 | 45 | 182 | 0 | 1.029 | GST | -1 | 0.17198 | 182 | 182 |  |  | -12.0724 | 182 | -0.17198 | -31.3003 | 0.77039 | 0.79255 |  |  |  |  | 128 | 0.022457
3108 | STRYKER_2G | 2 | North | YES | -0.066332 | 484 | 75 | 484 | 0 | 1.029 | GST | -1 | 0.17198 | 484 | 484 |  |  | -32.1047 | 484 | -0.17198 | -83.2382 | 0.78998 | 0.8115 |  |  |  |  | 129 | 0.022457
60081 | WHRLWIND1A | 1 | West | YES | -0.066019 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.17167 | 0 | 60 |  |  |  |  | -0.17167 | 0 | 0.78998 | 0.8115 |  |  |  |  | 130 | 0.022395
1416 | SWETWATR_1G | 1 | West | YES | -0.065247 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.17089 | 30 | 30 |  |  |  |  | -0.17089 | -5.1268 | 0.79119 | 0.81267 |  |  |  |  | 131 | 0.022157
1417 | SWETWATR_2G | 2 | West | YES | -0.065247 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.17089 | 72 | 72 |  |  |  |  | -0.17089 | -12.3044 | 0.79411 | 0.81547 |  |  |  |  | 132 | 0.021524
1418 | SWETWATR_3G | 3 | West | YES | -0.065247 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.17089 | 68 | 68 |  |  |  |  | -0.17089 | -11.6208 | 0.79686 | 0.81812 |  |  |  |  | 133 | 0.021524
1419 | SWETWATR_4G | 4 | West | YES | -0.065247 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.17089 | 61 | 61 |  |  |  |  | -0.17089 | -10.4246 | 0.79933 | 0.82049 |  |  |  |  | 134 | 0.021477
6407 | TURKTRAK1A | 1 | West | YES | -0.065221 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.17087 | 0 | 169.5 |  |  |  |  | -0.17087 | 0 | 0.79933 | 0.82049 |  |  |  |  | 135 | 0.021365
6144 | MCADOO1A | 1 | West | YES | -0.065112 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.17076 | 0 | 150 |  |  |  |  | -0.17076 | 0 | 0.79933 | 0.82049 |  |  |  |  | 136 | 0.021259
71051 | L_BITTCR1_1N | W1 | West | YES | -0.064849 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 37.5 |  |  |  |  | -0.1705 | 0 | 0.79933 | 0.82049 |  |  |  |  | 137 | 0.021165
71054 | L_SWEETW1_1N | W1 | West | YES | -0.064849 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 107.5 |  |  |  |  | -0.1705 | 0 | 0.79933 | 0.82049 |  |  |  |  | 138 | 0.021165
71057 | L_SWEETW1_2N | W1 | West | YES | -0.064849 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 135 |  |  |  |  | -0.1705 | 0 | 0.79933 | 0.82049 |  |  |  |  | 139 | 0.021165
71059 | L_SWEETW1_3N | W1 | West | YES | -0.064849 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 119 |  |  |  |  | -0.1705 | 0 | 0.79933 | 0.82049 |  |  |  |  | 140 | 0.021165
71060 | L_SWEETW1_4N | W1 | West | YES | -0.064849 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 105 |  |  |  |  | -0.1705 | 0 | 0.79933 | 0.82049 |  |  |  |  | 141 | 0.021165
71061 | L_SWEETW1_5N | W1 | West | YES | -0.064849 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 80.5 |  |  |  |  | -0.1705 | 0 | 0.79933 | 0.82049 |  |  |  |  | 142 | 0.021165
11056 | ROSCOE_1G | 1 | West | YES | -0.064846 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.17049 | 0 | 209 |  |  |  |  | -0.17049 | 0 | 0.79933 | 0.82049 |  |  |  |  | 143 | 0.021165
11057 | CHAMPION_1G | 1 | West | YES | -0.064846 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.17049 | 0 | 126.5 |  |  |  |  | -0.17049 | 0 | 0.79933 | 0.82049 |  |  |  |  | 144 | 0.021165
11058 | PYRON_1G | 1 | West | YES | -0.064846 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.17049 | 0 | 249 |  |  |  |  | -0.17049 | 0 | 0.79933 | 0.82049 |  |  |  |  | 145 | 0.021165
11059 | INADALE_1G | 1 | West | YES | -0.064846 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.17049 | 0 | 197 |  |  |  |  | -0.17049 | 0 | 0.79933 | 0.82049 |  |  |  |  | 146 | 0.021165
1343 | TRENTIPP_8 | 1 | West | YES | -0.064746 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.17039 | 0 | 150 |  |  |  |  | -0.17039 | 0 | 0.79933 | 0.82049 |  |  |  |  | 147 | 0.021165
1354 | AEPWIND_8 | 1 | West | YES | -0.064746 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.17039 | 0 | 101 |  |  |  |  | -0.17039 | 0 | 0.79933 | 0.82049 |  |  |  |  | 148 | 0.021165
36998 | RDCNYNG1 | 1 | West | YES | -0.064322 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.16997 | 0 | 84 |  |  |  |  | -0.16997 | 0 | 0.79933 | 0.82049 |  |  |  |  | 149 | 0.021165
1061 | CIELOGEN_1G | 1 | West | YES | -0.064142 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.16979 | 0 | 99 |  |  |  |  | -0.16979 | 0 | 0.79933 | 0.82049 |  |  |  |  | 150 | 0.021165
1062 | CIELOGEN_2G | 1 | West | YES | -0.064142 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.16979 | 0 | 61 |  |  |  |  | -0.16979 | 0 | 0.79933 | 0.82049 |  |  |  |  | 151 | 0.021165
1069 | KINDERMG_1G | 1 | West | YES | -0.064142 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0 | 0.79933 | 0.82049 |  |  |  |  | 152 | 0.021165
1070 | KINDERMG_2G | 1 | West | YES | -0.064142 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0 | 0.79933 | 0.82049 |  |  |  |  | 153 | 0.021165
1071 | KINDERMG_3G | 1 | West | YES | -0.064142 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0 | 0.79933 | 0.82049 |  |  |  |  | 154 | 0.021165
1068 | SCURRYCW_1G | 1 | West | YES | -0.064132 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.16978 | 0 | 141 |  |  |  |  | -0.16978 | 0 | 0.79933 | 0.82049 |  |  |  |  | 155 | 0.021165
1073 | SCURRYCW_2G | 2 | West | YES | -0.064132 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.16978 | 0 | 120 |  |  |  |  | -0.16978 | 0 | 0.79933 | 0.82049 |  |  |  |  | 156 | 0.021165
6637 | SNYDERW1A | 1 | West | YES | -0.064071 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.16972 | 0 | 63 |  |  |  |  | -0.16972 | 0 | 0.79933 | 0.82049 |  |  |  |  | 157 | 0.021165
1037 | MORGAN5G_5G | 5 | West | YES | -0.063995 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.16964 | 137 | 137 |  |  |  |  | -0.16964 | -23.241 | 0.80487 | 0.82578 |  |  |  |  | 158 | 0.021165
1039 | MRGNAG_1G | A | West | YES | -0.063995 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.16964 | 69 | 69 |  |  |  |  | -0.16964 | -11.7053 | 0.80766 | 0.82845 |  |  |  |  | 159 | 0.021165
1040 | MRGNBG_2G | B | West | YES | -0.063995 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.16964 | 71 | 71 |  |  |  |  | -0.16964 | -12.0446 | 0.81054 | 0.83119 |  |  |  |  | 160 | 0.021165
1041 | MRGNCG_3G | C | West | YES | -0.063995 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.16964 | 70 | 70 |  |  |  |  | -0.16964 | -11.875 | 0.81337 | 0.8339 |  |  |  |  | 161 | 0.020913
1042 | MRGNDG_4G | D | West | YES | -0.063995 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.16964 | 68 | 68 |  |  |  |  | -0.16964 | -11.5357 | 0.81612 | 0.83652 |  |  |  |  | 162 | 0.020786
1043 | MRGNEG_5G | E | West | YES | -0.063995 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.16964 | 70 | 70 |  |  |  |  | -0.16964 | -11.875 | 0.81896 | 0.83923 |  |  |  |  | 163 | 0.020655
1044 | MRGNFG_6G | F | West | YES | -0.063995 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.16964 | 66 | 66 |  |  |  |  | -0.16964 | -11.1964 | 0.82163 | 0.84178 |  |  |  |  | 164 | 0.020526
60058 | BUFF_GAP1A | 1 | West | YES | -0.063992 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.16964 | 0 | 120 |  |  |  |  | -0.16964 | 0 | 0.82163 | 0.84178 |  |  |  |  | 165 | 0.020401
60060 | CIRELLO | 1 | West | YES | -0.063992 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.16964 | 0 | 233 |  |  |  |  | -0.16964 | 0 | 0.82163 | 0.84178 |  |  |  |  | 166 | 0.020272
60063 | BUFF_GAP1B | 1 | West | YES | -0.063992 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.16964 | 0 | 170.2 |  |  |  |  | -0.16964 | 0 | 0.82163 | 0.84178 |  |  |  |  | 167 | 0.020151
60066 | H_HOLLOW1A | 1 | West | YES | -0.063992 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.16964 | 0 | 222 |  |  |  |  | -0.16964 | 0 | 0.82163 | 0.84178 |  |  |  |  | 168 | 0.020151
60068 | HHOLLOW21A | 1 | West | YES | -0.063992 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 184 |  |  |  |  | -0.16964 | 0 | 0.82163 | 0.84178 |  |  |  |  | 169 | 0.020151
60070 | HHOLLOW31A | 1 | West | YES | -0.063992 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 224 |  |  |  |  | -0.16964 | 0 | 0.82163 | 0.84178 |  |  |  |  | 170 | 0.020151
60072 | HHOLLOW41A | 1 | West | YES | -0.063992 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 115 |  |  |  |  | -0.16964 | 0 | 0.82163 | 0.84178 |  |  |  |  | 171 | 0.020151
1058 | LONGSHORE_5 | 1 | West | YES | -0.063837 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.16948 | 0 | 150 |  |  |  |  | -0.16948 | 0 | 0.82163 | 0.84178 |  |  |  |  | 172 | 0.020151
1058 | LONGSHORE_5 | 2 | West | YES | -0.063837 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.16948 | 0 | 220 |  |  |  |  | -0.16948 | 0 | 0.82163 | 0.84178 |  |  |  |  | 173 | 0.020151
11065 | ELBOWCK_1G | 1 | West | YES | -0.063837 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.16948 | 0 | 121.9 |  |  |  |  | -0.16948 | 0 | 0.82163 | 0.84178 |  |  |  |  | 174 | 0.020151
11309 | BULLCREK_2G | 1 | West | YES | -0.063719 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.16937 | 0 | 180 |  |  |  |  | -0.16937 | 0 | 0.82163 | 0.84178 |  |  |  |  | 175 | 0.020151
11310 | BULLCREK_1G | 1 | West | YES | -0.063719 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.16937 | 0 | 180 |  |  |  |  | -0.16937 | 0 | 0.82163 | 0.84178 |  |  |  |  | 176 | 0.020151
1045 | CALENG1G_1G | 1 | West | YES | -0.063663 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0 | 0.82163 | 0.84178 |  |  |  |  | 177 | 0.020151
1046 | CALENG2G_2G | 2 | West | YES | -0.063663 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0 | 0.82163 | 0.84178 |  |  |  |  | 178 | 0.020151
1047 | CALENG3G_3G | 3 | West | YES | -0.063663 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0 | 0.82163 | 0.84178 |  |  |  |  | 179 | 0.020151
11320 | COYOTE_1G | 1 | West | YES | -0.063659 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.16931 | 0 | 225 |  |  |  |  | -0.16931 | 0 | 0.82163 | 0.84178 |  |  |  |  | 180 | 0.020151
1360 | GUNSIGHT_8 | 1 | West | YES | -0.06341 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.16906 | 0 | 120 |  |  |  |  | -0.16906 | 0 | 0.82163 | 0.84178 |  |  |  |  | 181 | 0.020151
1327 | WILDHRSE_1G | 1 | West | YES | -0.063374 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.16902 | 0 | 120 |  |  |  |  | -0.16902 | 0 | 0.82163 | 0.84178 |  |  |  |  | 182 | 0.020151
13134 | CALFREST_4G | 4 | North | YES | -0.063173 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | -1 | 0.16882 | 151.5 | 151.5 |  |  | -9.5707 | 151.5 | -0.16882 | -25.5763 | 0.82776 | 0.8476 |  |  |  |  | 183 | 0.020151
13135 | CALFREST_5G | 5 | North | YES | -0.063173 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | -1 | 0.16882 | 152.3 | 152.3 |  |  | -9.6212 | 152.3 | -0.16882 | -25.7114 | 0.83392 | 0.85346 |  |  |  |  | 184 | 0.020151
13136 | CALFREST_6G | 6 | North | YES | -0.063173 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | -1 | 0.16882 | 177.5 | 177.5 |  |  | -11.2132 | 177.5 | -0.16882 | -29.9657 | 0.84111 | 0.86028 |  |  |  |  | 185 | 0.020151
1333 | MCDDONAL_8 | 1 | West | YES | -0.063168 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.16882 | 0 | 214.2 |  |  |  |  | -0.16882 | 0 | 0.84111 | 0.86028 |  |  |  |  | 186 | 0.019844
1328 | OCOTILLO_1G | 1 | West | YES | -0.063008 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.16866 | 0 | 58 |  |  |  |  | -0.16866 | 0 | 0.84111 | 0.86028 |  |  |  |  | 187 | 0.019535
13131 | CALFREST_1G | 1 | North | YES | -0.062996 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | -1 | 0.16864 | 150.7 | 150.7 |  |  | -9.4935 | 150.7 | -0.16864 | -25.4146 | 0.8472 | 0.86607 |  |  |  |  | 188 | 0.019175
13132 | CALFREST_2G | 2 | North | YES | -0.062996 | 151 | 57 | 151 | 0 | 1.031 | CC | -1 | 0.16864 | 151 | 151 |  |  | -9.5124 | 151 | -0.16864 | -25.4652 | 0.85331 | 0.87187 |  |  |  |  | 189 | 0.019175
13133 | CALFREST_3G | 3 | North | YES | -0.062996 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | -1 | 0.16864 | 177.4 | 177.4 |  |  | -11.1755 | 177.4 | -0.16864 | -29.9174 | 0.86049 | 0.87868 |  |  |  |  | 190 | 0.019175
11001 | NAV1CT | 1 | West | YES | -0.062916 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.16856 | 70.4 | 70.4 |  |  |  |  | -0.16856 | -11.8669 | 0.86334 | 0.88138 |  |  |  |  | 191 | 0.018863
11009 | NAV2CT | 1 | West | YES | -0.062916 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.16856 | 71.4 | 71.4 |  |  |  |  | -0.16856 | -12.0354 | 0.86623 | 0.88412 |  |  |  |  | 192 | 0.018551
11011 | NAV3ST | 1 | West | YES | -0.062916 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.16856 | 92.8 | 92.8 |  |  |  |  | -0.16856 | -15.6427 | 0.86999 | 0.88768 |  |  |  |  | 193 | 0.018184
11012 | NAV4CT | 1 | West | YES | -0.062916 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.16856 | 80 | 80 |  |  |  |  | -0.16856 | -13.4851 | 0.87323 | 0.89075 |  |  |  |  | 194 | 0.018038
11013 | NAV5CT | 1 | West | YES | -0.062916 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.16856 | 80 | 80 |  |  |  |  | -0.16856 | -13.4851 | 0.87646 | 0.89383 |  |  |  |  | 195 | 0.017889
11014 | NAV6ST | 1 | West | YES | -0.062916 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.16856 | 115 | 115 |  |  |  |  | -0.16856 | -19.3848 | 0.88112 | 0.89824 |  |  |  |  | 196 | 0.017695
11020 | TIEHVSG_1G | 1 | West | YES | -0.062906 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.16855 | 208.2 | 208.2 |  |  |  |  | -0.16855 | -35.0929 | 0.88954 | 0.90623 |  |  |  |  | 197 | 0.017528
11021 | TIEHVCG_1G | 1 | West | YES | -0.062906 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.16855 | 142.1 | 142.1 |  |  |  |  | -0.16855 | -23.9515 | 0.89529 | 0.91168 |  |  |  |  | 198 | 0.017361
11022 | TIEHVCG_2G | 1 | West | YES | -0.062906 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.16855 | 132.4 | 132.4 |  |  |  |  | -0.16855 | -22.3165 | 0.90065 | 0.91677 |  |  |  |  | 199 | 0.017121
11023 | TIEHVCG_3G | 1 | West | YES | -0.062906 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.16855 | 137.4 | 137.4 |  |  |  |  | -0.16855 | -23.1593 | 0.90621 | 0.92204 |  |  |  |  | 200 | 0.016687
11024 | TIEHVCG_4G | 1 | West | YES | -0.062906 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.16855 | 147 | 147 |  |  |  |  | -0.16855 | -24.7774 | 0.91216 | 0.92768 |  |  |  |  | 201 | 0.01639
11025 | TIEHVSG_2G | 1 | West | YES | -0.062906 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.16855 | 213.2 | 213.2 |  |  |  |  | -0.16855 | -35.9356 | 0.92079 | 0.93587 |  |  |  |  | 202 | 0.016113
1326 | STANTONW_8 | 1 | West | YES | -0.06289 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.16854 | 0 | 100.5 |  |  |  |  | -0.16854 | 0 | 0.92079 | 0.93587 |  |  |  |  | 203 | 0.015827
1320 | BSP 1 | 1 | West | YES | -0.062814 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.16846 | 0 | 0 |  |  |  |  | -0.16846 | 0 | 0.92079 | 0.93587 |  |  |  |  | 204 | 0.01552
76031 | L_GASCCR1_1N | W1 | West | YES | -0.062585 | 30 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.16823 | 0 | 150 |  |  |  |  | -0.16823 | 0 | 0.92079 | 0.93587 |  |  |  |  | 205 | 0.015074
60057 | CALLAHAN1A | 1 | West | YES | -0.062487 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | -1 | 0.16813 | 0 | 114 |  |  |  |  | -0.16813 | 0 | 0.92079 | 0.93587 |  |  |  |  | 206 | 0.015074
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.062293 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.16794 | 0 | 112.5 |  |  |  |  | -0.16794 | 0 | 0.92079 | 0.93587 |  |  |  |  | 207 | 0.015074
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.062293 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 149.5 |  |  |  |  | -0.16794 | 0 | 0.92079 | 0.93587 |  |  |  |  | 208 | 0.015074
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.062293 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 186 |  |  |  |  | -0.16794 | 0 | 0.92079 | 0.93587 |  |  |  |  | 209 | 0.015074
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.062293 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 214.5 |  |  |  |  | -0.16794 | 0 | 0.92079 | 0.93587 |  |  |  |  | 210 | 0.015074
11147 | NOTREES_1G | 1 | West | YES | -0.062197 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.16784 | 0 | 149 |  |  |  |  | -0.16784 | 0 | 0.92079 | 0.93587 |  |  |  |  | 211 | 0.015074
3381 | BBRN_1G | 1 | North | YES | -0.062158 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | -1 | 0.16781 | 0 | 618 |  |  | 0 | 0 | -0.16781 | 0 | 0.92079 | 0.93587 |  |  |  |  | 212 | 0.015074
3382 | BBRN_2G | 2 | North | YES | -0.062158 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | -1 | 0.16781 | 0 | 589 |  |  | 0 | 0 | -0.16781 | 0 | 0.92079 | 0.93587 |  |  |  |  | 213 | 0.015074
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.062075 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.16772 | 0 | 35 |  |  |  |  | -0.16772 | 0 | 0.92079 | 0.93587 |  |  |  |  | 214 | 0.015074
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.062075 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.16772 | 0 | 30 |  |  |  |  | -0.16772 | 0 | 0.92079 | 0.93587 |  |  |  |  | 215 | 0.015074
1002 | PBCTAGE_1G | A | West | YES | -0.062012 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.16766 | 66 | 66 |  |  |  |  | -0.16766 | -11.0655 | 0.92346 | 0.93839 |  |  |  |  | 216 | 0.015074
1003 | PBCTBGE_2G | B | West | YES | -0.062012 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.16766 | 66 | 66 |  |  |  |  | -0.16766 | -11.0655 | 0.92613 | 0.94091 |  |  |  |  | 217 | 0.015074
1004 | PBCTCGE_3G | C | West | YES | -0.062012 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.16766 | 67 | 67 |  |  |  |  | -0.16766 | -11.2332 | 0.92884 | 0.94346 |  |  |  |  | 218 | 0.015074
1005 | PBCTDGE_4G | D | West | YES | -0.062012 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.16766 | 68 | 68 |  |  |  |  | -0.16766 | -11.4009 | 0.9316 | 0.94606 |  |  |  |  | 219 | 0.014923
1006 | PBCTEGE_5G | E | West | YES | -0.062012 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.16766 | 67 | 67 |  |  |  |  | -0.16766 | -11.2332 | 0.93431 | 0.94862 |  |  |  |  | 220 | 0.014772
1007 | PB5GEN_6G | 5 | West | YES | -0.062012 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.16766 | 114 | 114 |  |  |  |  | -0.16766 | -19.1132 | 0.93892 | 0.95297 |  |  |  |  | 221 | 0.014618
1008 | PB6GEN_7G | 6 | West | YES | -0.062012 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.16766 | 515 | 515 |  |  |  |  | -0.16766 | -86.3447 | 0.95976 | 0.97263 |  |  |  |  | 222 | 0.014463
1349 | WESTXWIN_1G | 1 | West | YES | -0.061675 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.16732 | 0 | 6.6 |  |  |  |  | -0.16732 | 0 | 0.95976 | 0.97263 |  |  |  |  | 223 | 0.014309
1350 | NWPWRG1_1G | 1 | West | YES | -0.061675 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.16732 | 0 | 34.3 |  |  |  |  | -0.16732 | 0 | 0.95976 | 0.97263 |  |  |  |  | 224 | 0.014048
60007 | KING_SW1A | 1 | West | YES | -0.05606 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16171 | 0 | 80 |  |  |  |  | -0.16171 | 0 | 0.95976 | 0.97263 |  |  |  |  | 225 | 0.012868
60019 | KING_NW1A | 1 | West | YES | -0.05606 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16171 | 0 | 80 |  |  |  |  | -0.16171 | 0 | 0.95976 | 0.97263 |  |  |  |  | 226 | 0.012868
60201 | RIO DRCS | F | West | YES | -0.055786 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.16143 | 0 | 0 |  |  |  |  | -0.16143 | 0 | 0.95976 | 0.97263 |  |  |  |  | 227 | 0.012868
6016 | SWMESA | 1 | West | YES | -0.055675 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.16132 | 0 | 75 |  |  |  |  | -0.16132 | 0 | 0.95976 | 0.97263 |  |  |  |  | 228 | 0.012868
60003 | KING_NE1A | 1 | West | YES | -0.055675 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16132 | 0 | 80 |  |  |  |  | -0.16132 | 0 | 0.95976 | 0.97263 |  |  |  |  | 229 | 0.012868
60005 | KING_SE1A | 1 | West | YES | -0.055675 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.16132 | 0 | 40 |  |  |  |  | -0.16132 | 0 | 0.95976 | 0.97263 |  |  |  |  | 230 | 0.012868
60016 | WOODWRD11A | 1 | West | YES | -0.055604 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.16125 | 0 | 80 |  |  |  |  | -0.16125 | 0 | 0.95976 | 0.97263 |  |  |  |  | 231 | 0.012868
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.05559 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.16124 | 0 | 80 |  |  |  |  | -0.16124 | 0 | 0.95976 | 0.97263 |  |  |  |  | 232 | 0.012868
38437 | TNSRBNMESA9 | 1 | West | YES | -0.055531 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.16118 | 0 | 150 |  |  |  |  | -0.16118 | 0 | 0.95976 | 0.97263 |  |  |  |  | 233 | 0.012868
60017 | ORNNWP1 | 1 | West | YES | -0.053485 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.15913 | 0 | 80 |  |  |  |  | -0.15913 | 0 | 0.95976 | 0.97263 |  |  |  |  | 234 | 0.012868
60000 | DSKY2 | 1 | West | YES | -0.052969 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.15862 | 0 | 76.5 |  |  |  |  | -0.15862 | 0 | 0.95976 | 0.97263 |  |  |  |  | 235 | 0.012868
60018 | DSKY1 | 1 | West | YES | -0.052795 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.15844 | 0 | 84 |  |  |  |  | -0.15844 | 0 | 0.95976 | 0.97263 |  |  |  |  | 236 | 0.012868
48721 | LEG_1___1 | 1 | North | YES | -0.050274 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | -1 | 0.15592 | 0 | 827 |  |  | 0 | 0 | -0.15592 | 0 | 0.95976 | 0.97263 |  |  |  |  | 237 | 0.012868
48722 | LEG_2___2 | 2 | North | YES | -0.050274 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | -1 | 0.15592 | 0 | 819 |  |  | 0 | 0 | -0.15592 | 0 | 0.95976 | 0.97263 |  |  |  |  | 238 | 0.012868
60202 | FRNDDRCS | F | West | YES | -0.042109 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.14776 | 0 | 0 |  |  |  |  | -0.14776 | 0 | 0.95976 | 0.97263 |  |  |  |  | 239 | 0.012868
39960 | TNTNPONE_18 | 1 | North | YES | -0.041618 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | -1 | 0.14727 | 0 | 152.3 |  |  | 0 | 0 | -0.14727 | 0 | 0.95976 | 0.97263 |  |  |  |  | 240 | 0.012868
39970 | TNTNPONE_28 | 1 | North | YES | -0.041618 | 153 | 30 | 153 |  | 1.04 | LIGCO | -1 | 0.14727 | 0 | 153 |  |  | 0 | 0 | -0.14727 | 0 | 0.95976 | 0.97263 |  |  |  |  | 241 | 0.012868
990 | GIBN_CREK_G1 | 1 | North | YES | -0.021238 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | -1 | 0.12689 | 0 | 463 |  |  | 0 | 0 | -0.12689 | 0 | 0.95976 | 0.97263 |  |  |  |  | 242 | 0.012868
32798 | BRYN_TAMUGEN | 1 | North | YES | -0.016957 | 32 | 0 | 32 |  | 1.02 | GST | -1 | 0.1226 | 32 | 32 |  |  | -0.54262 | 32 | -0.1226 | -3.9234 | 0.96106 | 0.97353 |  |  |  |  | 243 | 0.012868
32886 | BRYN_ATKINS3 | MB | North | YES | -0.016796 | 0 | 5 | 12 |  | 1 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0 | 0.96106 | 0.97353 |  |  |  |  | 244 | 0.012868
32887 | BRYN_ATKINS6 | MB | North | YES | -0.016796 | 0 | 12 | 51 |  | 1.028 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0 | 0.96106 | 0.97353 |  |  |  |  | 245 | 0.012868
32888 | BRYN_ATKINS7 | 1 | North | YES | -0.016796 | 13.6 | 4 | 17 |  | 1.028 | GGT | -1 | 0.12244 | 17 | 17 |  |  | -0.28553 | 17 | -0.12244 | -2.0815 | 0.96175 | 0.974 |  |  |  |  | 246 | 0.012466
32890 | BRYN_ATKINS4 | MB | North | YES | -0.016796 | 0 | 5 | 22 |  | 1.031 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0 | 0.96175 | 0.974 |  |  |  |  | 247 | 0.012466
32891 | BRYN_ATKINS5 | MB | North | YES | -0.016796 | 0 | 5 | 25 |  | 1.031 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0 | 0.96175 | 0.974 |  |  |  |  | 248 | 0.012466
48671 | FTR_GT1_5105 | 1 | North | YES | -0.015218 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | -1 | 0.12087 | 154.2 | 154.2 |  |  | -2.3466 | 154.2 | -0.12087 | -18.6375 | 0.96799 | 0.97824 |  |  |  |  | 249 | 0.012252
48672 | FTR_GT2_5110 | 2 | North | YES | -0.015218 | 159 | 0 | 159 | 0 | 1.0319 | CC | -1 | 0.12087 | 159 | 159 |  |  | -2.4197 | 159 | -0.12087 | -19.2176 | 0.97442 | 0.98262 |  |  |  |  | 250 | 0.012252
48673 | FTR_GT3_5085 | 3 | North | YES | -0.015218 | 158 | 0 | 158 | 0 | 1.0319 | CC | -1 | 0.12087 | 158 | 158 |  |  | -2.4044 | 158 | -0.12087 | -19.0968 | 0.98082 | 0.98697 |  |  |  |  | 251 | 0.012252
48674 | FTR_CN4_5095 | 4 | North | YES | -0.015218 | 380 | 0 | 380 | 0 | 1.0319 | CC | -1 | 0.12087 | 380 | 380 |  |  | -5.7828 | 380 | -0.12087 | -45.929 | 0.9962 | 0.99743 |  |  |  |  | 252 | 0.010255
32883 | BRYN_DNSBY3 | 1 | North | YES | -0.014565 | 0 | 2 | 48 |  | 1.015 | GST | -1 | 0.12021 | 48 | 48 |  |  | -0.69912 | 48 | -0.12021 | -5.7702 | 0.99814 | 0.99874 |  |  |  |  | 253 | 0.0081967
32884 | BRYN_DNSBY13 | 1 | North | YES | -0.014565 | 46 | 2 | 46 | 0 | 1.015 | GST | -1 | 0.12021 | 46 | 46 |  |  | -0.66999 | 46 | -0.12021 | -5.5298 | 1 | 1 |  |  |  |  | 254 | 0.0061511
32892 | BRYN_DNSBY14 | 1 | North | YES | -0.014565 | 84 | 25 | 105 | 0 | 1.035 | GST | -1 | 0.12021 | 105 | 105 |  |  | -1.5293 | 105 | -0.12021 | -12.6223 | 1.0042 | 1.0029 |  |  |  |  | 255 | 0.001231
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.073157 | 15 | 15 | 0 | 15 |  |  | 0.073157 | 1.0974 | [6 empty] | 256 | 0.00060242
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | [6 empty] | 257 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | [6 empty] | 258 | -0.0013751
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | [6 empty] | 259 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | [6 empty] | 260 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | [6 empty] | 261 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | [6 empty] | 262 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | [6 empty] | 263 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | [6 empty] | 264 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.073157 | 0 | 0 |  |  |  |  | 0.073157 | 0 | [6 empty] | 265 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.016213 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | [6 empty] | 266 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.016213 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | [6 empty] | 267 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.016213 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | [6 empty] | 268 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.016213 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | [6 empty] | 269 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.016213 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | [6 empty] | 270 | 0
48885 | THW_5152 | B | Houston | YES | 0.019689 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.092846 | 59 | 59 |  |  |  |  | 0.092846 | 5.4779 | [6 empty] | 271 | 0
48885 | THW_5152 | A | Houston | YES | 0.019689 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.092846 | 58 | 58 |  |  |  |  | 0.092846 | 5.3851 | [6 empty] | 272 | 0
48886 | THW_5354 | D | Houston | YES | 0.019689 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.092846 | 58 | 58 |  |  |  |  | 0.092846 | 5.3851 | [6 empty] | 273 | 0
48886 | THW_5354 | C | Houston | YES | 0.019689 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.092846 | 57 | 57 |  |  |  |  | 0.092846 | 5.2922 | [6 empty] | 274 | 0
48887 | THW_5556 | E | Houston | YES | 0.019689 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.092846 | 59 | 59 |  |  |  |  | 0.092846 | 5.4779 | [6 empty] | 275 | 0
48887 | THW_5556 | F | Houston | YES | 0.019689 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.092846 | 57 | 57 |  |  |  |  | 0.092846 | 5.2922 | [6 empty] | 276 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.019936 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.093093 | 398 | 398 |  |  |  |  | 0.093093 | 37.0512 | [6 empty] | 277 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.020115 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.093272 | 162.8 | 162.8 |  |  |  |  | 0.093272 | 15.1848 | [6 empty] | 278 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.020115 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.093272 | 161.4 | 161.4 |  |  |  |  | 0.093272 | 15.0542 | [6 empty] | 279 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.020115 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.093272 | 158.9 | 158.9 |  |  |  |  | 0.093272 | 14.821 | [6 empty] | 280 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.020115 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.093272 | 269.2 | 269.2 |  |  |  |  | 0.093272 | 25.1089 | [6 empty] | 281 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 | [6 empty] | 282 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 | [6 empty] | 283 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 | [6 empty] | 284 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.020784 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.093941 | 0 | 0 |  |  |  |  | 0.093941 | 0 | [6 empty] | 285 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.020965 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | [6 empty] | 286 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.020965 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | [6 empty] | 287 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.020965 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | [6 empty] | 288 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.020965 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | [6 empty] | 289 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.020965 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | [6 empty] | 290 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.020965 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | [6 empty] | 291 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.020965 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 | [6 empty] | 292 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.020975 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.094132 | 744 | 744 |  |  |  |  | 0.094132 | 70.0345 | [6 empty] | 293 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.020987 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.094144 | 0 | 0 |  |  |  |  | 0.094144 | 0 | [6 empty] | 294 | 0
48651 | EP_1_2 | 1 | Houston | YES | 0.020998 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.094155 | 0 | 0 |  |  |  |  | 0.094155 | 0 | [6 empty] | 295 | 0
48651 | EP_1_2 | 2 | Houston | YES | 0.020998 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.094155 | 0 | 0 |  |  |  |  | 0.094155 | 0 | [6 empty] | 296 | 0
49803 | EXN_15GT | 1 | Houston | YES | 0.021324 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 297 | 0
49804 | EXN_16GT | 2 | Houston | YES | 0.021324 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 298 | 0
49805 | EXN_17GT | 3 | Houston | YES | 0.021324 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 299 | 0
49826 | EXN938GT | 5 | Houston | YES | 0.021324 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 300 | 0
49828 | EXN941GT | 10 | Houston | YES | 0.021324 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 301 | 0
49829 | EXN942GT | 11 | Houston | YES | 0.021324 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 302 | 0
49830 | EXN943GT | 12 | Houston | YES | 0.021324 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 303 | 0
49831 | EXN944GT | 13 | Houston | YES | 0.021324 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 304 | 0
49832 | EXN945GT | 9 | Houston | YES | 0.021324 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 305 | 0
49837 | EXN_GT | 4 | Houston | YES | 0.021324 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 306 | 0
49838 | EXN_14GT | 14 | Houston | YES | 0.021324 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 | [6 empty] | 307 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.021417 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.094574 | 12 | 12 |  |  |  |  | 0.094574 | 1.1349 | [6 empty] | 308 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.021662 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.094819 | 746 | 746 |  |  |  |  | 0.094819 | 70.7353 | [6 empty] | 309 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.022175 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.095332 | 107 | 107 |  |  |  |  | 0.095332 | 10.2006 | [6 empty] | 310 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.022175 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.095332 | 108 | 108 |  |  |  |  | 0.095332 | 10.2959 | [6 empty] | 311 | 0
48875 | THW_3132 | A | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 | [6 empty] | 312 | 0
48875 | THW_3132 | B | Houston | YES | 0.022175 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.095332 | 53 | 53 |  |  |  |  | 0.095332 | 5.0526 | [6 empty] | 313 | 0
48877 | THW_3334 | C | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 | [6 empty] | 314 | 0
48877 | THW_3334 | D | Houston | YES | 0.022175 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.095332 | 57 | 57 |  |  |  |  | 0.095332 | 5.4339 | [6 empty] | 315 | 0
48879 | THW_4142 | E | Houston | YES | 0.022175 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.095332 | 56 | 56 |  |  |  |  | 0.095332 | 5.3386 | [6 empty] | 316 | 0
48879 | THW_4142 | F | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 | [6 empty] | 317 | 0
48881 | THW_4344 | G | Houston | YES | 0.022175 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.095332 | 58 | 58 |  |  |  |  | 0.095332 | 5.5293 | [6 empty] | 318 | 0
48881 | THW_4344 | H | Houston | YES | 0.022175 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.095332 | 58 | 58 |  |  |  |  | 0.095332 | 5.5293 | [6 empty] | 319 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.022792 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.095949 | 0 | 0 |  |  |  |  | 0.095949 | 0 | [6 empty] | 320 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.022792 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.095949 | 0 | 0 |  |  |  |  | 0.095949 | 0 | [6 empty] | 321 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.022853 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.09601 | 42 | 42 |  |  |  |  | 0.09601 | 4.0324 | [6 empty] | 322 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.022853 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.09601 | 42 | 42 |  |  |  |  | 0.09601 | 4.0324 | [6 empty] | 323 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.022853 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.09601 | 39 | 39 |  |  |  |  | 0.09601 | 3.7444 | [6 empty] | 324 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.022853 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.09601 | 39 | 39 |  |  |  |  | 0.09601 | 3.7444 | [6 empty] | 325 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.022953 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.09611 | 0 | 0 |  |  |  |  | 0.09611 | 0 | [6 empty] | 326 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.023372 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 | [6 empty] | 327 | 0
48821 | SHELLG2 | 2 | Houston | YES | 0.023372 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 | [6 empty] | 328 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.023372 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 | [6 empty] | 329 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.023372 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 | [6 empty] | 330 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.023677 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 | [6 empty] | 331 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.023677 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 | [6 empty] | 332 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.023677 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 | [6 empty] | 333 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.023677 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.096834 | 228 | 228 |  |  |  |  | 0.096834 | 22.0783 | [6 empty] | 334 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.023683 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 | [6 empty] | 335 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.023683 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 | [6 empty] | 336 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.023683 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 | [6 empty] | 337 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.023683 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 | [6 empty] | 338 | 0
48845 | SOL_GT1 | 1 | Houston | YES | 0.023686 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.096843 | 16.2 | 16.2 |  |  |  |  | 0.096843 | 1.5689 | [6 empty] | 339 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.02369 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.096847 | 213 | 213 |  |  |  |  | 0.096847 | 20.6285 | [6 empty] | 340 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.023742 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.096899 | 0 | 0 |  |  |  |  | 0.096899 | 0 | [6 empty] | 341 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.023742 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.096899 | 0 | 0 |  |  |  |  | 0.096899 | 0 | [6 empty] | 342 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.023747 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.096904 | 165 | 165 |  |  |  |  | 0.096904 | 15.9892 | [6 empty] | 343 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.023763 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.09692 | 176 | 176 |  |  |  |  | 0.09692 | 17.058 | [6 empty] | 344 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | 0.023775 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.096932 | 18 | 18 |  |  |  |  | 0.096932 | 1.7448 | [6 empty] | 345 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | 0.023775 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.096932 | 12 | 12 |  |  |  |  | 0.096932 | 1.1632 | [6 empty] | 346 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.023993 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.09715 | 0 | 0 |  |  |  |  | 0.09715 | 0 | [6 empty] | 347 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.024207 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.097364 | 163.2 | 163.2 |  |  |  |  | 0.097364 | 15.8899 | [6 empty] | 348 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.024207 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.097364 | 157.1 | 157.1 |  |  |  |  | 0.097364 | 15.296 | [6 empty] | 349 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.024207 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.097364 | 157.5 | 157.5 |  |  |  |  | 0.097364 | 15.3349 | [6 empty] | 350 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.024207 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.097364 | 157 | 157 |  |  |  |  | 0.097364 | 15.2862 | [6 empty] | 351 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.024207 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.097364 | 282 | 282 |  |  |  |  | 0.097364 | 27.4568 | [6 empty] | 352 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.024434 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.097591 | 0 | 0 |  |  |  |  | 0.097591 | 0 | [6 empty] | 353 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.024434 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.097591 | 0 | 0 |  |  |  |  | 0.097591 | 0 | [6 empty] | 354 | 0
48691 | GBY_73741085 | B | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 | [6 empty] | 355 | 0
48691 | GBY_73741085 | A | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 | [6 empty] | 356 | 0
48692 | GBY_81821075 | D | Houston | YES | 0.024725 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.097882 | 55 | 55 |  |  |  |  | 0.097882 | 5.3835 | [6 empty] | 357 | 0
48692 | GBY_81821075 | C | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 | [6 empty] | 358 | 0
48693 | GBY_83841065 | F | Houston | YES | 0.024725 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.097882 | 54 | 54 |  |  |  |  | 0.097882 | 5.2857 | [6 empty] | 359 | 0
48693 | GBY_83841065 | E | Houston | YES | 0.024725 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.097882 | 57 | 57 |  |  |  |  | 0.097882 | 5.5793 | [6 empty] | 360 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.025309 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 | [6 empty] | 361 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.025309 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 | [6 empty] | 362 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.025309 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 | [6 empty] | 363 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.025309 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 | [6 empty] | 364 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.025774 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | [6 empty] | 365 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.025774 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | [6 empty] | 366 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.025774 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | [6 empty] | 367 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.025774 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | [6 empty] | 368 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.025774 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 | [6 empty] | 369 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | 0.026988 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.10015 | 0 | 0 |  |  |  |  | 0.10015 | 0 | [6 empty] | 370 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.028729 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 371 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.028729 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 372 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.028729 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 373 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.028729 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 374 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.028729 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 375 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.028729 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 376 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.028729 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 377 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.028729 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 378 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.028729 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 379 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.028729 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 380 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.028729 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 381 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.028729 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 382 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.028729 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 383 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.028729 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 384 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.028729 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 | [6 empty] | 385 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.032833 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.10599 | 166 | 166 |  |  |  |  | 0.10599 | 17.5944 | [6 empty] | 386 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.032833 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.10599 | 166 | 166 |  |  |  |  | 0.10599 | 17.5944 | [6 empty] | 387 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.032833 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.10599 | 248 | 248 |  |  |  |  | 0.10599 | 26.2856 | [6 empty] | 388 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.032833 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.10599 | 546 | 546 |  |  |  |  | 0.10599 | 57.8708 | [6 empty] | 389 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.032833 | 578.7 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.10599 | 0 | 654 |  |  |  |  | 0.10599 | 69.3177 | [6 empty] | 390 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.032833 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.10599 | 13 | 13 |  |  |  |  | 0.10599 | 1.3779
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.032933 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.10609 | 0 | 0 |  |  |  |  | 0.10609 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.03385 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.10701 | 167.7 | 167.7 |  |  |  |  | 0.10701 | 17.9451
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.03385 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.10701 | 166.4 | 166.4 |  |  |  |  | 0.10701 | 17.806
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.03385 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.10701 | 252.4 | 252.4 |  |  |  |  | 0.10701 | 27.0087
48730 | MNS_GT | 1 | Houston | YES | 0.033879 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.10704 | 0 | 0 |  |  |  |  | 0.10704 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.033903 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 651 |  |  |  |  | 0.10706 | 69.6963
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.033903 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 564 |  |  |  |  | 0.10706 | 60.3821
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.033903 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 603 |  |  |  |  | 0.10706 | 64.5574
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.04015 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.04015 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.04015 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.04015 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.041916 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.11507 | 0 | 0 |  |  |  |  | 0.11507 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.041916 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.11507 | 0 | 0 |  |  |  |  | 0.11507 | 0
49851 | DOW17000 | 37 | Houston | YES | 0.044148 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49858 | DOW38100 | 31 | Houston | YES | 0.044148 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49859 | DOW38200 | 33 | Houston | YES | 0.044148 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49860 | DOW38300 | 32 | Houston | YES | 0.044148 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49862 | DOW39100 | 36 | Houston | YES | 0.044148 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49863 | DOW39200 | 35 | Houston | YES | 0.044148 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49865 | DOW41000 | 41 | Houston | YES | 0.044148 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49866 | DOW42000 | 42 | Houston | YES | 0.044148 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49869 | DOW49000 | 45 | Houston | YES | 0.044148 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49870 | DOW61000 | 61 | Houston | YES | 0.044148 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49871 | DOW62000 | 62 | Houston | YES | 0.044148 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49872 | DOW63000 | 63 | Houston | YES | 0.044148 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49873 | DOW64000 | 64 | Houston | YES | 0.044148 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49876 | DOW65000 | 65 | Houston | YES | 0.044148 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49877 | DOW66000 | 66 | Houston | YES | 0.044148 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49878 | DOW67000 | 67 | Houston | YES | 0.044148 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49882 | DOW81000 | 81 | Houston | YES | 0.044148 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49884 | DOW82000 | 82 | Houston | YES | 0.044148 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49885 | DOW83000 | 83 | Houston | YES | 0.044148 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
49886 | DOW84000 | 84 | Houston | YES | 0.044148 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.045618 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.045618 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0
88253 | HAMILTON | F | South | YES | 0.045618 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.052688 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.12585 | 0 | 0 |  |  |  |  | 0.12585 | 0
48731 | CBE_GT1 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848
48732 | CBE_GT2 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848
48733 | CBE_ST12 | 1 | Houston | YES | 0.05559 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.12875 | 105 | 105 |  |  |  |  | 0.12875 | 13.5185
48734 | CBE_GT3 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848
48735 | CBE_GT4 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848
48736 | CBE_ST34 | 1 | Houston | YES | 0.05559 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.12875 | 105 | 105 |  |  |  |  | 0.12875 | 13.5185
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.05598 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.05598 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.05598 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | 0.056151 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.12931 | 0 | 0 |  |  |  |  | 0.12931 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | 0.056151 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.12931 | 0 | 0 |  |  |  |  | 0.12931 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.057715 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.13087 | 0 | 0 | 0 | 0 |  |  | 0.13087 | 0
8262 | ELPS | 1 | South | YES | 0.058475 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.13163 | 0 | 0 | 0 | 0 |  |  | 0.13163 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | 0.073077 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.14623 | 423.3 | 423.3 | 30.9335 | 423.3 |  |  | 0.14623 | 61.901
7035 | L_WIRTZ_1G1Y | 1 | South | YES | 0.073215 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.14637 | 0 | 0 | 0 | 0 |  |  | 0.14637 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | 0.073215 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.14637 | 0 | 0 | 0 | 0 |  |  | 0.14637 | 0
8134 | FOR #1 | 1 | South | YES | 0.077991 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
8138 | FOR #2 | 2 | South | YES | 0.077991 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
8153 | FOR #3 | 3 | South | YES | 0.077991 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
8154 | FOR #4 | 4 | South | YES | 0.077991 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
8155 | FOR #5 | 5 | South | YES | 0.077991 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
8156 | FOR #6 | 6 | South | YES | 0.077991 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
8157 | FOR #7 | 7 | South | YES | 0.077991 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
80051 | FOR #8 | 8 | South | YES | 0.077991 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
80052 | FOR #9 | 9 | South | YES | 0.077991 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
80053 | FOR #10 | 10 | South | YES | 0.077991 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0
80226 | ALCOA G | 1 | South | YES | 0.078601 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.15176 | 0 | 0 | 0 | 0 |  |  | 0.15176 | 0
8147 | UCAR #2 | 10 | South | YES | 0.080583 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0
8148 | UCAR #1 | 2 | South | YES | 0.080583 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0
80137 | CSDR89 | 9 | South | YES | 0.080583 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0
80137 | CSDR89 | 8 | South | YES | 0.080583 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0
80138 | CSDR7 | 7 | South | YES | 0.080583 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0
80139 | CSDR56 | 6 | South | YES | 0.080583 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0
80139 | CSDR56 | 5 | South | YES | 0.080583 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0
80140 | CSDR11 | 11 | South | YES | 0.080584 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0
80227 | AIRCO G | 1 | South | YES | 0.080868 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.15403 | 0 | 0 | 0 | 0 |  |  | 0.15403 | 0
80224 | VISTRONG1 | 1 | South | YES | 0.081411 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.15457 | 0 | 0 | 0 | 0 |  |  | 0.15457 | 0
80225 | VISTRONG2 | 2 | South | YES | 0.081411 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.15457 | 0 | 0 | 0 | 0 |  |  | 0.15457 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | 0.081623 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.15478 | 0 | 0 | 0 | 0 |  |  | 0.15478 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | 0.081623 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.15478 | 0 | 0 | 0 | 0 |  |  | 0.15478 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | 0.082165 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.15532 | 22 | 22 | 1.8076 | 22 |  |  | 0.15532 | 3.4171
5505 | RAYBURNGEN1 | 1 | South | YES | 0.082165 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.15532 | 11 | 11 | 0.90382 | 11 |  |  | 0.15532 | 1.7085
5506 | RAYBURNGEN2 | 1 | South | YES | 0.082165 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.15532 | 11 | 11 | 0.90382 | 11 |  |  | 0.15532 | 1.7085
80265 | LARECU40A | 4 | South | YES | 0.082565 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.15572 | 100 | 100 | 8.2565 | 100 |  |  | 0.15572 | 15.5722
80266 | LARECU50A | 5 | South | YES | 0.082565 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.15572 | 100 | 100 | 8.2565 | 100 |  |  | 0.15572 | 15.5722
80012 | LAR | F | South | YES | 0.082566 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.15572 | 0 | 0 | 0 | 0 |  |  | 0.15572 | 0
5508 | RAYBURNCC9 | 1 | South | YES | 0.082849 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.15601 | 47.7 | 47.7 | 3.9519 | 47.7 |  |  | 0.15601 | 7.4415
5509 | RAYBURNCC10 | 1 | South | YES | 0.082849 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.15601 | 37.3 | 37.3 | 3.0903 | 37.3 |  |  | 0.15601 | 5.819
5511 | RAYBURNCC7 | 1 | South | YES | 0.082849 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.15601 | 47.5 | 47.5 | 3.9353 | 47.5 |  |  | 0.15601 | 7.4103
5512 | RAYBURNCC8 | 1 | South | YES | 0.082849 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.15601 | 49.3 | 49.3 | 4.0845 | 49.3 |  |  | 0.15601 | 7.6911
8066 | DUP1V#1 | 1 | South | YES | 0.082883 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.15604 | 0 | 0 | 0 | 0 |  |  | 0.15604 | 0
8926 | LGE_GT10A | 1 | South | YES | 0.083143 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0
8927 | LGE_GT20A | 2 | South | YES | 0.083143 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0
8928 | LGE_STG0A | 3 | South | YES | 0.083143 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0
8930 | ICPGN10A | 1 | South | YES | 0.083143 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0
8931 | ICPGN20A | 2 | South | YES | 0.083143 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0
8932 | ICPGN30A | 3 | South | YES | 0.083143 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0
80223 | REYSHR G | 1 | South | YES | 0.083143 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0
88299 | ZAPATA | F | South | YES | 0.083317 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.15647 | 0 | 0 | 0 | 0 |  |  | 0.15647 | 0
8173 | VICEC51A | 5 | South | YES | 0.083722 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.15688 | 144 | 144 | 12.056 | 144 |  |  | 0.15688 | 22.5906
8174 | VICEC61A | 6 | South | YES | 0.083722 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.15688 | 188 | 188 | 15.7397 | 188 |  |  | 0.15688 | 29.4933
5728 | FALCONHYDRO2 | 2 | South | YES | 0.083825 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 0.083825 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 0.083825 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0
88508 | FALFURRI | F | South | YES | 0.083826 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0
8442 | NBEC7 | 7 | South | YES | 0.08386 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.15702 | 367 | 367 | 30.7766 | 367 |  |  | 0.15702 | 57.6254
8442 | NBEC7 | MB | South | YES | 0.08386 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.15702 | 0 | 0 | 0 | 0 |  |  | 0.15702 | 0
8560 | CNOPGT1 | 1 | South | YES | 0.083868 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0
8561 | CNOPGT2 | 2 | South | YES | 0.083868 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0
8562 | CNOPST1 | 3 | South | YES | 0.083868 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0
8456 | COSW#1 | 1 | South | YES | 0.083909 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.15707 | 0 | 0 | 0 | 0 |  |  | 0.15707 | 0
8457 | COSW#2 | 2 | South | YES | 0.083909 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.15707 | 0 | 0 | 0 | 0 |  |  | 0.15707 | 0
8459 | B_DAVIS0B | MB | South | YES | 0.084009 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.15717 | 0 | 0 | 0 | 0 |  |  | 0.15717 | 0
8460 | B_DAVIS0A | MB | South | YES | 0.084009 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.15717 | 0 | 0 | 0 | 0 |  |  | 0.15717 | 0
80263 | B_DAVIS31A | 3 | South | YES | 0.084009 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.15717 | 180 | 180 | 15.1216 | 180 |  |  | 0.15717 | 28.29
80264 | B_DAVIS41A | 4 | South | YES | 0.084009 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.15717 | 180 | 180 | 15.1216 | 180 |  |  | 0.15717 | 28.29
8506 | VAL #1 | 1 | South | YES | 0.084042 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.1572 | 0 | 0 | 0 | 0 |  |  | 0.1572 | 0
8507 | VAL #2 | 2 | South | YES | 0.084042 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.1572 | 0 | 0 | 0 | 0 |  |  | 0.1572 | 0
8461 | KOCH_UP0A | 1 | South | YES | 0.084115 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.15727 | 0 | 0 | 0 | 0 |  |  | 0.15727 | 0
8511 | OXY_CC0A | 1 | South | YES | 0.084121 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.15728 | 0 | 0 | 0 | 0 |  |  | 0.15728 | 0
8933 | FGNTS001 | 1 | South | YES | 0.084356 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.15751 | 146.5 | 146.5 | 12.3582 | 146.5 |  |  | 0.15751 | 23.0757
8934 | FGNTS101 | 2 | South | YES | 0.084356 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.15751 | 147.9 | 147.9 | 12.4763 | 147.9 |  |  | 0.15751 | 23.2962
8935 | FGNTS201 | 3 | South | YES | 0.084356 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.15751 | 173 | 173 | 14.5936 | 173 |  |  | 0.15751 | 27.2498
8517 | CELANEBI0A | 1 | South | YES | 0.084407 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.15756 | 0 | 0 | 0 | 0 |  |  | 0.15756 | 0
8936 | MVGN#1 | 1 | South | YES | 0.084446 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.1576 | 216.6 | 216.6 | 18.291 | 216.6 |  |  | 0.1576 | 34.1369
8937 | MVGN#2 | 2 | South | YES | 0.084446 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.1576 | 216.7 | 216.7 | 18.2994 | 216.7 |  |  | 0.1576 | 34.1527
8938 | MVGN#3 | 3 | South | YES | 0.084446 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.1576 | 250.9 | 250.9 | 21.1875 | 250.9 |  |  | 0.1576 | 39.5427
8981 | HECN1 | 1 | South | YES | 0.084446 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.1576 | 144.8 | 144.8 | 12.2278 | 144.8 |  |  | 0.1576 | 22.821
8982 | HECN2 | 2 | South | YES | 0.084446 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.1576 | 144.1 | 144.1 | 12.1687 | 144.1 |  |  | 0.1576 | 22.7107
8983 | HECN3 | 3 | South | YES | 0.084446 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.1576 | 171.9 | 171.9 | 14.5163 | 171.9 |  |  | 0.1576 | 27.092
5932 | SI_RAY9 | 9 | South | YES | 0.084476 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.15763 | 38 | 38 | 3.2101 | 38 |  |  | 0.15763 | 5.9901
5933 | SI_RAY6 | 6 | South | YES | 0.084476 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.15763 | 19.3 | 19.3 | 1.6304 | 19.3 |  |  | 0.15763 | 3.0423
5935 | SI_RAY10 | 10 | South | YES | 0.084476 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.15763 | 47 | 47 | 3.9704 | 47 |  |  | 0.15763 | 7.4088
80003 | MILHWYS | F | South | YES | 0.084476 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.15763 | 0 | 0 | 0 | 0 |  |  | 0.15763 | 0
80080 | GWINDT11A | 3 | South | YES | 0.084498 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 38 | 3.2109 | 38 |  |  | 0.15766 | 5.9909
80080 | GWINDT11A | 4 | South | YES | 0.084498 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 19 | 1.6055 | 19 |  |  | 0.15766 | 2.9955
80080 | GWINDT11A | 2 | South | YES | 0.084498 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 41 | 3.4644 | 41 |  |  | 0.15766 | 6.4639
80080 | GWINDT11A | 1 | South | YES | 0.084498 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 94 | 7.9428 | 94 |  |  | 0.15766 | 14.8196
80081 | GWINDT21A | 4 | South | YES | 0.084498 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 22 | 1.859 | 22 |  |  | 0.15766 | 3.4684
80081 | GWINDT21A | 1 | South | YES | 0.084498 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 94 | 7.9428 | 94 |  |  | 0.15766 | 14.8196
80081 | GWINDT21A | 3 | South | YES | 0.084498 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 43 | 3.6334 | 43 |  |  | 0.15766 | 6.7792
80081 | GWINDT21A | 2 | South | YES | 0.084498 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 36 | 3.0419 | 36 |  |  | 0.15766 | 5.6756
80180 | PNSCALT11A | 2 | South | YES | 0.084498 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 50 | 4.2249 | 50 |  |  | 0.15766 | 7.8828
80180 | PNSCALT11A | 1 | South | YES | 0.084498 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 148 | 12.5057 | 148 |  |  | 0.15766 | 23.333
80181 | PNSCALT21A | 2 | South | YES | 0.084498 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 50 | 4.2249 | 50 |  |  | 0.15766 | 7.8828
80181 | PNSCALT21A | 1 | South | YES | 0.084498 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 55 | 4.6474 | 55 |  |  | 0.15766 | 8.671
8161 | COLETO0A | 1 | South | YES | 0.0875 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.16066 | 0 | 633 | 55.3875 | 633 |  |  | 0.16066 | 101.6962
58909 | PEARSALLSCG1 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58909 | PEARSALLSCG1 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58909 | PEARSALLSCG1 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58909 | PEARSALLSCG1 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58909 | PEARSALLSCG1 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58909 | PEARSALLSCG1 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58919 | PEARSALLSCG2 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58919 | PEARSALLSCG2 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58919 | PEARSALLSCG2 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58919 | PEARSALLSCG2 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58919 | PEARSALLSCG2 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58919 | PEARSALLSCG2 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58929 | PEARSALLSCG3 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58929 | PEARSALLSCG3 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58929 | PEARSALLSCG3 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58929 | PEARSALLSCG3 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58929 | PEARSALLSCG3 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58929 | PEARSALLSCG3 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58949 | PEARSALLSCG4 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58949 | PEARSALLSCG4 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58949 | PEARSALLSCG4 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58949 | PEARSALLSCG4 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58949 | PEARSALLSCG4 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
58949 | PEARSALLSCG4 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514
88198 | BEEVILLE | F | South | YES | 0.088248 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.16141 | 0 | 0 | 0 | 0 |  |  | 0.16141 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | 0.089443 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.1626 | 24 | 24 | 2.1466 | 24 |  |  | 0.1626 | 3.9024
5891 | PEARSALLGEN2 | 1 | South | YES | 0.089443 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.1626 | 24.3 | 24.3 | 2.1735 | 24.3 |  |  | 0.1626 | 3.9512
5892 | PEARSALLGEN3 | 1 | South | YES | 0.089443 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.1626 | 23.9 | 23.9 | 2.1377 | 23.9 |  |  | 0.1626 | 3.8862
5903 | SANMIGUELGEN | 1 | South | YES | 0.095866 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.16902 | 0 | 396.3 | 37.9917 | 396.3 |  |  | 0.16902 | 66.984
8189 | CUECPL2A | 1 | South | YES | 0.097885 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.17104 | 0 | 0 | 0 | 0 |  |  | 0.17104 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.099303 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.099303 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.099303 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | 0.099885 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.17304 | 0 | 562 | 56.1354 | 562 |  |  | 0.17304 | 97.2498
5264 | LEON_LCP3G3 | 3 | South | YES | 0.099997 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.17315 | 58 | 58 | 5.7998 | 58 |  |  | 0.17315 | 10.043
5265 | LEON_LCP4G4 | 4 | South | YES | 0.099997 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.17315 | 89 | 89 | 8.8997 | 89 |  |  | 0.17315 | 15.4107
5266 | LEON_LCPCT1 | 1 | South | YES | 0.099997 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.17315 | 44 | 44 | 4.3999 | 44 |  |  | 0.17315 | 7.6188
5267 | LEON_LCPCT2 | 2 | South | YES | 0.099997 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.17315 | 44 | 44 | 4.3999 | 44 |  |  | 0.17315 | 7.6188
5268 | LEON_LCPCT3 | 3 | South | YES | 0.099997 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.17315 | 43 | 43 | 4.2999 | 43 |  |  | 0.17315 | 7.4456
5269 | LEON_LCPCT4 | 4 | South | YES | 0.099997 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.17315 | 45 | 45 | 4.4999 | 45 |  |  | 0.17315 | 7.7919
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.10033 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.17348 | 155 | 155 | 15.5507 | 155 |  |  | 0.17348 | 26.8901
5477 | BRA_AVR1_ST | 1 | South | YES | 0.10033 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.17348 | 174 | 174 | 17.4569 | 174 |  |  | 0.17348 | 30.1863
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.10033 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.17348 | 155 | 155 | 15.5507 | 155 |  |  | 0.17348 | 26.8901
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.10067 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.17383 | 407 | 407 | 40.9743 | 407 |  |  | 0.17383 | 70.7494
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.10072 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.17388 | 215 | 215 | 21.6546 | 215 |  |  | 0.17388 | 37.3834
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.10072 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.17388 | 216 | 216 | 21.7553 | 216 |  |  | 0.17388 | 37.5573
5396 | CALAVER_OWS1 | 1 | South | YES | 0.10085 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.174 | 418 | 418 | 42.154 | 418 |  |  | 0.174 | 72.7339
5397 | CALAVER_OWS2 | 2 | South | YES | 0.10085 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.174 | 400 | 400 | 40.3388 | 400 |  |  | 0.174 | 69.6018
5111 | CALAVER_JTD1 | 1 | South | YES | 0.10099 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.17415 | 0 | 430 | 43.4253 | 430 |  |  | 0.17415 | 74.883
5112 | CALAVER_JTD2 | 2 | South | YES | 0.10099 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.17415 | 0 | 430 | 43.4253 | 430 |  |  | 0.17415 | 74.883
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.10143 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.17459 | 61 | 61 | 6.1874 | 61 |  |  | 0.17459 | 10.65
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.10143 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.17459 | 95 | 95 | 9.636 | 95 |  |  | 0.17459 | 16.586
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.10143 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.17459 | 151 | 151 | 15.3162 | 151 |  |  | 0.17459 | 26.363
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.10343 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.17659 | 0 | 0 | 0 | 0 |  |  | 0.17659 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.10343 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.17659 | 0 | 0 | 0 | 0 |  |  | 0.17659 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.10451 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.17767 | 147 | 147 | 15.363 | 147 |  |  | 0.17767 | 26.1171
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.10451 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.17767 | 138 | 138 | 14.4224 | 138 |  |  | 0.17767 | 24.5181
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.10451 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.17767 | 146 | 146 | 15.2585 | 146 |  |  | 0.17767 | 25.9394
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.10451 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.17767 | 149 | 149 | 15.572 | 149 |  |  | 0.17767 | 26.4724
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.10451 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.17767 | 182 | 182 | 19.0208 | 182 |  |  | 0.17767 | 32.3355
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.10451 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.17767 | 203 | 203 | 21.2155 | 203 |  |  | 0.17767 | 36.0665
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.10567 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.17882 | 0 | 0 | 0 | 0 |  |  | 0.17882 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.10619 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.10619 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.10619 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.10842 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.18158 | 148 | 148 | 16.0459 | 148 |  |  | 0.18158 | 26.8732
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.10842 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.18158 | 148 | 148 | 16.0459 | 148 |  |  | 0.18158 | 26.8732
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.10842 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.18158 | 154 | 154 | 16.6964 | 154 |  |  | 0.18158 | 27.9626
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.10842 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.18158 | 293 | 293 | 31.7665 | 293 |  |  | 0.18158 | 53.2016
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.10859 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.18174 | 0 | 0 | 0 | 0 |  |  | 0.18174 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.11201 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.18517 | 0 | 0 | 0 | 0 |  |  | 0.18517 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.11201 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.18517 | 0 | 0 | 0 | 0 |  |  | 0.18517 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.11267 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.18583 | 223.9 | 223.9 | 25.2277 | 223.9 |  |  | 0.18583 | 41.6077
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.11267 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.18583 | 225 | 225 | 25.3516 | 225 |  |  | 0.18583 | 41.8121
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.11267 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.18583 | 224.6 | 224.6 | 25.3066 | 224.6 |  |  | 0.18583 | 41.7377
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.11267 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.18583 | 226.7 | 226.7 | 25.5432 | 226.7 |  |  | 0.18583 | 42.128
9000 | DECKR_G1 | 1 | South | YES | 0.11502 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.18818 | 321 | 321 | 36.9217 | 321 |  |  | 0.18818 | 60.4053
9001 | DECKR_G2 | 2 | South | YES | 0.11502 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.18818 | 426 | 426 | 48.9989 | 426 |  |  | 0.18818 | 80.164
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.11605 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.1892 | 132 | 132 | 15.3182 | 132 |  |  | 0.1892 | 24.975
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.11605 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.1892 | 139 | 139 | 16.1305 | 139 |  |  | 0.1892 | 26.2994
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.11605 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.1892 | 329 | 329 | 38.1795 | 329 |  |  | 0.1892 | 62.2483
9016 | SANDH_G1 | 1 | South | YES | 0.11611 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.18927 | 49 | 49 | 5.6894 | 49 |  |  | 0.18927 | 9.2741
9017 | SANDH_G2 | 2 | South | YES | 0.11611 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.18927 | 46 | 46 | 5.3411 | 46 |  |  | 0.18927 | 8.7063
9018 | SANDH_G3 | 3 | South | YES | 0.11611 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.18927 | 46 | 46 | 5.3411 | 46 |  |  | 0.18927 | 8.7063
9019 | SANDH_G4 | 4 | South | YES | 0.11611 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.18927 | 47 | 47 | 5.4572 | 47 |  |  | 0.18927 | 8.8956
9020 | SANDHG5A | 5A | South | YES | 0.11611 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.18927 | 155 | 155 | 17.9971 | 155 |  |  | 0.18927 | 29.3365
9021 | SANDHG5C | 5C | South | YES | 0.11611 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.18927 | 148 | 148 | 17.1843 | 148 |  |  | 0.18927 | 28.0116
9002 | DECKR_G3 | 3 | South | YES | 0.11697 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.19013 | 42 | 42 | 4.9129 | 42 |  |  | 0.19013 | 7.9855
9003 | DECKR_G4 | 4 | South | YES | 0.11697 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.19013 | 44 | 44 | 5.1469 | 44 |  |  | 0.19013 | 8.3658
9004 | DECKR_G5 | 5 | South | YES | 0.11697 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.19013 | 44 | 44 | 5.1469 | 44 |  |  | 0.19013 | 8.3658
9005 | DECKR_G6 | 6 | South | YES | 0.11697 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.19013 | 47 | 47 | 5.4978 | 47 |  |  | 0.19013 | 8.9362
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.11858 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.19174 | 0 | 436 | 51.7 | 436 |  |  | 0.19174 | 83.5966
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.11871 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.19187 | 0 | 606 | 71.9377 | 606 |  |  | 0.19187 | 116.2711
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.11871 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.19187 | 0 | 598 | 70.988 | 598 |  |  | 0.19187 | 114.7361
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.13412 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.20728 | 152.5 | 152.5 | 20.4531 | 152.5 |  |  | 0.20728 | 31.6097
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.13412 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.20728 | 149.5 | 149.5 | 20.0508 | 149.5 |  |  | 0.20728 | 30.9878
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.13412 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.20728 | 232.6 | 232.6 | 31.1961 | 232.6 |  |  | 0.20728 | 48.2125
3432 | SANDOW_4G | 4 | South | YES | 0.1349 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.20806 | 0 | 580 | 78.2426 | 580 |  |  | 0.20806 | 120.6739
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.13594 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.20909 | 158 | 158 | 21.4779 | 158 |  |  | 0.20909 | 33.0368
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.13594 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.20909 | 160 | 160 | 21.7498 | 160 |  |  | 0.20909 | 33.4549
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.13594 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.20909 | 175 | 175 | 23.7888 | 175 |  |  | 0.20909 | 36.5914
13432 | SANDOW_5G | 5 | South | YES | 0.1798 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.25295 | 0 | 581 | 104.4609 | 581 |  |  | 0.25295 | 146.9654
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Bound Gen
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | max of zone correlation | 0.073157 |  |  | Neg PTDF weight | Pos PTDF weight
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 |  |  |  |  | 0 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 |  |  |  |  | 0 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 |  |  |  |  | 0 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 |  |  | Weighted Shift Factors |  | 0 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 |  |  | South | 0.10565 | 0 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 |  |  | North | -0.073157 | 0 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 |  |  |  |  | 0 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | 1 | 0.073157 | 0 | 0 | 0 | 0 |  |  | 0.073157 | 0 | North |  |  |  | 0 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | 1 | 0.073157 | 0 | 0 |  |  |  |  | 0.073157 | 0 | Line Rating |  | 1072 |  | 0 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | 1 | 0.073157 | 15 | 15 | 0 | 15 |  |  | 0.073157 | 1.0974 | Impact Counter to Zone: |  | 0 |  | 0 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.016213 | 173 | 50 | 173 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 |  |  | 0% |  | 0 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.016213 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 |  |  |  |  | 0 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.016213 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | South |  |  |  | 0 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.016213 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | Line Rating |  | 1072 |  | 0 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.016213 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | 1 | 0.08937 | 0 | 0 |  |  |  |  | 0.08937 | 0 | Impact Counter to Zone: |  | 0 |  | 0 | 0
48886 | THW_5354 | C | Houston | YES | 0.019689 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.092846 | 57 | 57 |  |  |  |  | 0.092846 | 5.2922 |  |  | 0% |  | 0 | 0
48887 | THW_5556 | F | Houston | YES | 0.019689 | 45.6 | 5 | 57 |  | 1.0319 | GGT | 1 | 0.092846 | 57 | 57 |  |  |  |  | 0.092846 | 5.2922 |  |  |  |  | 0 | 0
48885 | THW_5152 | A | Houston | YES | 0.019689 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.092846 | 58 | 58 |  |  |  |  | 0.092846 | 5.3851 |  |  |  |  | 0 | 0
48886 | THW_5354 | D | Houston | YES | 0.019689 | 46.4 | 5 | 58 |  | 1.0319 | GGT | 1 | 0.092846 | 58 | 58 |  |  |  |  | 0.092846 | 5.3851 |  |  |  |  | 0 | 0
48885 | THW_5152 | B | Houston | YES | 0.019689 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.092846 | 59 | 59 |  |  |  |  | 0.092846 | 5.4779 |  |  |  |  | 0 | 0
48887 | THW_5556 | E | Houston | YES | 0.019689 | 47.2 | 5 | 59 |  | 1.0319 | GGT | 1 | 0.092846 | 59 | 59 |  |  |  |  | 0.092846 | 5.4779 |  |  |  |  | 0 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.019936 | 318.4 | 81 | 398 |  | 1.0362 | GSC | 1 | 0.093093 | 398 | 398 |  |  |  |  | 0.093093 | 37.0512 |  |  |  |  | 0 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.020115 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | 1 | 0.093272 | 158.9 | 158.9 |  |  |  |  | 0.093272 | 14.821 |  |  |  |  | 0 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.020115 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | 1 | 0.093272 | 161.4 | 161.4 |  |  |  |  | 0.093272 | 15.0542 |  |  |  |  | 0 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.020115 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | 1 | 0.093272 | 162.8 | 162.8 |  |  |  |  | 0.093272 | 15.1848 |  |  |  |  | 0 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.020115 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | 1 | 0.093272 | 269.2 | 269.2 |  |  |  |  | 0.093272 | 25.1089 |  |  |  |  | 0 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | GSC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 |  |  |  |  | 0 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 |  |  |  |  | 0 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.020685 | 172 | 0 | 172 | 0 | 1.027 | CC | 1 | 0.093842 | 172 | 172 |  |  |  |  | 0.093842 | 16.1409 |  |  |  |  | 0 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.020784 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | 1 | 0.093941 | 0 | 0 |  |  |  |  | 0.093941 | 0 |  |  |  |  | 0 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.020965 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 |  |  |  |  | 0 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.020965 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 |  |  |  |  | 0 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.020965 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 |  |  |  |  | 0 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.020965 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 |  |  |  |  | 0 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.020965 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 |  |  |  |  | 0 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.020965 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 |  |  |  |  | 0 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.020965 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | 1 | 0.094122 | 0 | 0 |  |  |  |  | 0.094122 | 0 |  |  |  |  | 0 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.020975 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | 1 | 0.094132 | 744 | 744 |  |  |  |  | 0.094132 | 70.0345 |  |  |  |  | 0 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.020987 | 15 | 0 | 15 |  | 1.021 | Cogen | 1 | 0.094144 | 0 | 0 |  |  |  |  | 0.094144 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 1 | Houston | YES | 0.020998 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | 1 | 0.094155 | 0 | 0 |  |  |  |  | 0.094155 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 2 | Houston | YES | 0.020998 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | 1 | 0.094155 | 0 | 0 |  |  |  |  | 0.094155 | 0 |  |  |  |  | 0 | 0
49803 | EXN_15GT | 1 | Houston | YES | 0.021324 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49804 | EXN_16GT | 2 | Houston | YES | 0.021324 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49805 | EXN_17GT | 3 | Houston | YES | 0.021324 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49826 | EXN938GT | 5 | Houston | YES | 0.021324 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49828 | EXN941GT | 10 | Houston | YES | 0.021324 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49829 | EXN942GT | 11 | Houston | YES | 0.021324 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49830 | EXN943GT | 12 | Houston | YES | 0.021324 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49831 | EXN944GT | 13 | Houston | YES | 0.021324 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49832 | EXN945GT | 9 | Houston | YES | 0.021324 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49837 | EXN_GT | 4 | Houston | YES | 0.021324 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
49838 | EXN_14GT | 14 | Houston | YES | 0.021324 | 140 | 0 | 148 |  | 1.0326 | Cogen | 1 | 0.094481 | 0 | 0 |  |  |  |  | 0.094481 | 0 |  |  |  |  | 0 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.021417 | 0 | 0 | 12 |  | 1.043 | GGT | 1 | 0.094574 | 12 | 12 |  |  |  |  | 0.094574 | 1.1349 |  |  |  |  | 0 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.021662 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | 1 | 0.094819 | 746 | 746 |  |  |  |  | 0.094819 | 70.7353 |  |  |  |  | 0 | 0
48875 | THW_3132 | B | Houston | YES | 0.022175 | 53 | 5 | 53 | 0 | 1.0435 | CC | 1 | 0.095332 | 53 | 53 |  |  |  |  | 0.095332 | 5.0526 |  |  |  |  | 0 | 0
48875 | THW_3132 | A | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 |  |  |  |  | 0 | 0
48877 | THW_3334 | C | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 |  |  |  |  | 0 | 0
48879 | THW_4142 | F | Houston | YES | 0.022175 | 55 | 5 | 55 | 0 | 1.0435 | CC | 1 | 0.095332 | 55 | 55 |  |  |  |  | 0.095332 | 5.2433 |  |  |  |  | 0 | 0
48879 | THW_4142 | E | Houston | YES | 0.022175 | 56 | 5 | 56 | 0 | 1.0435 | CC | 1 | 0.095332 | 56 | 56 |  |  |  |  | 0.095332 | 5.3386 |  |  |  |  | 0 | 0
48877 | THW_3334 | D | Houston | YES | 0.022175 | 57 | 5 | 57 | 0 | 1.0435 | CC | 1 | 0.095332 | 57 | 57 |  |  |  |  | 0.095332 | 5.4339 |  |  |  |  | 0 | 0
48881 | THW_4344 | G | Houston | YES | 0.022175 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.095332 | 58 | 58 |  |  |  |  | 0.095332 | 5.5293 |  |  |  |  | 0 | 0
48881 | THW_4344 | H | Houston | YES | 0.022175 | 58 | 5 | 58 | 0 | 1.0435 | CC | 1 | 0.095332 | 58 | 58 |  |  |  |  | 0.095332 | 5.5293 |  |  |  |  | 0 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.022175 | 107 | 19 | 107 | 0 | 1.0435 | CC | 1 | 0.095332 | 107 | 107 |  |  |  |  | 0.095332 | 10.2006 |  |  |  |  | 0 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.022175 | 108 | 19 | 108 | 0 | 1.0435 | CC | 1 | 0.095332 | 108 | 108 |  |  |  |  | 0.095332 | 10.2959 |  |  |  |  | 0 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.022792 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | 1 | 0.095949 | 0 | 0 |  |  |  |  | 0.095949 | 0 |  |  |  |  | 0 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.022792 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | 1 | 0.095949 | 0 | 0 |  |  |  |  | 0.095949 | 0 |  |  |  |  | 0 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.022853 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.09601 | 39 | 39 |  |  |  |  | 0.09601 | 3.7444 |  |  |  |  | 0 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.022853 | 39 | 0 | 39 | 0 | 1.0362 | GGT | 1 | 0.09601 | 39 | 39 |  |  |  |  | 0.09601 | 3.7444 |  |  |  |  | 0 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.022853 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.09601 | 42 | 42 |  |  |  |  | 0.09601 | 4.0324 |  |  |  |  | 0 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.022853 | 42 | 0 | 42 | 0 | 1.0362 | GGT | 1 | 0.09601 | 42 | 42 |  |  |  |  | 0.09601 | 4.0324 |  |  |  |  | 0 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.022953 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | 1 | 0.09611 | 0 | 0 |  |  |  |  | 0.09611 | 0 |  |  |  |  | 0 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.023372 | 71 | 34.5 | 71 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 |  |  |  |  | 0 | 0
48821 | SHELLG2 | 2 | Houston | YES | 0.023372 | 72 | 34.5 | 72 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.023372 | 30 | 0 | 30 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.023372 | 39 | 0 | 39 |  | 1.029 | Cogen | 1 | 0.096529 | 0 | 0 |  |  |  |  | 0.096529 | 0 |  |  |  |  | 0 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.023677 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 |  |  |  |  | 0 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.023677 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 |  |  |  |  | 0 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.023677 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | 1 | 0.096834 | 0 | 0 |  |  |  |  | 0.096834 | 0 |  |  |  |  | 0 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.023677 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | 1 | 0.096834 | 228 | 228 |  |  |  |  | 0.096834 | 22.0783 |  |  |  |  | 0 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.023683 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 |  |  |  |  | 0 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.023683 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 |  |  |  |  | 0 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.023683 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 |  |  |  |  | 0 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.023683 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | 1 | 0.09684 | 0 | 0 |  |  |  |  | 0.09684 | 0 |  |  |  |  | 0 | 0
48845 | SOL_GT1 | 1 | Houston | YES | 0.023686 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | 1 | 0.096843 | 16.2 | 16.2 |  |  |  |  | 0.096843 | 1.5689 |  |  |  |  | 0 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.02369 | 170.4 | 35 | 213 |  | 1.0326 | GST | 1 | 0.096847 | 213 | 213 |  |  |  |  | 0.096847 | 20.6285 |  |  |  |  | 0 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.023742 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | 1 | 0.096899 | 0 | 0 |  |  |  |  | 0.096899 | 0 |  |  |  |  | 0 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.023742 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | 1 | 0.096899 | 0 | 0 |  |  |  |  | 0.096899 | 0 |  |  |  |  | 0 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.023747 | 132 | 26 | 165 | 0 | 1.0217 | GST | 1 | 0.096904 | 165 | 165 |  |  |  |  | 0.096904 | 15.9892 |  |  |  |  | 0 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.023763 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | 1 | 0.09692 | 176 | 176 |  |  |  |  | 0.09692 | 17.058 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | 0.023775 | 0 | 0 | 12 |  | 1.014 | GGT | 1 | 0.096932 | 12 | 12 |  |  |  |  | 0.096932 | 1.1632 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | 0.023775 | 0 | 0 | 18 |  | 1.014 | GGT | 1 | 0.096932 | 18 | 18 |  |  |  |  | 0.096932 | 1.7448 |  |  |  |  | 0 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.023993 | 26 | 0 | 35 |  | 1 | Cogen | 1 | 0.09715 | 0 | 0 |  |  |  |  | 0.09715 | 0 |  |  |  |  | 0 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.024207 | 157 | 98 | 157 | 0 | 1.0319 | CC | 1 | 0.097364 | 157 | 157 |  |  |  |  | 0.097364 | 15.2862 |  |  |  |  | 0 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.024207 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | 1 | 0.097364 | 157.1 | 157.1 |  |  |  |  | 0.097364 | 15.296 |  |  |  |  | 0 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.024207 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | 1 | 0.097364 | 157.5 | 157.5 |  |  |  |  | 0.097364 | 15.3349 |  |  |  |  | 0 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.024207 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | 1 | 0.097364 | 163.2 | 163.2 |  |  |  |  | 0.097364 | 15.8899 |  |  |  |  | 0 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.024207 | 282 | 0 | 282 | 0 | 1.0319 | CC | 1 | 0.097364 | 282 | 282 |  |  |  |  | 0.097364 | 27.4568 |  |  |  |  | 0 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.024434 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | 1 | 0.097591 | 0 | 0 |  |  |  |  | 0.097591 | 0 |  |  |  |  | 0 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.024434 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | 1 | 0.097591 | 0 | 0 |  |  |  |  | 0.097591 | 0 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | B | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | A | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | C | Houston | YES | 0.024725 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | 1 | 0.097882 | 47 | 47 |  |  |  |  | 0.097882 | 4.6005 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | F | Houston | YES | 0.024725 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | 1 | 0.097882 | 54 | 54 |  |  |  |  | 0.097882 | 5.2857 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | D | Houston | YES | 0.024725 | 44 | 20 | 55 | 0 | 1.0362 | GGT | 1 | 0.097882 | 55 | 55 |  |  |  |  | 0.097882 | 5.3835 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | E | Houston | YES | 0.024725 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | 1 | 0.097882 | 57 | 57 |  |  |  |  | 0.097882 | 5.5793 |  |  |  |  | 0 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.025309 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 |  |  |  |  | 0 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.025309 | 62 | 0 | 62 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 |  |  |  |  | 0 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.025309 | 67 | 0 | 67 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 |  |  |  |  | 0 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.025309 | 65 | 0 | 65 |  | 1.0362 | Cogen | 1 | 0.098466 | 0 | 0 |  |  |  |  | 0.098466 | 0 |  |  |  |  | 0 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.025774 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 |  |  |  |  | 0 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.025774 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 |  |  |  |  | 0 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.025774 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 |  |  |  |  | 0 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.025774 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 |  |  |  |  | 0 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.025774 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | 1 | 0.098931 | 0 | 0 |  |  |  |  | 0.098931 | 0 |  |  |  |  | 0 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | 0.026988 | 0 | 72 | 459 |  | 1.0362 | GSC | 1 | 0.10015 | 0 | 0 |  |  |  |  | 0.10015 | 0 |  |  |  |  | 0 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.028729 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.028729 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.028729 | 53 | 0 | 53 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.028729 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.028729 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.028729 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.028729 | 96 | 0 | 96 |  | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.028729 | 244 | 0 | 244 | 0 | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.028729 | 40 | 0 | 40 |  | 1.005 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.028729 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.028729 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.028729 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.028729 | 103 | 59 | 103 | 0 | 1 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.028729 | 32 | 10 | 32 | 0 | 0.985 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.028729 | 30 | 10 | 30 | 0 | 0.985 | Cogen | 1 | 0.10189 | 0 | 0 |  |  |  |  | 0.10189 | 0 |  |  |  |  | 0 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.032833 | 0 | 0 | 13 |  | 1.05 | GGT | 1 | 0.10599 | 13 | 13 |  |  |  |  | 0.10599 | 1.3779 |  |  |  |  | 0 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.032833 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.10599 | 166 | 166 |  |  |  |  | 0.10599 | 17.5944 |  |  |  |  | 0 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.032833 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | 1 | 0.10599 | 166 | 166 |  |  |  |  | 0.10599 | 17.5944 |  |  |  |  | 0 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.032833 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | 1 | 0.10599 | 248 | 248 |  |  |  |  | 0.10599 | 26.2856 |  |  |  |  | 0 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.032833 | 546 | 217 | 546 | 0 | 1.0362 | GSC | 1 | 0.10599 | 546 | 546 |  |  |  |  | 0.10599 | 57.8708 |  |  |  |  | 0 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.032833 | 578.7 | 278 | 654 | 0 | 0.985 | LIGCO | 1 | 0.10599 | 0 | 654 |  |  |  |  | 0.10599 | 69.3177 |  |  |  |  | 0 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.032933 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | 1 | 0.10609 | 0 | 0 |  |  |  |  | 0.10609 | 0 |  |  |  |  | 0 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.03385 | 166.4 | 0 | 166.4 |  | 1.035 | CC | 1 | 0.10701 | 166.4 | 166.4 |  |  |  |  | 0.10701 | 17.806 |  |  |  |  | 0 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.03385 | 167.7 | 0 | 167.7 |  | 1.035 | CC | 1 | 0.10701 | 167.7 | 167.7 |  |  |  |  | 0.10701 | 17.9451 |  |  |  |  | 0 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.03385 | 252.4 | 0 | 252.4 |  | 1.035 | CC | 1 | 0.10701 | 252.4 | 252.4 |  |  |  |  | 0.10701 | 27.0087 |  |  |  |  | 0 | 0
48730 | MNS_GT | 1 | Houston | YES | 0.033879 | 43 | 0 | 46.1 |  | 1.029 | Cogen | 1 | 0.10704 | 0 | 0 |  |  |  |  | 0.10704 | 0 |  |  |  |  | 0 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.033903 | 564 | 277 | 564 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 564 |  |  |  |  | 0.10706 | 60.3821 |  |  |  |  | 0 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.033903 | 603 | 275 | 603 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 603 |  |  |  |  | 0.10706 | 64.5574 |  |  |  |  | 0 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.033903 | 651 | 280 | 651 |  | 1.035 | LIGCO | 1 | 0.10706 | 0 | 651 |  |  |  |  | 0.10706 | 69.6963 |  |  |  |  | 0 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.04015 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0 |  |  |  |  | 0 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.04015 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0 |  |  |  |  | 0 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.04015 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0 |  |  |  |  | 0 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.04015 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | 1 | 0.11331 | 0 | 0 |  |  |  |  | 0.11331 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.041916 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | 1 | 0.11507 | 0 | 0 |  |  |  |  | 0.11507 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.041916 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | 1 | 0.11507 | 0 | 0 |  |  |  |  | 0.11507 | 0 |  |  |  |  | 0 | 0
49851 | DOW17000 | 37 | Houston | YES | 0.044148 | 39 | 0 | 62 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49858 | DOW38100 | 31 | Houston | YES | 0.044148 | 45 | 0 | 71.4 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49859 | DOW38200 | 33 | Houston | YES | 0.044148 | 28 | 0 | 45 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49860 | DOW38300 | 32 | Houston | YES | 0.044148 | 63 | 0 | 101 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49862 | DOW39100 | 36 | Houston | YES | 0.044148 | 54 | 0 | 86 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49863 | DOW39200 | 35 | Houston | YES | 0.044148 | 55 | 0 | 88 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49865 | DOW41000 | 41 | Houston | YES | 0.044148 | 31 | 0 | 50 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49866 | DOW42000 | 42 | Houston | YES | 0.044148 | 11 | 0 | 18 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49869 | DOW49000 | 45 | Houston | YES | 0.044148 | 59 | 0 | 94 |  | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49870 | DOW61000 | 61 | Houston | YES | 0.044148 | 44 | 0 | 70 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49871 | DOW62000 | 62 | Houston | YES | 0.044148 | 40 | 0 | 63 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49872 | DOW63000 | 63 | Houston | YES | 0.044148 | 45 | 0 | 72 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49873 | DOW64000 | 64 | Houston | YES | 0.044148 | 41 | 0 | 64.8 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49876 | DOW65000 | 65 | Houston | YES | 0.044148 | 63 | 0 | 101 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49877 | DOW66000 | 66 | Houston | YES | 0.044148 | 61 | 0 | 97 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49878 | DOW67000 | 67 | Houston | YES | 0.044148 | 65 | 0 | 103 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49882 | DOW81000 | 81 | Houston | YES | 0.044148 | 47 | 0 | 76 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49884 | DOW82000 | 82 | Houston | YES | 0.044148 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49885 | DOW83000 | 83 | Houston | YES | 0.044148 | 51 | 0 | 80 | 0 | 1 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
49886 | DOW84000 | 84 | Houston | YES | 0.044148 | 107 | 0 | 171 | 0 | 0.98 | Cogen | 1 | 0.11731 | 0 | 0 |  |  |  |  | 0.11731 | 0 |  |  |  |  | 0 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.045618 | 33 | 13 | 33 | 0 | 1.03 | Hydro | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0 |  |  |  |  | 0 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.045618 | 25 | 13 | 25 | 0 | 1.03 | Hydro | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0 |  |  |  |  | 0 | 0
88253 | HAMILTON | F | South | YES | 0.045618 | 0 | 0 | 0 | 0 | 1.04 | BLT | 1 | 0.11878 | 0 | 0 | 0 | 0 |  |  | 0.11878 | 0 |  |  |  |  | 0 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | -0.014565 | 84 | 25 | 105 | 0 | 1.035 | GST | -1 | 0.12021 | 105 | 105 |  |  | -1.5293 | 105 | -0.12021 | -12.6223 |  |  |  |  | 0 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | -0.014565 | 0 | 2 | 48 |  | 1.015 | GST | -1 | 0.12021 | 48 | 48 |  |  | -0.69912 | 48 | -0.12021 | -5.7702 |  |  |  |  | 0 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | -0.014565 | 46 | 2 | 46 | 0 | 1.015 | GST | -1 | 0.12021 | 46 | 46 |  |  | -0.66999 | 46 | -0.12021 | -5.5298 |  |  |  |  | 0 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | -0.015218 | 380 | 0 | 380 | 0 | 1.0319 | CC | -1 | 0.12087 | 380 | 380 |  |  | -5.7828 | 380 | -0.12087 | -45.929 |  |  |  |  | 0 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | -0.015218 | 159 | 0 | 159 | 0 | 1.0319 | CC | -1 | 0.12087 | 159 | 159 |  |  | -2.4197 | 159 | -0.12087 | -19.2176 |  |  |  |  | 0 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | -0.015218 | 158 | 0 | 158 | 0 | 1.0319 | CC | -1 | 0.12087 | 158 | 158 |  |  | -2.4044 | 158 | -0.12087 | -19.0968 |  |  |  |  | 0 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | -0.015218 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | -1 | 0.12087 | 154.2 | 154.2 |  |  | -2.3466 | 154.2 | -0.12087 | -18.6375 |  |  |  |  | 0 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | -0.016796 | 13.6 | 4 | 17 |  | 1.028 | GGT | -1 | 0.12244 | 17 | 17 |  |  | -0.28553 | 17 | -0.12244 | -2.0815 |  |  |  |  | 0 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | -0.016796 | 0 | 5 | 12 |  | 1 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0 |  |  |  |  | 0 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | -0.016796 | 0 | 12 | 51 |  | 1.028 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0 |  |  |  |  | 0 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | -0.016796 | 0 | 5 | 22 |  | 1.031 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0 |  |  |  |  | 0 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | -0.016796 | 0 | 5 | 25 |  | 1.031 | GST | -1 | 0.12244 | 0 | 0 |  |  | 0 | 0 | -0.12244 | 0 |  |  |  |  | 0 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | -0.016957 | 32 | 0 | 32 |  | 1.02 | GST | -1 | 0.1226 | 32 | 32 |  |  | -0.54262 | 32 | -0.1226 | -3.9234 |  |  |  |  | 0 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.052688 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | 1 | 0.12585 | 0 | 0 |  |  |  |  | 0.12585 | 0 |  |  |  |  | 0 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | -0.021238 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | -1 | 0.12689 | 0 | 463 |  |  | 0 | 0 | -0.12689 | 0 |  |  |  |  | 0 | 0
48731 | CBE_GT1 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848 |  |  |  |  | 0 | 0
48732 | CBE_GT2 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848 |  |  |  |  | 0 | 0
48734 | CBE_GT3 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848 |  |  |  |  | 0 | 0
48735 | CBE_GT4 | 1 | Houston | YES | 0.05559 | 76 | 0 | 76 | 0 | 1.029 | CC | 1 | 0.12875 | 76 | 76 |  |  |  |  | 0.12875 | 9.7848 |  |  |  |  | 0 | 0
48733 | CBE_ST12 | 1 | Houston | YES | 0.05559 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.12875 | 105 | 105 |  |  |  |  | 0.12875 | 13.5185 |  |  |  |  | 0 | 0
48736 | CBE_ST34 | 1 | Houston | YES | 0.05559 | 105 | 0 | 105 | 0 | 1.029 | CC | 1 | 0.12875 | 105 | 105 |  |  |  |  | 0.12875 | 13.5185 |  |  |  |  | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.05598 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0 |  |  |  |  | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.05598 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0 |  |  |  |  | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.05598 | 0 | 0 | 15 |  | 1 | Hydro | 1 | 0.12914 | 0 | 0 | 0 | 0 |  |  | 0.12914 | 0 |  |  |  |  | 0 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | 0.056151 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | 1 | 0.12931 | 0 | 0 |  |  |  |  | 0.12931 | 0 |  |  |  |  | 0 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | 0.056151 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | 1 | 0.12931 | 0 | 0 |  |  |  |  | 0.12931 | 0 |  |  |  |  | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.057715 | 0 | 0 | 13.7 |  | 1 | Hydro | 1 | 0.13087 | 0 | 0 | 0 | 0 |  |  | 0.13087 | 0 |  |  |  |  | 0 | 0
8262 | ELPS | 1 | South | YES | 0.058475 | 6 | 6 | 6 | 0 | 1.15 | Hydro | 1 | 0.13163 | 0 | 0 | 0 | 0 |  |  | 0.13163 | 0 |  |  |  |  | 0 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | 0.073077 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | 1 | 0.14623 | 423.3 | 423.3 | 30.9335 | 423.3 |  |  | 0.14623 | 61.901 |  |  |  |  | 0 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | 0.073215 | 0 | 0 | 29 |  | 1 | Hydro | 1 | 0.14637 | 0 | 0 | 0 | 0 |  |  | 0.14637 | 0 |  |  |  |  | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | 0.073215 | 0 | 0 | 29.7 |  | 1 | Hydro | 1 | 0.14637 | 0 | 0 | 0 | 0 |  |  | 0.14637 | 0 |  |  |  |  | 0 | 0
39960 | TNTNPONE_18 | 1 | North | YES | -0.041618 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | -1 | 0.14727 | 0 | 152.3 |  |  | 0 | 0 | -0.14727 | 0 |  |  |  |  | 0 | 0
39970 | TNTNPONE_28 | 1 | North | YES | -0.041618 | 153 | 30 | 153 |  | 1.04 | LIGCO | -1 | 0.14727 | 0 | 153 |  |  | 0 | 0 | -0.14727 | 0 |  |  |  |  | 0 | 0
60202 | FRNDDRCS | F | West | YES | -0.042109 | 0 | 0 | 0 | 0 | 0.9985 | AVR | -1 | 0.14776 | 0 | 0 |  |  |  |  | -0.14776 | 0 |  |  |  |  | 0 | 0
8134 | FOR #1 | 1 | South | YES | 0.077991 | 54.1 | 45 | 79 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
8138 | FOR #2 | 2 | South | YES | 0.077991 | 63.1 | 45 | 81 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
8153 | FOR #3 | 3 | South | YES | 0.077991 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
8154 | FOR #4 | 4 | South | YES | 0.077991 | 63.1 | 60 | 80 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
8155 | FOR #5 | 5 | South | YES | 0.077991 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
8156 | FOR #6 | 6 | South | YES | 0.077991 | 24.9 | 5 | 25 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
8157 | FOR #7 | 7 | South | YES | 0.077991 | 28.8 | 5 | 46 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
80051 | FOR #8 | 8 | South | YES | 0.077991 | 28 | 28 | 28 |  | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
80052 | FOR #9 | 9 | South | YES | 0.077991 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
80053 | FOR #10 | 10 | South | YES | 0.077991 | 68.4 | 45 | 75 | 0 | 1 | Cogen | 1 | 0.15115 | 0 | 0 | 0 | 0 |  |  | 0.15115 | 0 |  |  |  |  | 0 | 0
80226 | ALCOA G | 1 | South | YES | 0.078601 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | 1 | 0.15176 | 0 | 0 | 0 | 0 |  |  | 0.15176 | 0 |  |  |  |  | 0 | 0
8147 | UCAR #2 | 10 | South | YES | 0.080583 | 18.2 | 0 | 28 |  | 1 | Cogen | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 |  |  |  |  | 0 | 0
8148 | UCAR #1 | 2 | South | YES | 0.080583 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 9 | South | YES | 0.080583 | 15 | 0 | 15 | 0 | 1.003 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 8 | South | YES | 0.080583 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 |  |  |  |  | 0 | 0
80138 | CSDR7 | 7 | South | YES | 0.080583 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 6 | South | YES | 0.080583 | 0 | 0 | 39 |  | 1.0033 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 5 | South | YES | 0.080583 | 15 | 0 | 15 |  | 1.0033 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 |  |  |  |  | 0 | 0
80140 | CSDR11 | 11 | South | YES | 0.080584 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | 1 | 0.15374 | 0 | 0 | 0 | 0 |  |  | 0.15374 | 0 |  |  |  |  | 0 | 0
80227 | AIRCO G | 1 | South | YES | 0.080868 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | 1 | 0.15403 | 0 | 0 | 0 | 0 |  |  | 0.15403 | 0 |  |  |  |  | 0 | 0
80224 | VISTRONG1 | 1 | South | YES | 0.081411 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | 1 | 0.15457 | 0 | 0 | 0 | 0 |  |  | 0.15457 | 0 |  |  |  |  | 0 | 0
80225 | VISTRONG2 | 2 | South | YES | 0.081411 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | 1 | 0.15457 | 0 | 0 | 0 | 0 |  |  | 0.15457 | 0 |  |  |  |  | 0 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | 0.081623 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.15478 | 0 | 0 | 0 | 0 |  |  | 0.15478 | 0 |  |  |  |  | 0 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | 0.081623 | 0 | 0 | 18 |  | 1 | Hydro | 1 | 0.15478 | 0 | 0 | 0 | 0 |  |  | 0.15478 | 0 |  |  |  |  | 0 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | 0.082165 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.15532 | 11 | 11 | 0.90382 | 11 |  |  | 0.15532 | 1.7085 |  |  |  |  | 0 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | 0.082165 | 0 | 1 | 11 |  | 1.0223 | GGT | 1 | 0.15532 | 11 | 11 | 0.90382 | 11 |  |  | 0.15532 | 1.7085 |  |  |  |  | 0 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | 0.082165 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | 1 | 0.15532 | 22 | 22 | 1.8076 | 22 |  |  | 0.15532 | 3.4171 |  |  |  |  | 0 | 0
80265 | LARECU40A | 4 | South | YES | 0.082565 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.15572 | 100 | 100 | 8.2565 | 100 |  |  | 0.15572 | 15.5722 |  |  |  |  | 0 | 0
80266 | LARECU50A | 5 | South | YES | 0.082565 | 80 | 0 | 100 |  | 1.039 | GGT | 1 | 0.15572 | 100 | 100 | 8.2565 | 100 |  |  | 0.15572 | 15.5722 |  |  |  |  | 0 | 0
80012 | LAR | F | South | YES | 0.082566 | 0 | 0 | 0 | 0 | 1.04 | DCTie | 1 | 0.15572 | 0 | 0 | 0 | 0 |  |  | 0.15572 | 0 |  |  |  |  | 0 | 0
48721 | LEG_1___1 | 1 | North | YES | -0.050274 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | -1 | 0.15592 | 0 | 827 |  |  | 0 | 0 | -0.15592 | 0 |  |  |  |  | 0 | 0
48722 | LEG_2___2 | 2 | North | YES | -0.050274 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | -1 | 0.15592 | 0 | 819 |  |  | 0 | 0 | -0.15592 | 0 |  |  |  |  | 0 | 0
5509 | RAYBURNCC10 | 1 | South | YES | 0.082849 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | 1 | 0.15601 | 37.3 | 37.3 | 3.0903 | 37.3 |  |  | 0.15601 | 5.819 |  |  |  |  | 0 | 0
5511 | RAYBURNCC7 | 1 | South | YES | 0.082849 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | 1 | 0.15601 | 47.5 | 47.5 | 3.9353 | 47.5 |  |  | 0.15601 | 7.4103 |  |  |  |  | 0 | 0
5508 | RAYBURNCC9 | 1 | South | YES | 0.082849 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | 1 | 0.15601 | 47.7 | 47.7 | 3.9519 | 47.7 |  |  | 0.15601 | 7.4415 |  |  |  |  | 0 | 0
5512 | RAYBURNCC8 | 1 | South | YES | 0.082849 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | 1 | 0.15601 | 49.3 | 49.3 | 4.0845 | 49.3 |  |  | 0.15601 | 7.6911 |  |  |  |  | 0 | 0
8066 | DUP1V#1 | 1 | South | YES | 0.082883 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | 1 | 0.15604 | 0 | 0 | 0 | 0 |  |  | 0.15604 | 0 |  |  |  |  | 0 | 0
8926 | LGE_GT10A | 1 | South | YES | 0.083143 | 158 | 0 | 158 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 |  |  |  |  | 0 | 0
8927 | LGE_GT20A | 2 | South | YES | 0.083143 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 |  |  |  |  | 0 | 0
8928 | LGE_STG0A | 3 | South | YES | 0.083143 | 100 | 0 | 100 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 |  |  |  |  | 0 | 0
8930 | ICPGN10A | 1 | South | YES | 0.083143 | 149 | 0 | 149 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 |  |  |  |  | 0 | 0
8931 | ICPGN20A | 2 | South | YES | 0.083143 | 150 | 0 | 150 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 |  |  |  |  | 0 | 0
8932 | ICPGN30A | 3 | South | YES | 0.083143 | 127 | 0 | 127 | 0 | 1.03 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 |  |  |  |  | 0 | 0
80223 | REYSHR G | 1 | South | YES | 0.083143 | 12 | 0 | 12 | 0 | 1.032 | Cogen | 1 | 0.1563 | 0 | 0 | 0 | 0 |  |  | 0.1563 | 0 |  |  |  |  | 0 | 0
88299 | ZAPATA | F | South | YES | 0.083317 | 0 | 0 | 0 | 0 | 1.02 | BLT | 1 | 0.15647 | 0 | 0 | 0 | 0 |  |  | 0.15647 | 0 |  |  |  |  | 0 | 0
8173 | VICEC51A | 5 | South | YES | 0.083722 | 144 | 18 | 144 | 0 | 1.025 | CC | 1 | 0.15688 | 144 | 144 | 12.056 | 144 |  |  | 0.15688 | 22.5906 |  |  |  |  | 0 | 0
8174 | VICEC61A | 6 | South | YES | 0.083722 | 188 | 42 | 188 | 0 | 1.025 | CC | 1 | 0.15688 | 188 | 188 | 15.7397 | 188 |  |  | 0.15688 | 29.4933 |  |  |  |  | 0 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | 0.083825 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0 |  |  |  |  | 0 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 0.083825 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0 |  |  |  |  | 0 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 0.083825 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0 |  |  |  |  | 0 | 0
88508 | FALFURRI | F | South | YES | 0.083826 | 0 | 0 | 0 | 0 | 1 | AVR | 1 | 0.15698 | 0 | 0 | 0 | 0 |  |  | 0.15698 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | MB | South | YES | 0.08386 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.15702 | 0 | 0 | 0 | 0 |  |  | 0.15702 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | 7 | South | YES | 0.08386 | 0 | 81 | 367 |  | 1.0298 | GST | 1 | 0.15702 | 367 | 367 | 30.7766 | 367 |  |  | 0.15702 | 57.6254 |  |  |  |  | 0 | 0
8560 | CNOPGT1 | 1 | South | YES | 0.083868 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0 |  |  |  |  | 0 | 0
8561 | CNOPGT2 | 2 | South | YES | 0.083868 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0 |  |  |  |  | 0 | 0
8562 | CNOPST1 | 3 | South | YES | 0.083868 | 153 | 0 | 153 | 0 | 1.03 | Cogen | 1 | 0.15703 | 0 | 0 | 0 | 0 |  |  | 0.15703 | 0 |  |  |  |  | 0 | 0
8456 | COSW#1 | 1 | South | YES | 0.083909 | 20 | 0 | 20 | 0 | 1.027 | Cogen | 1 | 0.15707 | 0 | 0 | 0 | 0 |  |  | 0.15707 | 0 |  |  |  |  | 0 | 0
8457 | COSW#2 | 2 | South | YES | 0.083909 | 14 | 0 | 14 | 0 | 1.027 | Cogen | 1 | 0.15707 | 0 | 0 | 0 | 0 |  |  | 0.15707 | 0 |  |  |  |  | 0 | 0
8459 | B_DAVIS0B | MB | South | YES | 0.084009 | 0 | 50 | 339 |  | 1.03 | GSC | 1 | 0.15717 | 0 | 0 | 0 | 0 |  |  | 0.15717 | 0 |  |  |  |  | 0 | 0
8460 | B_DAVIS0A | MB | South | YES | 0.084009 | 0 | 50 | 340 |  | 1.03 | GSC | 1 | 0.15717 | 0 | 0 | 0 | 0 |  |  | 0.15717 | 0 |  |  |  |  | 0 | 0
80263 | B_DAVIS31A | 3 | South | YES | 0.084009 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.15717 | 180 | 180 | 15.1216 | 180 |  |  | 0.15717 | 28.29 |  |  |  |  | 0 | 0
80264 | B_DAVIS41A | 4 | South | YES | 0.084009 | 0 | 0 | 180 |  | 1.0366 | CC | 1 | 0.15717 | 180 | 180 | 15.1216 | 180 |  |  | 0.15717 | 28.29 |  |  |  |  | 0 | 0
8506 | VAL #1 | 1 | South | YES | 0.084042 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.1572 | 0 | 0 | 0 | 0 |  |  | 0.1572 | 0 |  |  |  |  | 0 | 0
8507 | VAL #2 | 2 | South | YES | 0.084042 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | 1 | 0.1572 | 0 | 0 | 0 | 0 |  |  | 0.1572 | 0 |  |  |  |  | 0 | 0
8461 | KOCH_UP0A | 1 | South | YES | 0.084115 | 38 | 0 | 38 | 0 | 1.012 | Cogen | 1 | 0.15727 | 0 | 0 | 0 | 0 |  |  | 0.15727 | 0 |  |  |  |  | 0 | 0
8511 | OXY_CC0A | 1 | South | YES | 0.084121 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | 1 | 0.15728 | 0 | 0 | 0 | 0 |  |  | 0.15728 | 0 |  |  |  |  | 0 | 0
8933 | FGNTS001 | 1 | South | YES | 0.084356 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | 1 | 0.15751 | 146.5 | 146.5 | 12.3582 | 146.5 |  |  | 0.15751 | 23.0757 |  |  |  |  | 0 | 0
8934 | FGNTS101 | 2 | South | YES | 0.084356 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | 1 | 0.15751 | 147.9 | 147.9 | 12.4763 | 147.9 |  |  | 0.15751 | 23.2962 |  |  |  |  | 0 | 0
8935 | FGNTS201 | 3 | South | YES | 0.084356 | 173 | 0 | 173 | 0 | 1.03 | CC | 1 | 0.15751 | 173 | 173 | 14.5936 | 173 |  |  | 0.15751 | 27.2498 |  |  |  |  | 0 | 0
8517 | CELANEBI0A | 1 | South | YES | 0.084407 | 29 | 0 | 29 | 0 | 1.02 | Cogen | 1 | 0.15756 | 0 | 0 | 0 | 0 |  |  | 0.15756 | 0 |  |  |  |  | 0 | 0
8982 | HECN2 | 2 | South | YES | 0.084446 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | 1 | 0.1576 | 144.1 | 144.1 | 12.1687 | 144.1 |  |  | 0.1576 | 22.7107 |  |  |  |  | 0 | 0
8981 | HECN1 | 1 | South | YES | 0.084446 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | 1 | 0.1576 | 144.8 | 144.8 | 12.2278 | 144.8 |  |  | 0.1576 | 22.821 |  |  |  |  | 0 | 0
8983 | HECN3 | 3 | South | YES | 0.084446 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | 1 | 0.1576 | 171.9 | 171.9 | 14.5163 | 171.9 |  |  | 0.1576 | 27.092 |  |  |  |  | 0 | 0
8936 | MVGN#1 | 1 | South | YES | 0.084446 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | 1 | 0.1576 | 216.6 | 216.6 | 18.291 | 216.6 |  |  | 0.1576 | 34.1369 |  |  |  |  | 0 | 0
8937 | MVGN#2 | 2 | South | YES | 0.084446 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | 1 | 0.1576 | 216.7 | 216.7 | 18.2994 | 216.7 |  |  | 0.1576 | 34.1527 |  |  |  |  | 0 | 0
8938 | MVGN#3 | 3 | South | YES | 0.084446 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | 1 | 0.1576 | 250.9 | 250.9 | 21.1875 | 250.9 |  |  | 0.1576 | 39.5427 |  |  |  |  | 0 | 0
80003 | MILHWYS | F | South | YES | 0.084476 | 0 | 0 | 0 | 0 | 1.0168 | AVR | 1 | 0.15763 | 0 | 0 | 0 | 0 |  |  | 0.15763 | 0 |  |  |  |  | 0 | 0
5933 | SI_RAY6 | 6 | South | YES | 0.084476 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | 1 | 0.15763 | 19.3 | 19.3 | 1.6304 | 19.3 |  |  | 0.15763 | 3.0423 |  |  |  |  | 0 | 0
5932 | SI_RAY9 | 9 | South | YES | 0.084476 | 32 | 32 | 38 | 0 | 1.035 | CC | 1 | 0.15763 | 38 | 38 | 3.2101 | 38 |  |  | 0.15763 | 5.9901 |  |  |  |  | 0 | 0
5935 | SI_RAY10 | 10 | South | YES | 0.084476 | 47 | 10 | 47 | 0 | 1.03 | CC | 1 | 0.15763 | 47 | 47 | 3.9704 | 47 |  |  | 0.15763 | 7.4088 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 4 | South | YES | 0.084498 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 19 | 1.6055 | 19 |  |  | 0.15766 | 2.9955 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 4 | South | YES | 0.084498 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 22 | 1.859 | 22 |  |  | 0.15766 | 3.4684 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 2 | South | YES | 0.084498 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 36 | 3.0419 | 36 |  |  | 0.15766 | 5.6756 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 3 | South | YES | 0.084498 | 0 | 0 | 38 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 38 | 3.2109 | 38 |  |  | 0.15766 | 5.9909 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 2 | South | YES | 0.084498 | 0 | 0 | 41 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 41 | 3.4644 | 41 |  |  | 0.15766 | 6.4639 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 3 | South | YES | 0.084498 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 43 | 3.6334 | 43 |  |  | 0.15766 | 6.7792 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 2 | South | YES | 0.084498 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 50 | 4.2249 | 50 |  |  | 0.15766 | 7.8828 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 2 | South | YES | 0.084498 | 10 | 0 | 50 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 50 | 4.2249 | 50 |  |  | 0.15766 | 7.8828 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 1 | South | YES | 0.084498 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 55 | 4.6474 | 55 |  |  | 0.15766 | 8.671 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 1 | South | YES | 0.084498 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 94 | 7.9428 | 94 |  |  | 0.15766 | 14.8196 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 1 | South | YES | 0.084498 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 94 | 7.9428 | 94 |  |  | 0.15766 | 14.8196 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 1 | South | YES | 0.084498 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | 1 | 0.15766 | 0 | 148 | 12.5057 | 148 |  |  | 0.15766 | 23.333 |  |  |  |  | 0 | 0
60018 | DSKY1 | 1 | West | YES | -0.052795 | 21 | 0 | 84 | 0 | 1.023 | Wind | -1 | 0.15844 | 0 | 84 |  |  |  |  | -0.15844 | 0 |  |  |  |  | 0 | 0
60000 | DSKY2 | 1 | West | YES | -0.052969 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | -1 | 0.15862 | 0 | 76.5 |  |  |  |  | -0.15862 | 0 |  |  |  |  | 0 | 0
60017 | ORNNWP1 | 1 | West | YES | -0.053485 | 20 | 0 | 80 |  | 1.027 | Wind | -1 | 0.15913 | 0 | 80 |  |  |  |  | -0.15913 | 0 |  |  |  |  | 0 | 0
8161 | COLETO0A | 1 | South | YES | 0.0875 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | 1 | 0.16066 | 0 | 633 | 55.3875 | 633 |  |  | 0.16066 | 101.6962 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | 0.087727 | 0 | 0 | 8.4 |  | 1.027 | Diesel | 1 | 0.16088 | 8.4 | 8.4 | 0.73691 | 8.4 |  |  | 0.16088 | 1.3514 |  |  |  |  | 0 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | -0.055531 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.16118 | 0 | 150 |  |  |  |  | -0.16118 | 0 |  |  |  |  | 0 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.05559 | 20 | 0 | 80 | 0 | 1.0232 | Wind | -1 | 0.16124 | 0 | 80 |  |  |  |  | -0.16124 | 0 |  |  |  |  | 0 | 0
60016 | WOODWRD11A | 1 | West | YES | -0.055604 | 20 | 0 | 80 |  | 1.033 | Wind | -1 | 0.16125 | 0 | 80 |  |  |  |  | -0.16125 | 0 |  |  |  |  | 0 | 0
6016 | SWMESA | 1 | West | YES | -0.055675 | 18.8 | 0 | 75 |  | 1.03 | Wind | -1 | 0.16132 | 0 | 75 |  |  |  |  | -0.16132 | 0 |  |  |  |  | 0 | 0
60003 | KING_NE1A | 1 | West | YES | -0.055675 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16132 | 0 | 80 |  |  |  |  | -0.16132 | 0 |  |  |  |  | 0 | 0
60005 | KING_SE1A | 1 | West | YES | -0.055675 | 10 | 0 | 40 |  | 1.035 | Wind | -1 | 0.16132 | 0 | 40 |  |  |  |  | -0.16132 | 0 |  |  |  |  | 0 | 0
88198 | BEEVILLE | F | South | YES | 0.088248 | 0 | 0 | 0 | 0 | 1.02 | AVR | 1 | 0.16141 | 0 | 0 | 0 | 0 |  |  | 0.16141 | 0 |  |  |  |  | 0 | 0
60201 | RIO DRCS | F | West | YES | -0.055786 | 0 | 0 | 0 | 0 | 1.025 | AVR | -1 | 0.16143 | 0 | 0 |  |  |  |  | -0.16143 | 0 |  |  |  |  | 0 | 0
60007 | KING_SW1A | 1 | West | YES | -0.05606 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16171 | 0 | 80 |  |  |  |  | -0.16171 | 0 |  |  |  |  | 0 | 0
60019 | KING_NW1A | 1 | West | YES | -0.05606 | 20 | 0 | 80 |  | 1.03 | Wind | -1 | 0.16171 | 0 | 80 |  |  |  |  | -0.16171 | 0 |  |  |  |  | 0 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | 0.089443 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | 1 | 0.1626 | 23.9 | 23.9 | 2.1377 | 23.9 |  |  | 0.1626 | 3.8862 |  |  |  |  | 0 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | 0.089443 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | 1 | 0.1626 | 24 | 24 | 2.1466 | 24 |  |  | 0.1626 | 3.9024 |  |  |  |  | 0 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | 0.089443 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | 1 | 0.1626 | 24.3 | 24.3 | 2.1735 | 24.3 |  |  | 0.1626 | 3.9512 |  |  |  |  | 0 | 0
1349 | WESTXWIN_1G | 1 | West | YES | -0.061675 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | -1 | 0.16732 | 0 | 6.6 |  |  |  |  | -0.16732 | 0 |  |  |  |  | 0 | 0
1350 | NWPWRG1_1G | 1 | West | YES | -0.061675 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | -1 | 0.16732 | 0 | 34.3 |  |  |  |  | -0.16732 | 0 |  |  |  |  | 0 | 0
1008 | PB6GEN_7G | 6 | West | YES | -0.062012 | 515 | 130 | 515 | 0 | 1.036 | GST | -1 | 0.16766 | 515 | 515 |  |  |  |  | -0.16766 | -86.3447 |  |  |  |  | 0 | 0
1007 | PB5GEN_6G | 5 | West | YES | -0.062012 | 91.2 | 40 | 114 | 0 | 1.036 | GST | -1 | 0.16766 | 114 | 114 |  |  |  |  | -0.16766 | -19.1132 |  |  |  |  | 0 | 0
1005 | PBCTDGE_4G | D | West | YES | -0.062012 | 65 | 65 | 68 | 0 | 1.036 | GGT | -1 | 0.16766 | 68 | 68 |  |  |  |  | -0.16766 | -11.4009 |  |  |  |  | 0 | 0
1004 | PBCTCGE_3G | C | West | YES | -0.062012 | 62 | 62 | 67 | 0 | 1.036 | GGT | -1 | 0.16766 | 67 | 67 |  |  |  |  | -0.16766 | -11.2332 |  |  |  |  | 0 | 0
1006 | PBCTEGE_5G | E | West | YES | -0.062012 | 65 | 65 | 67 | 0 | 1.036 | GGT | -1 | 0.16766 | 67 | 67 |  |  |  |  | -0.16766 | -11.2332 |  |  |  |  | 0 | 0
1002 | PBCTAGE_1G | A | West | YES | -0.062012 | 64 | 64 | 66 | 0 | 1.036 | GGT | -1 | 0.16766 | 66 | 66 |  |  |  |  | -0.16766 | -11.0655 |  |  |  |  | 0 | 0
1003 | PBCTBGE_2G | B | West | YES | -0.062012 | 65 | 65 | 66 | 0 | 1.036 | GGT | -1 | 0.16766 | 66 | 66 |  |  |  |  | -0.16766 | -11.0655 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.062075 | 3.5 | 0 | 35 | 0 | 1 | Wind | -1 | 0.16772 | 0 | 35 |  |  |  |  | -0.16772 | 0 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.062075 | 3 | 0 | 30 | 0 | 1 | Wind | -1 | 0.16772 | 0 | 30 |  |  |  |  | -0.16772 | 0 |  |  |  |  | 0 | 0
3381 | BBRN_1G | 1 | North | YES | -0.062158 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | -1 | 0.16781 | 0 | 618 |  |  | 0 | 0 | -0.16781 | 0 |  |  |  |  | 0 | 0
3382 | BBRN_2G | 2 | North | YES | -0.062158 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | -1 | 0.16781 | 0 | 589 |  |  | 0 | 0 | -0.16781 | 0 |  |  |  |  | 0 | 0
11147 | NOTREES_1G | 1 | West | YES | -0.062197 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | -1 | 0.16784 | 0 | 149 |  |  |  |  | -0.16784 | 0 |  |  |  |  | 0 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.062293 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | -1 | 0.16794 | 0 | 112.5 |  |  |  |  | -0.16794 | 0 |  |  |  |  | 0 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.062293 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 149.5 |  |  |  |  | -0.16794 | 0 |  |  |  |  | 0 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.062293 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 186 |  |  |  |  | -0.16794 | 0 |  |  |  |  | 0 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.062293 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | -1 | 0.16794 | 0 | 214.5 |  |  |  |  | -0.16794 | 0 |  |  |  |  | 0 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.062487 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | -1 | 0.16813 | 0 | 114 |  |  |  |  | -0.16813 | 0 |  |  |  |  | 0 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | -0.062585 | 30 | 0 | 150 | 0 | 1.02 | Wind | -1 | 0.16823 | 0 | 150 |  |  |  |  | -0.16823 | 0 |  |  |  |  | 0 | 0
1320 | BSP 1 | 1 | West | YES | -0.062814 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | -1 | 0.16846 | 0 | 0 |  |  |  |  | -0.16846 | 0 |  |  |  |  | 0 | 0
1326 | STANTONW_8 | 1 | West | YES | -0.06289 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | -1 | 0.16854 | 0 | 100.5 |  |  |  |  | -0.16854 | 0 |  |  |  |  | 0 | 0
11025 | TIEHVSG_2G | 1 | West | YES | -0.062906 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | -1 | 0.16855 | 213.2 | 213.2 |  |  |  |  | -0.16855 | -35.9356 |  |  |  |  | 0 | 0
11020 | TIEHVSG_1G | 1 | West | YES | -0.062906 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | -1 | 0.16855 | 208.2 | 208.2 |  |  |  |  | -0.16855 | -35.0929 |  |  |  |  | 0 | 0
11024 | TIEHVCG_4G | 1 | West | YES | -0.062906 | 147 | 103 | 147 | 0 | 1.012 | CC | -1 | 0.16855 | 147 | 147 |  |  |  |  | -0.16855 | -24.7774 |  |  |  |  | 0 | 0
11021 | TIEHVCG_1G | 1 | West | YES | -0.062906 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | -1 | 0.16855 | 142.1 | 142.1 |  |  |  |  | -0.16855 | -23.9515 |  |  |  |  | 0 | 0
11023 | TIEHVCG_3G | 1 | West | YES | -0.062906 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | -1 | 0.16855 | 137.4 | 137.4 |  |  |  |  | -0.16855 | -23.1593 |  |  |  |  | 0 | 0
11022 | TIEHVCG_2G | 1 | West | YES | -0.062906 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | -1 | 0.16855 | 132.4 | 132.4 |  |  |  |  | -0.16855 | -22.3165 |  |  |  |  | 0 | 0
11014 | NAV6ST | 1 | West | YES | -0.062916 | 115 | 40 | 115 | 0 | 1.029 | CC | -1 | 0.16856 | 115 | 115 |  |  |  |  | -0.16856 | -19.3848 |  |  |  |  | 0 | 0
11011 | NAV3ST | 1 | West | YES | -0.062916 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | -1 | 0.16856 | 92.8 | 92.8 |  |  |  |  | -0.16856 | -15.6427 |  |  |  |  | 0 | 0
11012 | NAV4CT | 1 | West | YES | -0.062916 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.16856 | 80 | 80 |  |  |  |  | -0.16856 | -13.4851 |  |  |  |  | 0 | 0
11013 | NAV5CT | 1 | West | YES | -0.062916 | 80 | 18 | 80 | 0 | 1.029 | CC | -1 | 0.16856 | 80 | 80 |  |  |  |  | -0.16856 | -13.4851 |  |  |  |  | 0 | 0
11009 | NAV2CT | 1 | West | YES | -0.062916 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | -1 | 0.16856 | 71.4 | 71.4 |  |  |  |  | -0.16856 | -12.0354 |  |  |  |  | 0 | 0
11001 | NAV1CT | 1 | West | YES | -0.062916 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | -1 | 0.16856 | 70.4 | 70.4 |  |  |  |  | -0.16856 | -11.8669 |  |  |  |  | 0 | 0
13133 | CALFREST_3G | 3 | North | YES | -0.062996 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | -1 | 0.16864 | 177.4 | 177.4 |  |  | -11.1755 | 177.4 | -0.16864 | -29.9174 |  |  |  |  | 0 | 0
13132 | CALFREST_2G | 2 | North | YES | -0.062996 | 151 | 57 | 151 | 0 | 1.031 | CC | -1 | 0.16864 | 151 | 151 |  |  | -9.5124 | 151 | -0.16864 | -25.4652 |  |  |  |  | 0 | 0
13131 | CALFREST_1G | 1 | North | YES | -0.062996 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | -1 | 0.16864 | 150.7 | 150.7 |  |  | -9.4935 | 150.7 | -0.16864 | -25.4146 |  |  |  |  | 0 | 0
1328 | OCOTILLO_1G | 1 | West | YES | -0.063008 | 11.6 | 0 | 58 |  | 1.01 | Wind | -1 | 0.16866 | 0 | 58 |  |  |  |  | -0.16866 | 0 |  |  |  |  | 0 | 0
1333 | MCDDONAL_8 | 1 | West | YES | -0.063168 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | -1 | 0.16882 | 0 | 214.2 |  |  |  |  | -0.16882 | 0 |  |  |  |  | 0 | 0
13136 | CALFREST_6G | 6 | North | YES | -0.063173 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | -1 | 0.16882 | 177.5 | 177.5 |  |  | -11.2132 | 177.5 | -0.16882 | -29.9657 |  |  |  |  | 0 | 0
13135 | CALFREST_5G | 5 | North | YES | -0.063173 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | -1 | 0.16882 | 152.3 | 152.3 |  |  | -9.6212 | 152.3 | -0.16882 | -25.7114 |  |  |  |  | 0 | 0
13134 | CALFREST_4G | 4 | North | YES | -0.063173 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | -1 | 0.16882 | 151.5 | 151.5 |  |  | -9.5707 | 151.5 | -0.16882 | -25.5763 |  |  |  |  | 0 | 0
1327 | WILDHRSE_1G | 1 | West | YES | -0.063374 | 0 | 0 | 120 |  | 1 | Wind | -1 | 0.16902 | 0 | 120 |  |  |  |  | -0.16902 | 0 |  |  |  |  | 0 | 0
5903 | SANMIGUELGEN | 1 | South | YES | 0.095866 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | 1 | 0.16902 | 0 | 396.3 | 37.9917 | 396.3 |  |  | 0.16902 | 66.984 |  |  |  |  | 0 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.06341 | 0 | 0 | 120 |  | 1.01 | Wind | -1 | 0.16906 | 0 | 120 |  |  |  |  | -0.16906 | 0 |  |  |  |  | 0 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.063659 | 22.5 | 0 | 225 |  | 1 | Wind | -1 | 0.16931 | 0 | 225 |  |  |  |  | -0.16931 | 0 |  |  |  |  | 0 | 0
1045 | CALENG1G_1G | 1 | West | YES | -0.063663 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0 |  |  |  |  | 0 | 0
1046 | CALENG2G_2G | 2 | West | YES | -0.063663 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0 |  |  |  |  | 0 | 0
1047 | CALENG3G_3G | 3 | West | YES | -0.063663 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | -1 | 0.16931 | 0 | 0 |  |  |  |  | -0.16931 | 0 |  |  |  |  | 0 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.063719 | 20.9 | 0 | 180 |  | 1 | Wind | -1 | 0.16937 | 0 | 180 |  |  |  |  | -0.16937 | 0 |  |  |  |  | 0 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.063719 | 15.1 | 0 | 180 |  | 1 | Wind | -1 | 0.16937 | 0 | 180 |  |  |  |  | -0.16937 | 0 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 1 | West | YES | -0.063837 | 30 | 0 | 150 |  | 1.01 | Wind | -1 | 0.16948 | 0 | 150 |  |  |  |  | -0.16948 | 0 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 2 | West | YES | -0.063837 | 44 | 0 | 220 |  | 1.01 | Wind | -1 | 0.16948 | 0 | 220 |  |  |  |  | -0.16948 | 0 |  |  |  |  | 0 | 0
11065 | ELBOWCK_1G | 1 | West | YES | -0.063837 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | -1 | 0.16948 | 0 | 121.9 |  |  |  |  | -0.16948 | 0 |  |  |  |  | 0 | 0
60058 | BUFF_GAP1A | 1 | West | YES | -0.063992 | 24 | 0 | 120 |  | 1 | Wind | -1 | 0.16964 | 0 | 120 |  |  |  |  | -0.16964 | 0 |  |  |  |  | 0 | 0
60060 | CIRELLO | 1 | West | YES | -0.063992 | 46.6 | 0 | 233 | 0 | 1 | Wind | -1 | 0.16964 | 0 | 233 |  |  |  |  | -0.16964 | 0 |  |  |  |  | 0 | 0
60063 | BUFF_GAP1B | 1 | West | YES | -0.063992 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | -1 | 0.16964 | 0 | 170.2 |  |  |  |  | -0.16964 | 0 |  |  |  |  | 0 | 0
60066 | H_HOLLOW1A | 1 | West | YES | -0.063992 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | -1 | 0.16964 | 0 | 222 |  |  |  |  | -0.16964 | 0 |  |  |  |  | 0 | 0
60068 | HHOLLOW21A | 1 | West | YES | -0.063992 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 184 |  |  |  |  | -0.16964 | 0 |  |  |  |  | 0 | 0
60070 | HHOLLOW31A | 1 | West | YES | -0.063992 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 224 |  |  |  |  | -0.16964 | 0 |  |  |  |  | 0 | 0
60072 | HHOLLOW41A | 1 | West | YES | -0.063992 | 23 | 0 | 115 | 0 | 1.025 | Wind | -1 | 0.16964 | 0 | 115 |  |  |  |  | -0.16964 | 0 |  |  |  |  | 0 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.063995 | 109.6 | 40 | 137 | 0 | 1.029 | GST | -1 | 0.16964 | 137 | 137 |  |  |  |  | -0.16964 | -23.241 |  |  |  |  | 0 | 0
1040 | MRGNBG_2G | B | West | YES | -0.063995 | 70 | 70 | 71 | 0 | 1.029 | GGT | -1 | 0.16964 | 71 | 71 |  |  |  |  | -0.16964 | -12.0446 |  |  |  |  | 0 | 0
1041 | MRGNCG_3G | C | West | YES | -0.063995 | 69 | 69 | 70 | 0 | 1.029 | GGT | -1 | 0.16964 | 70 | 70 |  |  |  |  | -0.16964 | -11.875 |  |  |  |  | 0 | 0
1043 | MRGNEG_5G | E | West | YES | -0.063995 | 68 | 68 | 70 | 0 | 1.029 | GGT | -1 | 0.16964 | 70 | 70 |  |  |  |  | -0.16964 | -11.875 |  |  |  |  | 0 | 0
1039 | MRGNAG_1G | A | West | YES | -0.063995 | 69 | 69 | 69 | 0 | 1.029 | GGT | -1 | 0.16964 | 69 | 69 |  |  |  |  | -0.16964 | -11.7053 |  |  |  |  | 0 | 0
1042 | MRGNDG_4G | D | West | YES | -0.063995 | 68 | 68 | 68 | 0 | 1.029 | GGT | -1 | 0.16964 | 68 | 68 |  |  |  |  | -0.16964 | -11.5357 |  |  |  |  | 0 | 0
1044 | MRGNFG_6G | F | West | YES | -0.063995 | 66 | 66 | 66 | 0 | 1.029 | GGT | -1 | 0.16964 | 66 | 66 |  |  |  |  | -0.16964 | -11.1964 |  |  |  |  | 0 | 0
6637 | SNYDERW1A | 1 | West | YES | -0.064071 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | -1 | 0.16972 | 0 | 63 |  |  |  |  | -0.16972 | 0 |  |  |  |  | 0 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.064132 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | -1 | 0.16978 | 0 | 141 |  |  |  |  | -0.16978 | 0 |  |  |  |  | 0 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.064132 | 24 | 0 | 120 | 0 | 1.0217 | Wind | -1 | 0.16978 | 0 | 120 |  |  |  |  | -0.16978 | 0 |  |  |  |  | 0 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.064142 | 19.8 | 0 | 99 |  | 1 | Wind | -1 | 0.16979 | 0 | 99 |  |  |  |  | -0.16979 | 0 |  |  |  |  | 0 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.064142 | 12.2 | 0 | 61 |  | 1 | Wind | -1 | 0.16979 | 0 | 61 |  |  |  |  | -0.16979 | 0 |  |  |  |  | 0 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.064142 | 25 | 5 | 25 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0 |  |  |  |  | 0 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.064142 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0 |  |  |  |  | 0 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.064142 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | -1 | 0.16979 | 0 | 0 |  |  |  |  | -0.16979 | 0 |  |  |  |  | 0 | 0
36998 | RDCNYNG1 | 1 | West | YES | -0.064322 | 16.8 | 0 | 84 |  | 1.01 | Wind | -1 | 0.16997 | 0 | 84 |  |  |  |  | -0.16997 | 0 |  |  |  |  | 0 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.064746 | 30 | 0 | 150 |  | 1.014 | Wind | -1 | 0.17039 | 0 | 150 |  |  |  |  | -0.17039 | 0 |  |  |  |  | 0 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.064746 | 20.2 | 0 | 101 |  | 1 | Wind | -1 | 0.17039 | 0 | 101 |  |  |  |  | -0.17039 | 0 |  |  |  |  | 0 | 0
11056 | ROSCOE_1G | 1 | West | YES | -0.064846 | 41.8 | 0 | 209 |  | 1 | Wind | -1 | 0.17049 | 0 | 209 |  |  |  |  | -0.17049 | 0 |  |  |  |  | 0 | 0
11057 | CHAMPION_1G | 1 | West | YES | -0.064846 | 25.3 | 0 | 126.5 |  | 1 | Wind | -1 | 0.17049 | 0 | 126.5 |  |  |  |  | -0.17049 | 0 |  |  |  |  | 0 | 0
11058 | PYRON_1G | 1 | West | YES | -0.064846 | 49.8 | 0 | 249 |  | 1 | Wind | -1 | 0.17049 | 0 | 249 |  |  |  |  | -0.17049 | 0 |  |  |  |  | 0 | 0
11059 | INADALE_1G | 1 | West | YES | -0.064846 | 39.4 | 0 | 197 |  | 1 | Wind | -1 | 0.17049 | 0 | 197 |  |  |  |  | -0.17049 | 0 |  |  |  |  | 0 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | -0.064849 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 37.5 |  |  |  |  | -0.1705 | 0 |  |  |  |  | 0 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | -0.064849 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 107.5 |  |  |  |  | -0.1705 | 0 |  |  |  |  | 0 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | -0.064849 | 27 | 0 | 135 |  | 1.02 | Wind | -1 | 0.1705 | 0 | 135 |  |  |  |  | -0.1705 | 0 |  |  |  |  | 0 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | -0.064849 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 119 |  |  |  |  | -0.1705 | 0 |  |  |  |  | 0 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | -0.064849 | 21 | 0 | 105 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 105 |  |  |  |  | -0.1705 | 0 |  |  |  |  | 0 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | -0.064849 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | -1 | 0.1705 | 0 | 80.5 |  |  |  |  | -0.1705 | 0 |  |  |  |  | 0 | 0
6144 | MCADOO1A | 1 | West | YES | -0.065112 | 15 | 0 | 150 | 0 | 1.025 | Wind | -1 | 0.17076 | 0 | 150 |  |  |  |  | -0.17076 | 0 |  |  |  |  | 0 | 0
6407 | TURKTRAK1A | 1 | West | YES | -0.065221 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | -1 | 0.17087 | 0 | 169.5 |  |  |  |  | -0.17087 | 0 |  |  |  |  | 0 | 0
1417 | SWETWATR_2G | 2 | West | YES | -0.065247 | 72 | 36 | 72 | 0 | 1.026 | CC | -1 | 0.17089 | 72 | 72 |  |  |  |  | -0.17089 | -12.3044 |  |  |  |  | 0 | 0
1418 | SWETWATR_3G | 3 | West | YES | -0.065247 | 68 | 36 | 68 | 0 | 1.026 | CC | -1 | 0.17089 | 68 | 68 |  |  |  |  | -0.17089 | -11.6208 |  |  |  |  | 0 | 0
1419 | SWETWATR_4G | 4 | West | YES | -0.065247 | 61 | 36 | 61 | 0 | 1.026 | CC | -1 | 0.17089 | 61 | 61 |  |  |  |  | -0.17089 | -10.4246 |  |  |  |  | 0 | 0
1416 | SWETWATR_1G | 1 | West | YES | -0.065247 | 30 | 18 | 30 | 0 | 1.026 | CC | -1 | 0.17089 | 30 | 30 |  |  |  |  | -0.17089 | -5.1268 |  |  |  |  | 0 | 0
8189 | CUECPL2A | 1 | South | YES | 0.097885 | 12 | 0 | 12 | 0 | 1.02 | Cogen | 1 | 0.17104 | 0 | 0 | 0 | 0 |  |  | 0.17104 | 0 |  |  |  |  | 0 | 0
60081 | WHRLWIND1A | 1 | West | YES | -0.066019 | 12 | 0 | 60 | 0 | 1.03 | Wind | -1 | 0.17167 | 0 | 60 |  |  |  |  | -0.17167 | 0 |  |  |  |  | 0 | 0
3108 | STRYKER_2G | 2 | North | YES | -0.066332 | 484 | 75 | 484 | 0 | 1.029 | GST | -1 | 0.17198 | 484 | 484 |  |  | -32.1047 | 484 | -0.17198 | -83.2382 |  |  |  |  | 0 | 0
3107 | STRYKER_1G | 1 | North | YES | -0.066332 | 145.6 | 45 | 182 | 0 | 1.029 | GST | -1 | 0.17198 | 182 | 182 |  |  | -12.0724 | 182 | -0.17198 | -31.3003 |  |  |  |  | 0 | 0
3309 | ASPN_G | 1 | North | YES | -0.066592 | 50 | 0 | 50 |  | 1 | Bio | -1 | 0.17224 | 50 | 50 |  |  | -3.3296 | 50 | -0.17224 | -8.612 |  |  |  |  | 0 | 0
3348 | CHAMPION_1G | MB | North | YES | -0.066625 | 0 | 42 | 42 |  | 1 | Cogen | -1 | 0.17227 | 0 | 0 |  |  | 0 | 0 | -0.17227 | 0 |  |  |  |  | 0 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.099303 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0 |  |  |  |  | 0 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.099303 | 0 | 0 | 35 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0 |  |  |  |  | 0 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.099303 | 0 | 0 | 36 |  | 1 | Hydro | 1 | 0.17246 | 0 | 0 | 0 | 0 |  |  | 0.17246 | 0 |  |  |  |  | 0 | 0
13119 | TGATEWAY_4G | 4 | North | YES | -0.067045 | 399 | 65 | 399 | 0 | 1.0232 | CC | -1 | 0.17269 | 399 | 399 |  |  | -26.751 | 399 | -0.17269 | -68.9044 |  |  |  |  | 0 | 0
13116 | TGATEWAY_1G | 1 | North | YES | -0.067045 | 151 | 30 | 151 | 0 | 1.0232 | CC | -1 | 0.17269 | 151 | 151 |  |  | -10.1238 | 151 | -0.17269 | -26.0766 |  |  |  |  | 0 | 0
13118 | TGATEWAY_3G | 3 | North | YES | -0.067045 | 148 | 30 | 148 | 0 | 1.0232 | CC | -1 | 0.17269 | 148 | 148 |  |  | -9.9227 | 148 | -0.17269 | -25.5585 |  |  |  |  | 0 | 0
13117 | TGATEWAY_2G | 2 | North | YES | -0.067045 | 130 | 30 | 130 | 0 | 1.0232 | CC | -1 | 0.17269 | 130 | 130 |  |  | -8.7158 | 130 | -0.17269 | -22.4501 |  |  |  |  | 0 | 0
1437 | MESQUITW_1G | 1 | North | YES | -0.067055 | 40 | 0 | 400 | 0 | 1.023 | Wind | -1 | 0.1727 | 0 | 400 |  |  | 0 | 0 | -0.1727 | 0 |  |  |  |  | 0 | 0
1438 | MESQUITW_2G | 1 | North | YES | -0.067058 | 23.6 | 0 | 236 |  | 1.017 | Wind | -1 | 0.17271 | 0 | 236 |  |  | 0 | 0 | -0.17271 | 0 |  |  |  |  | 0 | 0
3097 | MARTLAKE_1G | 1 | North | YES | -0.067389 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 790 |  |  | 0 | 0 | -0.17304 | 0 |  |  |  |  | 0 | 0
3098 | MARTLAKE_2G | 2 | North | YES | -0.067389 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 795 |  |  | 0 | 0 | -0.17304 | 0 |  |  |  |  | 0 | 0
3099 | MARTLAKE_3G | 3 | North | YES | -0.067389 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | -1 | 0.17304 | 0 | 804 |  |  | 0 | 0 | -0.17304 | 0 |  |  |  |  | 0 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | 0.099885 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | 1 | 0.17304 | 0 | 562 | 56.1354 | 562 |  |  | 0.17304 | 97.2498 |  |  |  |  | 0 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | 0.099997 | 43 | 24 | 43 | 0 | 1.0197 | GGT | 1 | 0.17315 | 43 | 43 | 4.2999 | 43 |  |  | 0.17315 | 7.4456 |  |  |  |  | 0 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | 0.099997 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.17315 | 44 | 44 | 4.3999 | 44 |  |  | 0.17315 | 7.6188 |  |  |  |  | 0 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | 0.099997 | 44 | 24 | 44 | 0 | 1.0197 | GGT | 1 | 0.17315 | 44 | 44 | 4.3999 | 44 |  |  | 0.17315 | 7.6188 |  |  |  |  | 0 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | 0.099997 | 45 | 24 | 45 | 0 | 1.0197 | GGT | 1 | 0.17315 | 45 | 45 | 4.4999 | 45 |  |  | 0.17315 | 7.7919 |  |  |  |  | 0 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | 0.099997 | 0 | 20 | 58 |  | 1.0197 | GST | 1 | 0.17315 | 58 | 58 | 5.7998 | 58 |  |  | 0.17315 | 10.043 |  |  |  |  | 0 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | 0.099997 | 89 | 25 | 89 | 0 | 1.0197 | GST | 1 | 0.17315 | 89 | 89 | 8.8997 | 89 |  |  | 0.17315 | 15.4107 |  |  |  |  | 0 | 0
1442 | COKFIELD_5 | 1 | North | YES | -0.067751 | 16.5 | 0 | 165 |  | 1.029 | Wind | -1 | 0.1734 | 0 | 165 |  |  | 0 | 0 | -0.1734 | 0 |  |  |  |  | 0 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.10033 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.17348 | 155 | 155 | 15.5507 | 155 |  |  | 0.17348 | 26.8901 |  |  |  |  | 0 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.10033 | 155 | 90 | 155 | 0 | 1.025 | CC | 1 | 0.17348 | 155 | 155 | 15.5507 | 155 |  |  | 0.17348 | 26.8901 |  |  |  |  | 0 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | 0.10033 | 174 | 138 | 174 | 0 | 1.025 | CC | 1 | 0.17348 | 174 | 174 | 17.4569 | 174 |  |  | 0.17348 | 30.1863 |  |  |  |  | 0 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.10067 | 407 | 60 | 407 | 0 | 1.0138 | GST | 1 | 0.17383 | 407 | 407 | 40.9743 | 407 |  |  | 0.17383 | 70.7494 |  |  |  |  | 0 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.10072 | 215 | 40 | 215 | 0 | 1.0192 | GST | 1 | 0.17388 | 215 | 215 | 21.6546 | 215 |  |  | 0.17388 | 37.3834 |  |  |  |  | 0 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.10072 | 216 | 40 | 216 | 0 | 1.0192 | GST | 1 | 0.17388 | 216 | 216 | 21.7553 | 216 |  |  | 0.17388 | 37.5573 |  |  |  |  | 0 | 0
6100 | OKLA7A | EQ | West | YES | -0.068286 | 50 | -220 | 220 | 0 | 1.035 | DCTie | -1 | 0.17393 | 0 | 0 |  |  |  |  | -0.17393 | 0 |  |  |  |  | 0 | 0
6752 | OKLA0A | 1 | West | YES | -0.068286 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | -1 | 0.17393 | 0 | 649.7 |  |  |  |  | -0.17393 | 0 |  |  |  |  | 0 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | 0.10085 | 400 | 80 | 400 | 0 | 1.0192 | GST | 1 | 0.174 | 400 | 400 | 40.3388 | 400 |  |  | 0.174 | 69.6018 |  |  |  |  | 0 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | 0.10085 | 418 | 80 | 418 | 0 | 1.0192 | GST | 1 | 0.174 | 418 | 418 | 42.154 | 418 |  |  | 0.174 | 72.7339 |  |  |  |  | 0 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | 0.10099 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.17415 | 0 | 430 | 43.4253 | 430 |  |  | 0.17415 | 74.883 |  |  |  |  | 0 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | 0.10099 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | 1 | 0.17415 | 0 | 430 | 43.4253 | 430 |  |  | 0.17415 | 74.883 |  |  |  |  | 0 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.10143 | 48.8 | 20 | 61 | 0 | 1.012 | GST | 1 | 0.17459 | 61 | 61 | 6.1874 | 61 |  |  | 0.17459 | 10.65 |  |  |  |  | 0 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.10143 | 95 | 25 | 95 | 0 | 1.012 | GST | 1 | 0.17459 | 95 | 95 | 9.636 | 95 |  |  | 0.17459 | 16.586 |  |  |  |  | 0 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.10143 | 151 | 40 | 151 | 0 | 1.012 | GST | 1 | 0.17459 | 151 | 151 | 15.3162 | 151 |  |  | 0.17459 | 26.363 |  |  |  |  | 0 | 0
1432 | GRHAMSES_2G | 2 | North | YES | -0.069944 | 294.9 | 90 | 366 | 0 | 1.014 | GST | -1 | 0.17559 | 366 | 366 |  |  | -25.5995 | 366 | -0.17559 | -64.2666 |  |  |  |  | 0 | 0
12424 | FPLEFR2S_G | 4 | North | YES | -0.070029 | 415 | 191 | 415 | 0 | 1 | CC | -1 | 0.17568 | 415 | 415 |  |  | -29.062 | 415 | -0.17568 | -72.9058 |  |  |  |  | 0 | 0
12414 | FPLEFR1S_G | 4 | North | YES | -0.070029 | 414 | 191 | 414 | 0 | 1 | CC | -1 | 0.17568 | 414 | 414 |  |  | -28.992 | 414 | -0.17568 | -72.7302 |  |  |  |  | 0 | 0
12412 | FPLEFR1B_G | 2 | North | YES | -0.070029 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.17568 | 164 | 164 |  |  | -11.4848 | 164 | -0.17568 | -28.811 |  |  |  |  | 0 | 0
12413 | FPLEFR1C_G | 3 | North | YES | -0.070029 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.17568 | 164 | 164 |  |  | -11.4848 | 164 | -0.17568 | -28.811 |  |  |  |  | 0 | 0
12423 | FPLEFR2C_G | 3 | North | YES | -0.070029 | 163 | 72 | 163 | 0 | 1 | CC | -1 | 0.17568 | 163 | 163 |  |  | -11.4147 | 163 | -0.17568 | -28.6353 |  |  |  |  | 0 | 0
12421 | FPLEFR2A_G | 1 | North | YES | -0.070029 | 162 | 72 | 162 | 0 | 1 | CC | -1 | 0.17568 | 162 | 162 |  |  | -11.3447 | 162 | -0.17568 | -28.4596 |  |  |  |  | 0 | 0
12411 | FPLEFR1A_G | 1 | North | YES | -0.070029 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.17568 | 161 | 161 |  |  | -11.2747 | 161 | -0.17568 | -28.2839 |  |  |  |  | 0 | 0
12422 | FPLEFR2B_G | 2 | North | YES | -0.070029 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.17568 | 161 | 161 |  |  | -11.2747 | 161 | -0.17568 | -28.2839 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 1 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 2 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 2 | North | YES | -0.070041 | 13.6 | 12 | 17 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 1 | North | YES | -0.070041 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.17569 | 0 | 0 |  |  | 0 | 0 | -0.17569 | 0 |  |  |  |  | 0 | 0
1433 | GRHAMSES_1G | 1 | North | YES | -0.070142 | 242 | 60 | 242 | 0 | 1.038 | GST | -1 | 0.17579 | 242 | 242 |  |  | -16.9744 | 242 | -0.17579 | -42.5411 |  |  |  |  | 0 | 0
3126 | TRINIDAD_6G | 1 | North | YES | -0.070556 | 179.2 | 46 | 224 | 0 | 1 | GST | -1 | 0.1762 | 224 | 224 |  |  | -15.8045 | 224 | -0.1762 | -39.4696 |  |  |  |  | 0 | 0
2452 | LKHB2_G | 2 | North | YES | -0.070564 | 516 | 80 | 516 | 0 | 1.022 | GST | -1 | 0.17621 | 516 | 516 |  |  | -36.411 | 516 | -0.17621 | -90.9252 |  |  |  |  | 0 | 0
2451 | LKHB1_G | 1 | North | YES | -0.070564 | 0 | 80 | 391 |  | 1.022 | GST | -1 | 0.17621 | 391 | 391 |  |  | -27.5905 | 391 | -0.17621 | -68.8988 |  |  |  |  | 0 | 0
12440 | PARKD_1SVC8 | 1 | North | YES | -0.070682 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.17633 | 0 | 0 |  |  | 0 | 0 | -0.17633 | 0 |  |  |  |  | 0 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | -0.070682 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.17633 | 0 | 0 |  |  | 0 | 0 | -0.17633 | 0 |  |  |  |  | 0 | 0
950 | STEAM3 | 1 | North | YES | -0.070707 | 41 | 13 | 42 | 0 | 1.02 | GST | -1 | 0.17635 | 42 | 42 |  |  | -2.9697 | 42 | -0.17635 | -7.4069 |  |  |  |  | 0 | 0
949 | STEAM2 | 1 | North | YES | -0.070707 | 26 | 8 | 26 | 0 | 0.99 | GST | -1 | 0.17635 | 26 | 26 |  |  | -1.8384 | 26 | -0.17635 | -4.5852 |  |  |  |  | 0 | 0
948 | STEAM1 | 1 | North | YES | -0.070707 | 0 | 12 | 20 |  | 1.02 | GST | -1 | 0.17635 | 20 | 20 |  |  | -1.4141 | 20 | -0.17635 | -3.5271 |  |  |  |  | 0 | 0
844 | OLINGER_G3 | 1 | North | YES | -0.070819 | 103.9 | 45 | 150 | 0 | 1.03 | GST | -1 | 0.17647 | 150 | 150 |  |  | -10.6228 | 150 | -0.17647 | -26.47 |  |  |  |  | 0 | 0
843 | OLINGER_G2 | 1 | North | YES | -0.070819 | 76.2 | 25 | 110 | 0 | 1.03 | GST | -1 | 0.17647 | 110 | 110 |  |  | -7.7901 | 110 | -0.17647 | -19.4113 |  |  |  |  | 0 | 0
842 | OLINGER_G1 | 1 | North | YES | -0.070819 | 55.4 | 20 | 79 | 0 | 1.03 | GST | -1 | 0.17647 | 79 | 79 |  |  | -5.5947 | 79 | -0.17647 | -13.9409 |  |  |  |  | 0 | 0
845 | OLINGER_G4 | 1 | North | YES | -0.070819 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | -1 | 0.17647 | 76 | 76 |  |  | -5.3822 | 76 | -0.17647 | -13.4115 |  |  |  |  | 0 | 0
837 | NEWMAN_G5 | 1 | North | YES | -0.070826 | 0 | 15 | 40 |  | 1.01 | GST | -1 | 0.17647 | 40 | 40 |  |  | -2.833 | 40 | -0.17647 | -7.0589 |  |  |  |  | 0 | 0
1701 | MOSES_1G | 1 | North | YES | -0.070891 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 558 |  |  | 0 | 0 | -0.17654 | 0 |  |  |  |  | 0 | 0
1702 | MOSES_2G | 2 | North | YES | -0.070891 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 579 |  |  | 0 | 0 | -0.17654 | 0 |  |  |  |  | 0 | 0
1703 | MOSES_3G | 3 | North | YES | -0.070891 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | -1 | 0.17654 | 0 | 808 |  |  | 0 | 0 | -0.17654 | 0 |  |  |  |  | 0 | 0
5925 | DCEAST | EQ | North | YES | -0.070891 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | -1 | 0.17654 | 0 | 0 |  |  | 0 | 0 | -0.17654 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.10343 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.17659 | 0 | 0 | 0 | 0 |  |  | 0.17659 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.10343 | 0 | 0 | 2.4 |  | 1 | Hydro | 1 | 0.17659 | 0 | 0 | 0 | 0 |  |  | 0.17659 | 0 |  |  |  |  | 0 | 0
1675 | PEC_1G | 1 | North | YES | -0.070943 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0 |  |  |  |  | 0 | 0
1676 | PEC_2G | 2 | North | YES | -0.070943 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0 |  |  |  |  | 0 | 0
1677 | PEC_3G | 3 | North | YES | -0.070943 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | -1 | 0.17659 | 0 | 0 |  |  | 0 | 0 | -0.17659 | 0 |  |  |  |  | 0 | 0
1683 | LAMARPWR_6G | 6 | North | YES | -0.071002 | 198 | 129.1 | 198 | 0 | 1.038 | CC | -1 | 0.17665 | 198 | 198 |  |  | -14.0584 | 198 | -0.17665 | -34.9766 |  |  |  |  | 0 | 0
1680 | LAMARPWR_3G | 3 | North | YES | -0.071002 | 196 | 129.1 | 196 | 0 | 1.038 | CC | -1 | 0.17665 | 196 | 196 |  |  | -13.9164 | 196 | -0.17665 | -34.6233 |  |  |  |  | 0 | 0
1678 | LAMARPWR_1G | 1 | North | YES | -0.071002 | 160 | 67.7 | 160 | 0 | 1.038 | CC | -1 | 0.17665 | 160 | 160 |  |  | -11.3603 | 160 | -0.17665 | -28.264 |  |  |  |  | 0 | 0
1682 | LAMARPWR_5G | 5 | North | YES | -0.071002 | 157 | 67.7 | 157 | 0 | 1.038 | CC | -1 | 0.17665 | 157 | 157 |  |  | -11.1473 | 157 | -0.17665 | -27.734 |  |  |  |  | 0 | 0
1679 | LAMARPWR_2G | 2 | North | YES | -0.071002 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.17665 | 156 | 156 |  |  | -11.0763 | 156 | -0.17665 | -27.5574 |  |  |  |  | 0 | 0
1681 | LAMARPWR_4G | 4 | North | YES | -0.071002 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.17665 | 156 | 156 |  |  | -11.0763 | 156 | -0.17665 | -27.5574 |  |  |  |  | 0 | 0
1689 | VALLEY_3G | 3 | North | YES | -0.07107 | 0 | 25 | 375 |  | 1.003 | GST | -1 | 0.17672 | 375 | 375 |  |  | -26.6513 | 375 | -0.17672 | -66.2691 |  |  |  |  | 0 | 0
11693 | KMICHIST3_G | 3 | North | YES | -0.07107 | 312 | 60 | 312 | 0 | 1.026 | CC | -1 | 0.17672 | 312 | 312 |  |  | -22.1738 | 312 | -0.17672 | -55.1359 |  |  |  |  | 0 | 0
11696 | KMICHIST6_G | 6 | North | YES | -0.07107 | 310 | 60 | 310 | 0 | 1.026 | CC | -1 | 0.17672 | 310 | 310 |  |  | -22.0317 | 310 | -0.17672 | -54.7825 |  |  |  |  | 0 | 0
11695 | KMICHICT5_G | 5 | North | YES | -0.07107 | 148 | 80 | 148 | 0 | 1.026 | CC | -1 | 0.17672 | 148 | 148 |  |  | -10.5184 | 148 | -0.17672 | -26.1542 |  |  |  |  | 0 | 0
11692 | KMICHICT2_G | 2 | North | YES | -0.07107 | 146 | 80 | 146 | 0 | 1.026 | CC | -1 | 0.17672 | 146 | 146 |  |  | -10.3762 | 146 | -0.17672 | -25.8008 |  |  |  |  | 0 | 0
11691 | KMICHICT1_G | 1 | North | YES | -0.07107 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.17672 | 144 | 144 |  |  | -10.2341 | 144 | -0.17672 | -25.4473 |  |  |  |  | 0 | 0
11694 | KMICHICT4_G | 4 | North | YES | -0.07107 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.17672 | 144 | 144 |  |  | -10.2341 | 144 | -0.17672 | -25.4473 |  |  |  |  | 0 | 0
1688 | VALLEY_2G | 2 | North | YES | -0.071166 | 527 | 90 | 527 | 0 | 1.029 | GSC | -1 | 0.17681 | 527 | 527 |  |  | -37.5045 | 527 | -0.17681 | -93.1808 |  |  |  |  | 0 | 0
1687 | VALLEY_1G | 1 | North | YES | -0.071166 | 136 | 15 | 170 | 0 | 1.029 | GST | -1 | 0.17681 | 170 | 170 |  |  | -12.0982 | 170 | -0.17681 | -30.0583 |  |  |  |  | 0 | 0
6948 | DENISNDM | 1 | North | YES | -0.071253 | 40 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.1769 | 0 | 0 |  |  | 0 | 0 | -0.1769 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 2 | North | YES | -0.071253 | 31 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.1769 | 0 | 0 |  |  | 0 | 0 | -0.1769 | 0 |  |  |  |  | 0 | 0
2371 | COLLIN_1G | MB | North | YES | -0.071683 | 0 | 40 | 138 |  | 1.022 | GST | -1 | 0.17733 | 0 | 0 |  |  | 0 | 0 | -0.17733 | 0 |  |  |  |  | 0 | 0
1455 | WCPWRCO_3G | 3 | North | YES | -0.071787 | 242 | 50 | 242 |  | 1.02 | CC | -1 | 0.17743 | 242 | 242 |  |  | -17.3725 | 242 | -0.17743 | -42.9392 |  |  |  |  | 0 | 0
1453 | WCPWRCO_1G | 1 | North | YES | -0.071787 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.17743 | 204 | 204 |  |  | -14.6445 | 204 | -0.17743 | -36.1967 |  |  |  |  | 0 | 0
1454 | WCPWRCO_2G | 2 | North | YES | -0.071787 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.17743 | 204 | 204 |  |  | -14.6445 | 204 | -0.17743 | -36.1967 |  |  |  |  | 0 | 0
2417 | MTCK8_G | 8 | North | YES | -0.071897 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | -1 | 0.17754 | 556 | 556 |  |  | -39.9747 | 556 | -0.17754 | -98.7149 |  |  |  |  | 0 | 0
2413 | MTCK6_G | 6 | North | YES | -0.071897 | 0 | 30 | 118 |  | 1.022 | GST | -1 | 0.17754 | 118 | 118 |  |  | -8.4838 | 118 | -0.17754 | -20.9503 |  |  |  |  | 0 | 0
2414 | MTCK7_G | 7 | North | YES | -0.071897 | 0 | 30 | 115 |  | 1.022 | GST | -1 | 0.17754 | 115 | 115 |  |  | -8.2682 | 115 | -0.17754 | -20.4176 |  |  |  |  | 0 | 0
1600 | BARTNWND_1G | 1 | North | YES | -0.071906 | 12 | 0 | 120 | 0 | 1.022 | Wind | -1 | 0.17755 | 0 | 120 |  |  | 0 | 0 | -0.17755 | 0 |  |  |  |  | 0 | 0
344 | MRSSHPRD | 1 | North | YES | -0.071924 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.17757 | 0 | 0 |  |  | 0 | 0 | -0.17757 | 0 |  |  |  |  | 0 | 0
345 | MRSSHPRD01 | 2 | North | YES | -0.071924 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.17757 | 0 | 0 |  |  | 0 | 0 | -0.17757 | 0 |  |  |  |  | 0 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.10451 | 138 | 30 | 138 | 0 | 1.02 | CC | 1 | 0.17767 | 138 | 138 | 14.4224 | 138 |  |  | 0.17767 | 24.5181 |  |  |  |  | 0 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.10451 | 146 | 30 | 146 | 0 | 1.02 | CC | 1 | 0.17767 | 146 | 146 | 15.2585 | 146 |  |  | 0.17767 | 25.9394 |  |  |  |  | 0 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.10451 | 147 | 30 | 147 | 0 | 1.02 | CC | 1 | 0.17767 | 147 | 147 | 15.363 | 147 |  |  | 0.17767 | 26.1171 |  |  |  |  | 0 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.10451 | 149 | 30 | 149 | 0 | 1.02 | CC | 1 | 0.17767 | 149 | 149 | 15.572 | 149 |  |  | 0.17767 | 26.4724 |  |  |  |  | 0 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.10451 | 182 | 30 | 182 | 0 | 1.02 | CC | 1 | 0.17767 | 182 | 182 | 19.0208 | 182 |  |  | 0.17767 | 32.3355 |  |  |  |  | 0 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.10451 | 203 | 30 | 203 | 0 | 1.02 | CC | 1 | 0.17767 | 203 | 203 | 21.2155 | 203 |  |  | 0.17767 | 36.0665 |  |  |  |  | 0 | 0
728 | WOLFRIDGE801 | 1 | North | YES | -0.072064 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | -1 | 0.17771 | 0 | 112.5 |  |  | 0 | 0 | -0.17771 | 0 |  |  |  |  | 0 | 0
924 | SPENCER_G5 | 1 | North | YES | -0.072141 | 52 | 20 | 66 | 0 | 1.03 | GST | -1 | 0.17779 | 66 | 66 |  |  | -4.7613 | 66 | -0.17779 | -11.7341 |  |  |  |  | 0 | 0
923 | SPENCER_G4 | 1 | North | YES | -0.072141 | 48 | 20 | 61 | 0 | 1.03 | GST | -1 | 0.17779 | 61 | 61 |  |  | -4.4006 | 61 | -0.17779 | -10.8451 |  |  |  |  | 0 | 0
2383 | NTHLK3_G | 3 | North | YES | -0.072188 | 0 | 50 | 329 |  | 1.022 | GST | -1 | 0.17784 | 329 | 329 |  |  | -23.7499 | 329 | -0.17784 | -58.5079 |  |  |  |  | 0 | 0
2382 | NTHLK2_G | 2 | North | YES | -0.072188 | 0 | 35 | 181 |  | 1.022 | GST | -1 | 0.17784 | 181 | 181 |  |  | -13.066 | 181 | -0.17784 | -32.1883 |  |  |  |  | 0 | 0
2381 | NTHLK1_G | 1 | North | YES | -0.072188 | 0 | 35 | 156 |  | 1.022 | GST | -1 | 0.17784 | 156 | 156 |  |  | -11.2613 | 156 | -0.17784 | -27.7424 |  |  |  |  | 0 | 0
580 | JCKCNTY801 | 1 | North | YES | -0.072706 | 288 | 0 | 288 | 0 | 1.022 | CC | -1 | 0.17835 | 288 | 288 |  |  | -20.9393 | 288 | -0.17835 | -51.3659 |  |  |  |  | 0 | 0
581 | JCKCNTY802 | 2 | North | YES | -0.072706 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.17835 | 147 | 147 |  |  | -10.6878 | 147 | -0.17835 | -26.218 |  |  |  |  | 0 | 0
582 | JCKCNTY803 | 3 | North | YES | -0.072706 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.17835 | 147 | 147 |  |  | -10.6878 | 147 | -0.17835 | -26.218 |  |  |  |  | 0 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.10567 | 0 | 0 | 4 |  | 1 | Hydro | 1 | 0.17882 | 0 | 0 | 0 | 0 |  |  | 0.17882 | 0 |  |  |  |  | 0 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | -0.073342 | 196 | 130 | 196 | 0 | 1.036 | CC | -1 | 0.17899 | 196 | 196 |  |  | -14.375 | 196 | -0.17899 | -35.082 |  |  |  |  | 0 | 0
12323 | ENNSTRAC_2G | 2 | North | YES | -0.073342 | 116 | 100 | 116 | 0 | 1.036 | CC | -1 | 0.17899 | 116 | 116 |  |  | -8.5077 | 116 | -0.17899 | -20.7628 |  |  |  |  | 0 | 0
1861 | EAGLEMNT_1G | MB | North | YES | -0.073375 | 0 | 30 | 112 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0 |  |  |  |  | 0 | 0
1862 | EAGLEMNT_2G | MB | North | YES | -0.073375 | 0 | 40 | 100 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0 |  |  |  |  | 0 | 0
1863 | EAGLEMNT_3G | MB | North | YES | -0.073375 | 0 | 50 | 378 |  | 1.022 | GST | -1 | 0.17902 | 0 | 0 |  |  | 0 | 0 | -0.17902 | 0 |  |  |  |  | 0 | 0
505 | NTHTEXAS03 | 3 | North | YES | -0.07364 | 30.4 | 15 | 38 |  | 1.015 | GST | -1 | 0.17929 | 38 | 38 |  |  | -2.7983 | 38 | -0.17929 | -6.8129 |  |  |  |  | 0 | 0
503 | NTHTEXAS01 | 1 | North | YES | -0.07364 | 0 | 5 | 18 |  | 1.015 | GST | -1 | 0.17929 | 18 | 18 |  |  | -1.3255 | 18 | -0.17929 | -3.2272 |  |  |  |  | 0 | 0
504 | NTHTEXAS02 | 2 | North | YES | -0.07364 | 14.4 | 5 | 18 |  | 1.015 | GST | -1 | 0.17929 | 18 | 18 |  |  | -1.3255 | 18 | -0.17929 | -3.2272 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.10619 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.10619 | 0 | 0 | 2.4 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.10619 | 0 | 0 | 2.8 |  | 1.025 | Hydro | 1 | 0.17935 | 0 | 0 | 0 | 0 |  |  | 0.17935 | 0 |  |  |  |  | 0 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | -0.073825 | 6 | 0 | 60 | 0 | 1.022 | Wind | -1 | 0.17947 | 0 | 60 |  |  | 0 | 0 | -0.17947 | 0 |  |  |  |  | 0 | 0
1898 | COMCHEPK_1G | 1 | North | YES | -0.074064 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | -1 | 0.17971 | 0 | 0 |  |  | 0 | 0 | -0.17971 | 0 |  |  |  |  | 0 | 0
1899 | COMCHEPK_2G | 2 | North | YES | -0.074064 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | -1 | 0.17971 | 0 | 0 |  |  | 0 | 0 | -0.17971 | 0 |  |  |  |  | 0 | 0
1879 | WLFHOLW_3G | 3 | North | YES | -0.074234 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | -1 | 0.17988 | 272.4 | 272.4 |  |  | -20.2213 | 272.4 | -0.17988 | -48.9998 |  |  |  |  | 0 | 0
1877 | WLFHOLW_1G | 1 | North | YES | -0.074234 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | -1 | 0.17988 | 217.3 | 217.3 |  |  | -16.131 | 217.3 | -0.17988 | -39.0883 |  |  |  |  | 0 | 0
1878 | WLFHOLW_2G | 2 | North | YES | -0.074234 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | -1 | 0.17988 | 215.7 | 215.7 |  |  | -16.0123 | 215.7 | -0.17988 | -38.8005 |  |  |  |  | 0 | 0
334 | RWMILLER03 | 3 | North | YES | -0.074418 | 166.4 | 65 | 208 | 0 | 1.04 | GST | -1 | 0.18007 | 208 | 208 |  |  | -15.4789 | 208 | -0.18007 | -37.4537 |  |  |  |  | 0 | 0
333 | RWMILLER02 | 2 | North | YES | -0.074418 | 95.2 | 37 | 119 | 0 | 1.04 | GST | -1 | 0.18007 | 119 | 119 |  |  | -8.8557 | 119 | -0.18007 | -21.4278 |  |  |  |  | 0 | 0
335 | RWMILLER04 | 4 | North | YES | -0.074418 | 81.6 | 0 | 102 | 0 | 1.04 | GST | -1 | 0.18007 | 102 | 102 |  |  | -7.5906 | 102 | -0.18007 | -18.3667 |  |  |  |  | 0 | 0
336 | RWMILLER05 | 5 | North | YES | -0.074418 | 80.8 | 0 | 101 | 0 | 1.04 | GST | -1 | 0.18007 | 101 | 101 |  |  | -7.5162 | 101 | -0.18007 | -18.1866 |  |  |  |  | 0 | 0
332 | RWMILLER01 | 1 | North | YES | -0.074418 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | -1 | 0.18007 | 73 | 73 |  |  | -5.4325 | 73 | -0.18007 | -13.1448 |  |  |  |  | 0 | 0
1889 | DECRDOVA_1G | 1 | North | YES | -0.074446 | 779 | 255 | 779 | 0 | 1.02 | GSC | -1 | 0.18009 | 779 | 779 |  |  | -57.9934 | 779 | -0.18009 | -140.293 |  |  |  |  | 0 | 0
1948 | HANDLEY_4G | 4 | North | YES | -0.074468 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.18012 | 435 | 435 |  |  | -32.3936 | 435 | -0.18012 | -78.3503 |  |  |  |  | 0 | 0
1949 | HANDLEY_5G | 5 | North | YES | -0.07457 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.18022 | 435 | 435 |  |  | -32.438 | 435 | -0.18022 | -78.3947 |  |  |  |  | 0 | 0
1947 | HANDLEY_3G | 3 | North | YES | -0.07457 | 316 | 100 | 395 | 0 | 1.022 | GST | -1 | 0.18022 | 395 | 395 |  |  | -29.4551 | 395 | -0.18022 | -71.186 |  |  |  |  | 0 | 0
1892 | DECRDOVA_2G | A | North | YES | -0.075535 | 65 | 65 | 70 | 0 | 1.025 | GGT | -1 | 0.18118 | 70 | 70 |  |  | -5.2874 | 70 | -0.18118 | -12.6828 |  |  |  |  | 0 | 0
1893 | DECRDOVA_3G | B | North | YES | -0.075535 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.18118 | 69 | 69 |  |  | -5.2119 | 69 | -0.18118 | -12.5016 |  |  |  |  | 0 | 0
1894 | DECRDOVA_4G | C | North | YES | -0.075535 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.18118 | 69 | 69 |  |  | -5.2119 | 69 | -0.18118 | -12.5016 |  |  |  |  | 0 | 0
1895 | DECRDOVA_5G | D | North | YES | -0.075535 | 65 | 65 | 68 | 0 | 1.025 | GGT | -1 | 0.18118 | 68 | 68 |  |  | -5.1364 | 68 | -0.18118 | -12.3204 |  |  |  |  | 0 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.10842 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.18158 | 148 | 148 | 16.0459 | 148 |  |  | 0.18158 | 26.8732 |  |  |  |  | 0 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.10842 | 148 | 0 | 148 | 0 | 1.02 | CC | 1 | 0.18158 | 148 | 148 | 16.0459 | 148 |  |  | 0.18158 | 26.8732 |  |  |  |  | 0 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.10842 | 154 | 0 | 154 | 0 | 1.02 | CC | 1 | 0.18158 | 154 | 154 | 16.6964 | 154 |  |  | 0.18158 | 27.9626 |  |  |  |  | 0 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.10842 | 293 | 0 | 293 | 0 | 1.02 | CC | 1 | 0.18158 | 293 | 293 | 31.7665 | 293 |  |  | 0.18158 | 53.2016 |  |  |  |  | 0 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.10859 | 0 | 0 | 6 |  | 1 | Hydro | 1 | 0.18174 | 0 | 0 | 0 | 0 |  |  | 0.18174 | 0 |  |  |  |  | 0 | 0
1941 | MDLTHELP_1G | 1 | North | YES | -0.077237 | 216.4 | 74 | 216.4 | 0 | 1 | CC | -1 | 0.18288 | 216.4 | 216.4 |  |  | -16.7141 | 216.4 | -0.18288 | -39.5762 |  |  |  |  | 0 | 0
1942 | MDLTHELP_2G | 2 | North | YES | -0.077237 | 216.1 | 74 | 216.1 | 0 | 1 | CC | -1 | 0.18288 | 216.1 | 216.1 |  |  | -16.6909 | 216.1 | -0.18288 | -39.5214 |  |  |  |  | 0 | 0
1938 | MDLTHELP_6G | 6 | North | YES | -0.077577 | 226 | 74 | 226 | 0 | 1 | CC | -1 | 0.18322 | 226 | 226 |  |  | -17.5324 | 226 | -0.18322 | -41.4088 |  |  |  |  | 0 | 0
1937 | MDLTHELP_5G | 5 | North | YES | -0.077577 | 224 | 74 | 224 | 0 | 1 | CC | -1 | 0.18322 | 224 | 224 |  |  | -17.3772 | 224 | -0.18322 | -41.0423 |  |  |  |  | 0 | 0
1943 | MDLTHELP_3G | 3 | North | YES | -0.077577 | 212 | 74 | 212 | 0 | 1 | CC | -1 | 0.18322 | 212 | 212 |  |  | -16.4463 | 212 | -0.18322 | -38.8436 |  |  |  |  | 0 | 0
1944 | MDLTHELP_4G | 4 | North | YES | -0.077577 | 211 | 74 | 211 | 0 | 1 | CC | -1 | 0.18322 | 211 | 211 |  |  | -16.3687 | 211 | -0.18322 | -38.6604 |  |  |  |  | 0 | 0
366 | JNSNCNTY802 | 1 | North | YES | -0.078006 | 168 | 20 | 168 | 0 | 1.02 | Cogen | -1 | 0.18365 | 0 | 0 |  |  | 0 | 0 | -0.18365 | 0 |  |  |  |  | 0 | 0
367 | JNSNCNTY802 | 2 | North | YES | -0.078006 | 90 | 20 | 90 | 0 | 1.02 | Cogen | -1 | 0.18365 | 0 | 0 |  |  | 0 | 0 | -0.18365 | 0 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.1116 | 50 | 0 | 50 | 0 | 1.025 | GGT | 1 | 0.18476 | 50 | 50 | 5.5803 | 50 |  |  | 0.18476 | 9.2381 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.11201 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.18517 | 0 | 0 | 0 | 0 |  |  | 0.18517 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.11201 | 0 | 0 | 8 |  | 1 | Hydro | 1 | 0.18517 | 0 | 0 | 0 | 0 |  |  | 0.18517 | 0 |  |  |  |  | 0 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.11267 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | 1 | 0.18583 | 223.9 | 223.9 | 25.2277 | 223.9 |  |  | 0.18583 | 41.6077 |  |  |  |  | 0 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.11267 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | 1 | 0.18583 | 224.6 | 224.6 | 25.3066 | 224.6 |  |  | 0.18583 | 41.7377 |  |  |  |  | 0 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.11267 | 225 | 74 | 225 | 0 | 1.008 | CC | 1 | 0.18583 | 225 | 225 | 25.3516 | 225 |  |  | 0.18583 | 41.8121 |  |  |  |  | 0 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.11267 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | 1 | 0.18583 | 226.7 | 226.7 | 25.5432 | 226.7 |  |  | 0.18583 | 42.128 |  |  |  |  | 0 | 0
9000 | DECKR_G1 | 1 | South | YES | 0.11502 | 280 | 50 | 321 | 0 | 1.015 | GST | 1 | 0.18818 | 321 | 321 | 36.9217 | 321 |  |  | 0.18818 | 60.4053 |  |  |  |  | 0 | 0
9001 | DECKR_G2 | 2 | South | YES | 0.11502 | 400 | 50 | 426 | 0 | 1.015 | GST | 1 | 0.18818 | 426 | 426 | 48.9989 | 426 |  |  | 0.18818 | 80.164 |  |  |  |  | 0 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.11605 | 132 | 40 | 132 | 0 | 1.02 | GST | 1 | 0.1892 | 132 | 132 | 15.3182 | 132 |  |  | 0.1892 | 24.975 |  |  |  |  | 0 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.11605 | 133 | 32 | 139 | 0 | 1.02 | GST | 1 | 0.1892 | 139 | 139 | 16.1305 | 139 |  |  | 0.1892 | 26.2994 |  |  |  |  | 0 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.11605 | 324.9 | 60 | 329 | 0 | 1.02 | GST | 1 | 0.1892 | 329 | 329 | 38.1795 | 329 |  |  | 0.1892 | 62.2483 |  |  |  |  | 0 | 0
9017 | SANDH_G2 | 2 | South | YES | 0.11611 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.18927 | 46 | 46 | 5.3411 | 46 |  |  | 0.18927 | 8.7063 |  |  |  |  | 0 | 0
9018 | SANDH_G3 | 3 | South | YES | 0.11611 | 45 | 2 | 46 | 0 | 1.0175 | GGT | 1 | 0.18927 | 46 | 46 | 5.3411 | 46 |  |  | 0.18927 | 8.7063 |  |  |  |  | 0 | 0
9019 | SANDH_G4 | 4 | South | YES | 0.11611 | 0 | 2 | 47 |  | 1.0175 | GGT | 1 | 0.18927 | 47 | 47 | 5.4572 | 47 |  |  | 0.18927 | 8.8956 |  |  |  |  | 0 | 0
9016 | SANDH_G1 | 1 | South | YES | 0.11611 | 45 | 2 | 49 | 0 | 1.0175 | GGT | 1 | 0.18927 | 49 | 49 | 5.6894 | 49 |  |  | 0.18927 | 9.2741 |  |  |  |  | 0 | 0
9021 | SANDHG5C | 5C | South | YES | 0.11611 | 140 | 0 | 148 | 0 | 1.0175 | CC | 1 | 0.18927 | 148 | 148 | 17.1843 | 148 |  |  | 0.18927 | 28.0116 |  |  |  |  | 0 | 0
9020 | SANDHG5A | 5A | South | YES | 0.11611 | 150 | 84 | 155 | 0 | 1.0175 | CC | 1 | 0.18927 | 155 | 155 | 17.9971 | 155 |  |  | 0.18927 | 29.3365 |  |  |  |  | 0 | 0
9002 | DECKR_G3 | 3 | South | YES | 0.11697 | 0 | 24 | 42 |  | 1.015 | GGT | 1 | 0.19013 | 42 | 42 | 4.9129 | 42 |  |  | 0.19013 | 7.9855 |  |  |  |  | 0 | 0
9003 | DECKR_G4 | 4 | South | YES | 0.11697 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.19013 | 44 | 44 | 5.1469 | 44 |  |  | 0.19013 | 8.3658 |  |  |  |  | 0 | 0
9004 | DECKR_G5 | 5 | South | YES | 0.11697 | 44 | 24 | 44 | 0 | 1.015 | GGT | 1 | 0.19013 | 44 | 44 | 5.1469 | 44 |  |  | 0.19013 | 8.3658 |  |  |  |  | 0 | 0
9005 | DECKR_G6 | 6 | South | YES | 0.11697 | 44 | 24 | 47 | 0 | 1.015 | GGT | 1 | 0.19013 | 47 | 47 | 5.4978 | 47 |  |  | 0.19013 | 8.9362 |  |  |  |  | 0 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.11858 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | 1 | 0.19174 | 0 | 436 | 51.7 | 436 |  |  | 0.19174 | 83.5966 |  |  |  |  | 0 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.11871 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | 1 | 0.19187 | 0 | 598 | 70.988 | 598 |  |  | 0.19187 | 114.7361 |  |  |  |  | 0 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.11871 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | 1 | 0.19187 | 0 | 606 | 71.9377 | 606 |  |  | 0.19187 | 116.2711 |  |  |  |  | 0 | 0
244 | WHITNYDM01 | 1 | North | YES | -0.096791 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.20244 | 0 | 0 |  |  | 0 | 0 | -0.20244 | 0 |  |  |  |  | 0 | 0
245 | WHITNYDM02 | 2 | North | YES | -0.096791 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.20244 | 0 | 0 |  |  | 0 | 0 | -0.20244 | 0 |  |  |  |  | 0 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.13412 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | 1 | 0.20728 | 149.5 | 149.5 | 20.0508 | 149.5 |  |  | 0.20728 | 30.9878 |  |  |  |  | 0 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.13412 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | 1 | 0.20728 | 152.5 | 152.5 | 20.4531 | 152.5 |  |  | 0.20728 | 31.6097 |  |  |  |  | 0 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.13412 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | 1 | 0.20728 | 232.6 | 232.6 | 31.1961 | 232.6 |  |  | 0.20728 | 48.2125 |  |  |  |  | 0 | 0
251 | BOSQUESW803 | 2 | North | YES | -0.10187 | 150 | 0 | 150 | 0 | 1.032 | CC | -1 | 0.20751 | 150 | 150 |  |  | -15.2799 | 150 | -0.20751 | -31.1271 |  |  |  |  | 0 | 0
253 | BOSQUESW804 | 2 | North | YES | -0.10187 | 80 | 0 | 80 | 0 | 1.032 | CC | -1 | 0.20751 | 80 | 80 |  |  | -8.1493 | 80 | -0.20751 | -16.6011 |  |  |  |  | 0 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.1349 | 580 | 225 | 580 |  | 1.029 | LIGCO | 1 | 0.20806 | 0 | 580 | 78.2426 | 580 |  |  | 0.20806 | 120.6739 |  |  |  |  | 0 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.13594 | 158.6 | 110 | 158 | 0 | 1 | CC | 1 | 0.20909 | 158 | 158 | 21.4779 | 158 |  |  | 0.20909 | 33.0368 |  |  |  |  | 0 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.13594 | 157.7 | 107 | 160 | 0 | 1 | CC | 1 | 0.20909 | 160 | 160 | 21.7498 | 160 |  |  | 0.20909 | 33.4549 |  |  |  |  | 0 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.13594 | 173.9 | 72 | 175 | 0 | 1 | CC | 1 | 0.20909 | 175 | 175 | 23.7888 | 175 |  |  | 0.20909 | 36.5914 |  |  |  |  | 0 | 0
238 | BOSQUESW505 | 1 | North | YES | -0.10901 | 255 | 0 | 255 | 0 | 1.02 | CC | -1 | 0.21466 | 255 | 255 |  |  | -27.7983 | 255 | -0.21466 | -54.7385 |  |  |  |  | 0 | 0
247 | BOSQUESW501 | 2 | North | YES | -0.10901 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | -1 | 0.21466 | 156 | 156 |  |  | -17.006 | 156 | -0.21466 | -33.4871 |  |  |  |  | 0 | 0
239 | BOSQUESW502 | 1 | North | YES | -0.10901 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | -1 | 0.21466 | 149 | 149 |  |  | -16.2429 | 149 | -0.21466 | -31.9844 |  |  |  |  | 0 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | -0.11345 | 177.6 | 40 | 222 | 0 | 1.029 | GST | -1 | 0.2191 | 222 | 222 |  |  | -25.1857 | 222 | -0.2191 | -48.6395 |  |  |  |  | 0 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | -0.11345 | 60 | 33 | 75 |  | 1.029 | GST | -1 | 0.2191 | 75 | 75 |  |  | -8.5087 | 75 | -0.2191 | -16.4323 |  |  |  |  | 0 | 0
3404 | THOUSE_2G | 2 | North | YES | -0.11377 | 807 | 250 | 807 | 0 | 1.012 | GSC | -1 | 0.21941 | 807 | 807 |  |  | -91.8084 | 807 | -0.21941 | -177.066 |  |  |  |  | 0 | 0
3403 | THOUSE_1G | 1 | North | YES | -0.11377 | 563 | 200 | 563 | 0 | 1.012 | GSC | -1 | 0.21941 | 563 | 563 |  |  | -64.0497 | 563 | -0.21941 | -123.5293 |  |  |  |  | 0 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.1798 | 581 | 225 | 581 |  | 1.029 | LIGCO | 1 | 0.25295 | 0 | 581 | 104.4609 | 581 |  |  | 0.25295 | 146.9654 |  |  |  |  | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0

## Zones
Houston | 1
North | -1
South | 1
West | -1
SET UP AREA, copy & paste values to cell B1
Source | South |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | North | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1073 | SCURRYCW_2G | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3126 | TRINIDAD_6G | GST
3309 | ASPN_G | Bio
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5920 | WELSHDC1 | DCTie
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6096 | NORTHDC7 | DCTie
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NBEC7 | GST
8442 | NBEC7 | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11056 | ROSCOE_1G | Wind
11057 | CHAMPION_1G | Wind
11058 | PYRON_1G | Wind
11059 | INADALE_1G | Wind
11065 | ELBOWCK_1G | Wind
11147 | NOTREES_1G | Wind
11309 | BULLCREK_2G | Wind
11310 | BULLCREK_1G | Wind
11320 | COYOTE_1G | Wind
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
48940 | WARVUE_GT1 | Cogen
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
71061 | L_SWEETW1_5N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
76095 | L_CAPRSI1_1N | Wind
76096 | L_CAPRSI1_2N | Wind
76097 | L_CAPRGE1_1N | Wind
80003 | MILHWYS | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80263 | B_DAVIS31A | CC
80264 | B_DAVIS41A | CC
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
86104 | CID-138 | DCTie
86105 | CID-230 | DCTie
86106 | CUF-230 | DCTie
86107 | CUF-138 | DCTie
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR