## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  | Summary of Key Data points | Value
File Description: Cont_ Cokfield to GrahamSES and LongCreek to GrahamSES1_5 OL_ TonkawawI_5 to GrahamSES
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K27 |  | Number of units | 645
|  |  | Dec PTDF cutoff point | 102
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  | Dec PTDF cutoff unit | OKLA0A
|  |  | Dec 10% unit | LONGSHORE_5
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  | Dec max cumltv zone impact - cumltv zone share | 0.051368
|  |  | Dec max cumltv zone impact - cumltv zone share pt | 52
Step 5 | Enter Dennis' file name into cell K27 |  | Dec max cumltv zone impact - cumltv zone share unit | BULLCREK_1G
|  |  | West Zonal weighted AWGSF | 0.25633
Step 6 | click the step one button |  | North Zonal weighted AWGSF | -0.021071
|  |  | Inc PTDF cutoff point | 543
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  | Inc PTDF cutoff unit | COKFIELD_5
| X6:X30, or to the end of the selected list. |  | Inc 10% unit | KMICHIST3_G
|  |  | Inc max cumltv zone impact - cumltv zone share | 0.015067
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  | Inc max cumltv zone impact - cumltv zone share pt | 143
| of the formulas in columns L:V (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  | Inc max cumltv zone impact - cumltv zone share unit | BOSQUESW501
| If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct leng |  | West Zonal weighted AWGSF | 0.25633
| It is only necessary to match the Distributed Slack - Dec worksheet. |  | North Zonal weighted AWGSF | -0.021071
|  |  | Min of zone correlation | 0.023604
Step 9 | Click the step 2 button |  | Bounary gen in North Zone | 0
| The last file saved will still be open, yopu will need to close this file. |  | Bounary gen in soucre zone as % of line | 0%
| This sheet willno longer be open. |  | Bounary gen in West Zone | 0
|  |  | Bounary gen in soucre zone as % of line | 0
|  |  | OL element line rating | 1072
|  |  | West Zonal weighted AWGSF | 0.25633
|  | WN_043009automation.xls | North Zonal weighted AWGSF | -0.021071
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ Cokfield to GrahamSES and LongCreek to GrahamSES1_5 OL_ TonkawawI_5 to GrahamSES |  | i_PTDF_DEC_pt | 102 |  | BULLCREK_1G | Unit at max
11056 | ROSCOE_1G | 1 | West | YES | 0.37703 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.3981 | 0 | 209 | 78.7989 | 209 |  |  | 0.3981 | 83.2026 | 0.019273 | 0.026563 |  |  | i_10pctunit | 6 |  | 52 | # units @ max
11057 | CHAMPION_1G | 1 | West | YES | 0.37703 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.3981 | 0 | 126.5 | 47.694 | 126.5 |  |  | 0.3981 | 50.3595 | 0.030938 | 0.04264 |  |  | # units | 645 |  | 0.051368 | delta max
11058 | PYRON_1G | 1 | West | YES | 0.37703 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.3981 | 0 | 249 | 93.88 | 249 |  |  | 0.3981 | 99.1266 | 0.0539 | 0.074287 | [5 empty] | Delta
11059 | INADALE_1G | 1 | West | YES | 0.37703 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.3981 | 0 | 197 | 74.2745 | 197 |  |  | 0.3981 | 78.4255 | 0.072067 | 0.099324 | Weighted Shift Factors |  |  |  | 1 | 0.0072895
1058 | LONGSHORE_5 | 1 | West | YES | 0.29363 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.3147 | 0 | 150 | 44.0444 | 150 |  |  | 0.3147 | 47.205 | 0.085899 | 0.11439 | West | 0.25633 |  |  | 2 | 0.011702
1058 | LONGSHORE_5 | 2 | West | YES | 0.29363 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.3147 | 0 | 220 | 64.5984 | 220 |  |  | 0.3147 | 69.234 | 0.10619 | 0.1365 | North | -0.021071 |  |  | 3 | 0.020386
11065 | ELBOWCK_1G | 1 | West | YES | 0.29363 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.3147 | 0 | 121.9 | 35.7934 | 121.9 |  |  | 0.3147 | 38.3619 | 0.11743 | 0.14874 |  |  |  |  | 4 | 0.027257
1045 | CALENG1G_1G | 1 | West | YES | 0.29237 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0 | 0.11743 | 0.14874 |  |  |  |  | 5 | 0.028495
1046 | CALENG2G_2G | 2 | West | YES | 0.29237 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0 | 0.11743 | 0.14874 |  |  |  |  | 6 | 0.030311
1047 | CALENG3G_3G | 3 | West | YES | 0.29237 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0 | 0.11743 | 0.14874 |  |  |  |  | 7 | 0.031317
11001 | NAV1CT | 1 | West | YES | 0.28807 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.30914 | 70.4 | 70.4 | 20.2803 | 70.4 |  |  | 0.30914 | 21.7637 | 0.12392 | 0.15569 |  |  |  |  | 8 | 0.031317
11009 | NAV2CT | 1 | West | YES | 0.28807 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.30914 | 71.4 | 71.4 | 20.5684 | 71.4 |  |  | 0.30914 | 22.0729 | 0.1305 | 0.16274 |  |  |  |  | 9 | 0.031317
11011 | NAV3ST | 1 | West | YES | 0.28807 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.30914 | 92.8 | 92.8 | 26.7332 | 92.8 |  |  | 0.30914 | 28.6885 | 0.13906 | 0.1719 |  |  |  |  | 10 | 0.031317
11012 | NAV4CT | 1 | West | YES | 0.28807 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30914 | 80 | 80 | 23.0458 | 80 |  |  | 0.30914 | 24.7315 | 0.14644 | 0.17979 |  |  |  |  | 11 | 0.031773
11013 | NAV5CT | 1 | West | YES | 0.28807 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30914 | 80 | 80 | 23.0458 | 80 |  |  | 0.30914 | 24.7315 | 0.15382 | 0.18769 |  |  |  |  | 12 | 0.032236
11014 | NAV6ST | 1 | West | YES | 0.28807 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.30914 | 115 | 115 | 33.1284 | 115 |  |  | 0.30914 | 35.5515 | 0.16442 | 0.19904 |  |  |  |  | 13 | 0.032837
11020 | TIEHVSG_1G | 1 | West | YES | 0.28801 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.30908 | 208.2 | 208.2 | 59.9641 | 208.2 |  |  | 0.30908 | 64.351 | 0.18362 | 0.21958 |  |  |  |  | 14 | 0.033355
11021 | TIEHVCG_1G | 1 | West | YES | 0.28801 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.30908 | 142.1 | 142.1 | 40.9265 | 142.1 |  |  | 0.30908 | 43.9207 | 0.19672 | 0.23361 |  |  |  |  | 15 | 0.033873
11022 | TIEHVCG_2G | 1 | West | YES | 0.28801 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.30908 | 132.4 | 132.4 | 38.1328 | 132.4 |  |  | 0.30908 | 40.9226 | 0.20893 | 0.24667 |  |  |  |  | 16 | 0.034618
11023 | TIEHVCG_3G | 1 | West | YES | 0.28801 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.30908 | 137.4 | 137.4 | 39.5728 | 137.4 |  |  | 0.30908 | 42.468 | 0.2216 | 0.26023 |  |  |  |  | 17 | 0.035963
11024 | TIEHVCG_4G | 1 | West | YES | 0.28801 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.30908 | 147 | 147 | 42.3378 | 147 |  |  | 0.30908 | 45.4352 | 0.23516 | 0.27473 |  |  |  |  | 18 | 0.036881
11025 | TIEHVSG_2G | 1 | West | YES | 0.28801 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.30908 | 213.2 | 213.2 | 61.4042 | 213.2 |  |  | 0.30908 | 65.8965 | 0.25482 | 0.29577 |  |  |  |  | 19 | 0.037736
1002 | PBCTAGE_1G | A | West | YES | 0.28269 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.30376 | 66 | 66 | 18.6577 | 66 |  |  | 0.30376 | 20.0483 | 0.26091 | 0.30217 |  |  |  |  | 20 | 0.038624
1003 | PBCTBGE_2G | B | West | YES | 0.28269 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.30376 | 66 | 66 | 18.6577 | 66 |  |  | 0.30376 | 20.0483 | 0.26699 | 0.30857 |  |  |  |  | 21 | 0.039574
1004 | PBCTCGE_3G | C | West | YES | 0.28269 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.30376 | 67 | 67 | 18.9404 | 67 |  |  | 0.30376 | 20.3521 | 0.27317 | 0.31507 |  |  |  |  | 22 | 0.040951
1005 | PBCTDGE_4G | D | West | YES | 0.28269 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.30376 | 68 | 68 | 19.2231 | 68 |  |  | 0.30376 | 20.6559 | 0.27944 | 0.32166 |  |  |  |  | 23 | 0.041265
1006 | PBCTEGE_5G | E | West | YES | 0.28269 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.30376 | 67 | 67 | 18.9404 | 67 |  |  | 0.30376 | 20.3521 | 0.28562 | 0.32816 |  |  |  |  | 24 | 0.041579
1007 | PB5GEN_6G | 5 | West | YES | 0.28269 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.30376 | 114 | 114 | 32.2269 | 114 |  |  | 0.30376 | 34.629 | 0.29613 | 0.33922 |  |  |  |  | 25 | 0.041898
1008 | PB6GEN_7G | 6 | West | YES | 0.28269 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.30376 | 515 | 515 | 145.5864 | 515 |  |  | 0.30376 | 156.4378 | 0.34362 | 0.38916 |  |  |  |  | 26 | 0.042222
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.28257 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.30364 | 0 | 35 | 9.8898 | 35 |  |  | 0.30364 | 10.6273 | 0.34685 | 0.39255 |  |  |  |  | 27 | 0.042541
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.28257 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.30364 | 0 | 30 | 8.477 | 30 |  |  | 0.30364 | 9.1091 | 0.34962 | 0.39546 |  |  |  |  | 28 | 0.043084
11147 | NOTREES_1G | 1 | West | YES | 0.28221 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.30329 | 0 | 149 | 42.05 | 149 |  |  | 0.30329 | 45.1896 | 0.36336 | 0.40989 |  |  |  |  | 29 | 0.045536
1326 | STANTONW_8 | 1 | West | YES | 0.28117 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.30224 | 0 | 100.5 | 28.2574 | 100.5 |  |  | 0.30224 | 30.375 | 0.37263 | 0.41959 |  |  |  |  | 30 | 0.045701
1037 | MORGAN5G_5G | 5 | West | YES | 0.28106 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.30213 | 137 | 137 | 38.5047 | 137 |  |  | 0.30213 | 41.3914 | 0.38526 | 0.4328 |  |  |  |  | 31 | 0.045843
1039 | MRGNAG_1G | A | West | YES | 0.28106 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.30213 | 69 | 69 | 19.3929 | 69 |  |  | 0.30213 | 20.8467 | 0.39162 | 0.43946 |  |  |  |  | 32 | 0.046529
1040 | MRGNBG_2G | B | West | YES | 0.28106 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.30213 | 71 | 71 | 19.955 | 71 |  |  | 0.30213 | 21.451 | 0.39817 | 0.4463 |  |  |  |  | 33 | 0.046959
1041 | MRGNCG_3G | C | West | YES | 0.28106 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.30213 | 70 | 70 | 19.6739 | 70 |  |  | 0.30213 | 21.1489 | 0.40463 | 0.45306 |  |  |  |  | 34 | 0.04754
1042 | MRGNDG_4G | D | West | YES | 0.28106 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.30213 | 68 | 68 | 19.1118 | 68 |  |  | 0.30213 | 20.5446 | 0.4109 | 0.45961 |  |  |  |  | 35 | 0.047832
1043 | MRGNEG_5G | E | West | YES | 0.28106 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.30213 | 70 | 70 | 19.6739 | 70 |  |  | 0.30213 | 21.1489 | 0.41735 | 0.46637 |  |  |  |  | 36 | 0.048133
1044 | MRGNFG_6G | F | West | YES | 0.28106 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.30213 | 66 | 66 | 18.5497 | 66 |  |  | 0.30213 | 19.9404 | 0.42344 | 0.47273 |  |  |  |  | 37 | 0.04843
1328 | OCOTILLO_1G | 1 | West | YES | 0.27857 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.29964 | 0 | 58 | 16.1571 | 58 |  |  | 0.29964 | 17.3792 | 0.42879 | 0.47828 |  |  |  |  | 38 | 0.048718
1333 | MCDDONAL_8 | 1 | West | YES | 0.27836 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.29943 | 0 | 214.2 | 59.6254 | 214.2 |  |  | 0.29943 | 64.1387 | 0.44854 | 0.49876 |  |  |  |  | 39 | 0.049015
1327 | WILDHRSE_1G | 1 | West | YES | 0.27488 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.29595 | 0 | 120 | 32.986 | 120 |  |  | 0.29595 | 35.5145 | 0.4596 | 0.51009 |  |  |  |  | 40 | 0.049294
1360 | GUNSIGHT_8 | 1 | West | YES | 0.27338 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.29445 | 0 | 120 | 32.806 | 120 |  |  | 0.29445 | 35.3345 | 0.47067 | 0.52138 |  |  |  |  | 41 | 0.049494
1320 | BSP 1 | 1 | West | YES | 0.27101 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.29208 | 0 | 0 | 0 | 0 |  |  | 0.29208 | 0 | 0.47067 | 0.52138 |  |  |  |  | 42 | 0.050218
1416 | SWETWATR_1G | 1 | West | YES | 0.27072 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.29179 | 30 | 30 | 8.1217 | 30 |  |  | 0.29179 | 8.7538 | 0.47344 | 0.52417 |  |  |  |  | 43 | 0.05049
1417 | SWETWATR_2G | 2 | West | YES | 0.27072 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.29179 | 72 | 72 | 19.492 | 72 |  |  | 0.29179 | 21.0091 | 0.48008 | 0.53088 |  |  |  |  | 44 | 0.050705
1418 | SWETWATR_3G | 3 | West | YES | 0.27072 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.29179 | 68 | 68 | 18.4091 | 68 |  |  | 0.29179 | 19.8419 | 0.48635 | 0.53721 |  |  |  |  | 45 | 0.050705
1419 | SWETWATR_4G | 4 | West | YES | 0.27072 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.29179 | 61 | 61 | 16.514 | 61 |  |  | 0.29179 | 17.7994 | 0.49197 | 0.54289 |  |  |  |  | 46 | 0.050733
11320 | COYOTE_1G | 1 | West | YES | 0.2705 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.29157 | 0 | 225 | 60.8625 | 225 |  |  | 0.29157 | 65.6034 | 0.51272 | 0.56384 |  |  |  |  | 47 | 0.050801
11309 | BULLCREK_2G | 1 | West | YES | 0.26996 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.29103 | 0 | 180 | 48.5919 | 180 |  |  | 0.29103 | 52.3846 | 0.52932 | 0.58056 |  |  |  |  | 48 | 0.050865
11310 | BULLCREK_1G | 1 | West | YES | 0.26996 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.29103 | 0 | 180 | 48.5919 | 180 |  |  | 0.29103 | 52.3846 | 0.54592 | 0.59729 |  |  |  |  | 49 | 0.050922
6637 | SNYDERW1A | 1 | West | YES | 0.26571 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.28678 | 0 | 63 | 16.7397 | 63 |  |  | 0.28678 | 18.0672 | 0.55173 | 0.60305 |  |  |  |  | 50 | 0.051117
1068 | SCURRYCW_1G | 1 | West | YES | 0.26283 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.28391 | 0 | 141 | 37.0597 | 141 |  |  | 0.28391 | 40.0307 | 0.56473 | 0.61583 |  |  |  |  | 51 | 0.051242
1073 | SCURRYCW_2G | 2 | West | YES | 0.26283 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.28391 | 0 | 120 | 31.5402 | 120 |  |  | 0.28391 | 34.0687 | 0.5758 | 0.62671 |  |  |  |  | 52 | 0.051368
1061 | CIELOGEN_1G | 1 | West | YES | 0.26256 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.28364 | 0 | 99 | 25.9939 | 99 |  |  | 0.28364 | 28.0799 | 0.58493 | 0.63568 |  |  |  |  | 53 | 0.051326
1062 | CIELOGEN_2G | 1 | West | YES | 0.26256 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.28364 | 0 | 61 | 16.0165 | 61 |  |  | 0.28364 | 17.3018 | 0.59055 | 0.6412 |  |  |  |  | 54 | 0.051103
1069 | KINDERMG_1G | 1 | West | YES | 0.26256 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0 | 0.59055 | 0.6412 |  |  |  |  | 55 | 0.050914
1070 | KINDERMG_2G | 1 | West | YES | 0.26256 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0 | 0.59055 | 0.6412 |  |  |  |  | 56 | 0.050749
1071 | KINDERMG_3G | 1 | West | YES | 0.26256 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0 | 0.59055 | 0.6412 |  |  |  |  | 57 | 0.050648
1349 | WESTXWIN_1G | 1 | West | YES | 0.26137 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.28244 | 0 | 6.6 | 1.725 | 6.6 |  |  | 0.28244 | 1.8641 | 0.59116 | 0.64179 |  |  |  |  | 58 | 0.050648
1350 | NWPWRG1_1G | 1 | West | YES | 0.26137 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.28244 | 0 | 34.3 | 8.9649 | 34.3 |  |  | 0.28244 | 9.6876 | 0.59432 | 0.64489 |  |  |  |  | 59 | 0.050648
60007 | KING_SW1A | 1 | West | YES | 0.25893 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28 | 0 | 80 | 20.7147 | 80 |  |  | 0.28 | 22.4004 | 0.6017 | 0.65204 |  |  |  |  | 60 | 0.050648
60019 | KING_NW1A | 1 | West | YES | 0.25893 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28 | 0 | 80 | 20.7147 | 80 |  |  | 0.28 | 22.4004 | 0.60908 | 0.65919 |  |  |  |  | 61 | 0.050634
76031 | L_GASCCR1_1N | W1 | West | YES | 0.25872 | 30 | 0 | 150 |  | 1.02 | Wind | 1 | 0.27979 | 0 | 150 | 38.8074 | 150 |  |  | 0.27979 | 41.968 | 0.62291 | 0.67259 |  |  |  |  | 62 | 0.050564
60201 | RIO DRCS | F | West | YES | 0.25816 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.27923 | 0 | 0 | 0 | 0 |  |  | 0.27923 | 0 | 0.62291 | 0.67259 |  |  |  |  | 63 | 0.050338
6016 | SWMESA | 1 | West | YES | 0.25764 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.27871 | 0 | 75 | 19.3228 | 75 |  |  | 0.27871 | 20.9031 | 0.62983 | 0.67926 |  |  |  |  | 64 | 0.050112
60003 | KING_NE1A | 1 | West | YES | 0.25764 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27871 | 0 | 80 | 20.611 | 80 |  |  | 0.27871 | 22.2966 | 0.6372 | 0.68638 |  |  |  |  | 65 | 0.049678
60005 | KING_SE1A | 1 | West | YES | 0.25764 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.27871 | 0 | 40 | 10.3055 | 40 |  |  | 0.27871 | 11.1483 | 0.64089 | 0.68994 |  |  |  |  | 66 | 0.049678
60016 | WOODWRD11A | 1 | West | YES | 0.25744 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.27851 | 0 | 80 | 20.5951 | 80 |  |  | 0.27851 | 22.2808 | 0.64827 | 0.69705 |  |  |  |  | 67 | 0.049435
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.25739 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.27846 | 0 | 80 | 20.5909 | 80 |  |  | 0.27846 | 22.2765 | 0.65565 | 0.70416 |  |  |  |  | 68 | 0.049176
38437 | TNSRBNMESA9 | 1 | West | YES | 0.25715 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.27822 | 0 | 150 | 38.5729 | 150 |  |  | 0.27822 | 41.7336 | 0.66948 | 0.71749 |  |  |  |  | 69 | 0.049047
71051 | L_BITTCR1_1N | W1 | West | YES | 0.25649 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 37.5 | 9.6182 | 37.5 |  |  | 0.27756 | 10.4084 | 0.67294 | 0.72081 |  |  |  |  | 70 | 0.048783
71054 | L_SWEETW1_1N | W1 | West | YES | 0.25649 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 107.5 | 27.5722 | 107.5 |  |  | 0.27756 | 29.8374 | 0.68285 | 0.73034 |  |  |  |  | 71 | 0.048517
71057 | L_SWEETW1_2N | W1 | West | YES | 0.25649 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 135 | 34.6256 | 135 |  |  | 0.27756 | 37.4702 | 0.6953 | 0.7423 |  |  |  |  | 72 | 0.048008
71059 | L_SWEETW1_3N | W1 | West | YES | 0.25649 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 119 | 30.5218 | 119 |  |  | 0.27756 | 33.0293 | 0.70627 | 0.75284 |  |  |  |  | 73 | 0.047873
71060 | L_SWEETW1_4N | W1 | West | YES | 0.25649 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 105 | 26.931 | 105 |  |  | 0.27756 | 29.1435 | 0.71596 | 0.76215 |  |  |  |  | 74 | 0.047486
71061 | L_SWEETW1_5N | W1 | West | YES | 0.25649 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 80.5 | 20.6471 | 80.5 |  |  | 0.27756 | 22.3433 | 0.72338 | 0.76928 |  |  |  |  | 75 | 0.046999
36998 | RDCNYNG1 | 1 | West | YES | 0.25225 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.27332 | 0 | 84 | 21.1888 | 84 |  |  | 0.27332 | 22.9588 | 0.73113 | 0.77661 |  |  |  |  | 76 | 0.04657
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.25162 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.27269 | 0 | 112.5 | 28.3074 | 112.5 |  |  | 0.27269 | 30.6778 | 0.7415 | 0.7864 |  |  |  |  | 77 | 0.046191
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.25162 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 149.5 | 37.6173 | 149.5 |  |  | 0.27269 | 40.7674 | 0.75529 | 0.79942 |  |  |  |  | 78 | 0.045901
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.25162 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 186 | 46.8015 | 186 |  |  | 0.27269 | 50.7207 | 0.77244 | 0.81561 |  |  |  |  | 79 | 0.045485
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.25162 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 214.5 | 53.9727 | 214.5 |  |  | 0.27269 | 58.4924 | 0.79222 | 0.83429 |  |  |  |  | 80 | 0.044904
60017 | ORNNWP1 | 1 | West | YES | 0.24984 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.27091 | 0 | 80 | 19.987 | 80 |  |  | 0.27091 | 21.6726 | 0.7996 | 0.84121 |  |  |  |  | 81 | 0.044133
60018 | DSKY1 | 1 | West | YES | 0.24737 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.26844 | 0 | 84 | 20.7789 | 84 |  |  | 0.26844 | 22.5489 | 0.80734 | 0.8484 |  |  |  |  | 82 | 0.043174
60000 | DSKY2 | 1 | West | YES | 0.24668 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.26775 | 0 | 76.5 | 18.8706 | 76.5 |  |  | 0.26775 | 20.4826 | 0.8144 | 0.85494 |  |  |  |  | 83 | 0.042067
1343 | TRENTIPP_8 | 1 | West | YES | 0.2173 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.23837 | 0 | 150 | 32.5951 | 150 |  |  | 0.23837 | 35.7558 | 0.82823 | 0.86636 |  |  |  |  | 84 | 0.041609
1354 | AEPWIND_8 | 1 | West | YES | 0.2173 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.23837 | 0 | 101 | 21.9474 | 101 |  |  | 0.23837 | 24.0756 | 0.83754 | 0.87404 |  |  |  |  | 85 | 0.041062
60202 | FRNDDRCS | F | West | YES | 0.21035 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.23142 | 0 | 0 | 0 | 0 |  |  | 0.23142 | 0 | 0.83754 | 0.87404 |  |  |  |  | 86 | 0.040546
60058 | BUFF_GAP1A | 1 | West | YES | 0.20991 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.23098 | 0 | 120 | 25.189 | 120 |  |  | 0.23098 | 27.7175 | 0.84861 | 0.88289 |  |  |  |  | 87 | 0.038129
60060 | CIRELLO | 1 | West | YES | 0.20991 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.23098 | 0 | 233 | 48.9086 | 233 |  |  | 0.23098 | 53.8181 | 0.8701 | 0.90007 |  |  |  |  | 88 | 0.036501
60063 | BUFF_GAP1B | 1 | West | YES | 0.20991 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.23098 | 0 | 170.2 | 35.7263 | 170.2 |  |  | 0.23098 | 39.3126 | 0.88579 | 0.91263 |  |  |  |  | 89 | 0.036501
60066 | H_HOLLOW1A | 1 | West | YES | 0.20991 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.23098 | 0 | 222 | 46.5996 | 222 |  |  | 0.23098 | 51.2773 | 0.90626 | 0.929 |  |  |  |  | 90 | 0.034284
60068 | HHOLLOW21A | 1 | West | YES | 0.20991 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 184 | 38.6231 | 184 |  |  | 0.23098 | 42.5001 | 0.92323 | 0.94256 |  |  |  |  | 91 | 0.029979
60070 | HHOLLOW31A | 1 | West | YES | 0.20991 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 224 | 47.0194 | 224 |  |  | 0.23098 | 51.7393 | 0.94389 | 0.95908 |  |  |  |  | 92 | 0.026835
60072 | HHOLLOW41A | 1 | West | YES | 0.20991 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 115 | 24.1394 | 115 |  |  | 0.23098 | 26.5626 | 0.95449 | 0.96756 |  |  |  |  | 93 | 0.022733
6144 | MCADOO1A | 1 | West | YES | 0.20699 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.22806 | 0 | 150 | 31.0488 | 150 |  |  | 0.22806 | 34.2094 | 0.96832 | 0.97848 |  |  |  |  | 94 | 0.019334
60057 | CALLAHAN1A | 1 | West | YES | 0.1794 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.20047 | 0 | 114 | 20.4511 | 114 |  |  | 0.20047 | 22.8532 | 0.97884 | 0.98578 |  |  |  |  | 95 | 0.015195
6407 | TURKTRAK1A | 1 | West | YES | 0.17738 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.19846 | 0 | 169.5 | 30.0668 | 169.5 |  |  | 0.19846 | 33.6383 | 0.99447 | 0.99652 |  |  |  |  | 96 | 0.013071
60081 | WHRLWIND1A | 1 | West | YES | 0.16067 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.18174 | 0 | 60 | 9.6403 | 60 |  |  | 0.18174 | 10.9046 | 1 | 1 |  |  |  |  | 97 | 0.01016
6100 | OKLA7A | EQ | West | YES | 0.065172 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.086243 | 0 | 0 | 0 | 0 |  |  | 0.086243 | 0 | 1 | 1 |  |  |  |  | 98 | 0.0069432
6752 | OKLA0A | 1 | West | YES | 0.065172 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.086243 | 0 | 649.7 | 42.3422 | 649.7 |  |  | 0.086243 | 56.0319 | 1.0599 | 1.0179 |  |  |  |  | 99 | 0.0020516
1438 | MESQUITW_2G | 1 | North | YES | 0.23272 | 23.6 | 0 | 236 |  | 1.017 | Wind | -1 | 0.023604 | 0 | 236 |  |  | 0 | 0 | -0.023604 | 0 | [6 empty] | 100 | 0
1442 | COKFIELD_5 | 1 | North | YES | 0.23272 | 16.5 | 0 | 165 |  | 1.029 | Wind | -1 | 0.023604 | 0 | 165 |  |  | 0 | 0 | -0.023604 | 0 | [6 empty] | 101 | 0
1437 | MESQUITW_1G | 1 | North | YES | 0.23258 | 40 | 0 | 400 | 0 | 1.023 | Wind | -1 | 0.023741 | 0 | 400 |  |  | 0 | 0 | -0.023741 | 0 | [6 empty] | 102 | -0.042024
8032 | AMISTADHYD1 | 1 | South | YES | 0.070288 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 | [6 empty] | 103 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.070288 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 | [6 empty] | 104 | 0
88253 | HAMILTON | F | South | YES | 0.070288 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 | [6 empty] | 105 | 0
8262 | ELPS | 1 | South | YES | 0.050982 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.20534 | 0 | 0 |  |  |  |  | -0.20534 | 0 | [6 empty] | 106 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.019601 | 6 | 0 | 60 | 0 | 1.022 | Wind | -1 | 0.23673 | 0 | 60 |  |  | 0 | 0 | -0.23673 | 0 | [6 empty] | 107 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.011136 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.24519 | 0 | 0 |  |  |  |  | -0.24519 | 0 | [6 empty] | 108 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 109 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 110 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 111 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 112 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 113 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 114 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 115 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 116 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 117 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 118 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 119 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 120 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 121 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 122 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 123 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 124 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 125 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 126 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 127 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 128 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 129 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 130 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 131 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | [6 empty] | 132 | 0
80265 | LARECU40A | 4 | South | YES | 0.008895 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.24743 | 100 | 100 |  |  |  |  | -0.24743 | -24.7431 | [6 empty] | 133 | 0
80266 | LARECU50A | 5 | South | YES | 0.008895 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.24743 | 100 | 100 |  |  |  |  | -0.24743 | -24.7431 | [6 empty] | 134 | 0
80012 | LAR | F | South | YES | 0.008892 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.24743 | 0 | 0 |  |  |  |  | -0.24743 | 0 | [6 empty] | 135 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | 0.008293 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.24803 | 24 | 24 |  |  |  |  | -0.24803 | -5.9528 | [6 empty] | 136 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | 0.008293 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.24803 | 24.3 | 24.3 |  |  |  |  | -0.24803 | -6.0272 | [6 empty] | 137 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | 0.008293 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.24803 | 23.9 | 23.9 |  |  |  |  | -0.24803 | -5.928 | [6 empty] | 138 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | 0.007166 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.24916 | 423.3 | 423.3 |  |  |  |  | -0.24916 | -105.4695 | [6 empty] | 139 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.007137 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 | [6 empty] | 140 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.007137 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 | [6 empty] | 141 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.007137 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 | [6 empty] | 142 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | 0.006511 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.24982 | 0 | 0 |  |  |  |  | -0.24982 | 0 | [6 empty] | 143 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | 0.006511 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.24982 | 0 | 0 |  |  |  |  | -0.24982 | 0 | [6 empty] | 144 | 0
88299 | ZAPATA | F | South | YES | 0.004802 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.25152 | 0 | 0 |  |  |  |  | -0.25152 | 0 | [6 empty] | 145 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | 0.004572 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.25175 | 0 | 0 |  |  |  |  | -0.25175 | 0 | [6 empty] | 146 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | 0.004572 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.25175 | 0 | 0 |  |  |  |  | -0.25175 | 0 | [6 empty] | 147 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | 0.002028 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 | [6 empty] | 148 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 0.002028 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 | [6 empty] | 149 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 0.002028 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 | [6 empty] | 150 | 0
88508 | FALFURRI | F | South | YES | 0.001585 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.25474 | 0 | 0 |  |  |  |  | -0.25474 | 0 | [6 empty] | 151 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.25633 | 15 | 15 |  |  |  |  | -0.25633 | -3.8449 | [6 empty] | 152 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 153 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 154 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 155 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 156 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 157 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 158 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 159 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 160 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | [6 empty] | 161 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.000265 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.25659 | 58 | 58 |  |  |  |  | -0.25659 | -14.8823 | [6 empty] | 162 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | -0.000265 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.25659 | 89 | 89 |  |  |  |  | -0.25659 | -22.8366 | [6 empty] | 163 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | -0.000265 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.25659 | 44 | 44 |  |  |  |  | -0.25659 | -11.29 | [6 empty] | 164 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | -0.000265 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.25659 | 44 | 44 |  |  |  |  | -0.25659 | -11.29 | [6 empty] | 165 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | -0.000265 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.25659 | 43 | 43 |  |  |  |  | -0.25659 | -11.0334 | [6 empty] | 166 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | -0.000265 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.25659 | 45 | 45 |  |  |  |  | -0.25659 | -11.5466 | [6 empty] | 167 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.000719 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.25705 | 407 | 407 |  |  |  |  | -0.25705 | -104.6174 | [6 empty] | 168 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.000795 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 | [6 empty] | 169 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.000795 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 | [6 empty] | 170 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.000795 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 | [6 empty] | 171 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.000856 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.25718 | 215 | 215 |  |  |  |  | -0.25718 | -55.2942 | [6 empty] | 172 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.000856 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.25718 | 216 | 216 |  |  |  |  | -0.25718 | -55.5514 | [6 empty] | 173 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.000864 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.25719 | 418 | 418 |  |  |  |  | -0.25719 | -107.5055 | [6 empty] | 174 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | -0.000864 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.25719 | 400 | 400 |  |  |  |  | -0.25719 | -102.8761 | [6 empty] | 175 | 0
8933 | FGNTS001 | 1 | South | YES | -0.000871 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.2572 | 146.5 | 146.5 |  |  |  |  | -0.2572 | -37.6794 | [6 empty] | 176 | 0
8934 | FGNTS101 | 2 | South | YES | -0.000871 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.2572 | 147.9 | 147.9 |  |  |  |  | -0.2572 | -38.0395 | [6 empty] | 177 | 0
8935 | FGNTS201 | 3 | South | YES | -0.000871 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.2572 | 173 | 173 |  |  |  |  | -0.2572 | -44.4951 | [6 empty] | 178 | 0
88198 | BEEVILLE | F | South | YES | -0.000901 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.25723 | 0 | 0 |  |  |  |  | -0.25723 | 0 | [6 empty] | 179 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | -0.00095 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.25728 | 0 | 430 |  |  |  |  | -0.25728 | 0 | [6 empty] | 180 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.00095 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.25728 | 0 | 430 |  |  |  |  | -0.25728 | 0 | [6 empty] | 181 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.001181 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.25751 | 0 | 396.3 |  |  |  |  | -0.25751 | 0 | [6 empty] | 182 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.001247 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.25757 | 61 | 61 |  |  |  |  | -0.25757 | -15.712 | [6 empty] | 183 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.001247 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.25757 | 95 | 95 |  |  |  |  | -0.25757 | -24.4695 | [6 empty] | 184 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.001247 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.25757 | 151 | 151 |  |  |  |  | -0.25757 | -38.8936 | [6 empty] | 185 | 0
8981 | HECN1 | 1 | South | YES | -0.001359 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.25769 | 144.8 | 144.8 |  |  |  |  | -0.25769 | -37.3128 | [6 empty] | 186 | 0
8982 | HECN2 | 2 | South | YES | -0.001359 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.25769 | 144.1 | 144.1 |  |  |  |  | -0.25769 | -37.1324 | [6 empty] | 187 | 0
8983 | HECN3 | 3 | South | YES | -0.001359 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.25769 | 171.9 | 171.9 |  |  |  |  | -0.25769 | -44.2961 | [6 empty] | 188 | 0
8936 | MVGN#1 | 1 | South | YES | -0.00136 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.25769 | 216.6 | 216.6 |  |  |  |  | -0.25769 | -55.8148 | [6 empty] | 189 | 0
8937 | MVGN#2 | 2 | South | YES | -0.00136 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.25769 | 216.7 | 216.7 |  |  |  |  | -0.25769 | -55.8406 | [6 empty] | 190 | 0
8938 | MVGN#3 | 3 | South | YES | -0.00136 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.25769 | 250.9 | 250.9 |  |  |  |  | -0.25769 | -64.6535 | [6 empty] | 191 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.001366 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.25769 | 155 | 155 |  |  |  |  | -0.25769 | -39.9423 | [6 empty] | 192 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | -0.001366 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.25769 | 174 | 174 |  |  |  |  | -0.25769 | -44.8384 | [6 empty] | 193 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.001366 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.25769 | 155 | 155 |  |  |  |  | -0.25769 | -39.9423 | [6 empty] | 194 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.001502 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.25783 | 0 | 562 |  |  |  |  | -0.25783 | 0 | [6 empty] | 195 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.001567 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.25789 | 38 | 38 |  |  |  |  | -0.25789 | -9.7999 | [6 empty] | 196 | 0
5933 | SI_RAY6 | 6 | South | YES | -0.001567 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.25789 | 19.3 | 19.3 |  |  |  |  | -0.25789 | -4.9773 | [6 empty] | 197 | 0
5935 | SI_RAY10 | 10 | South | YES | -0.001567 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.25789 | 47 | 47 |  |  |  |  | -0.25789 | -12.121 | [6 empty] | 198 | 0
80003 | MILHWYS | F | South | YES | -0.001567 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.25789 | 0 | 0 |  |  |  |  | -0.25789 | 0 | [6 empty] | 199 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.001676 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.258 | 0 | 0 |  |  |  |  | -0.258 | 0 | [6 empty] | 200 | 0
80080 | GWINDT11A | 3 | South | YES | -0.001696 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 38 |  |  |  |  | -0.25802 | 0 | [6 empty] | 201 | 0
80080 | GWINDT11A | 4 | South | YES | -0.001696 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 19 |  |  |  |  | -0.25802 | 0 | [6 empty] | 202 | 0
80080 | GWINDT11A | 2 | South | YES | -0.001696 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 41 |  |  |  |  | -0.25802 | 0 | [6 empty] | 203 | 0
80080 | GWINDT11A | 1 | South | YES | -0.001696 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 94 |  |  |  |  | -0.25802 | 0 | [6 empty] | 204 | 0
80081 | GWINDT21A | 4 | South | YES | -0.001696 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 22 |  |  |  |  | -0.25802 | 0 | [6 empty] | 205 | 0
80081 | GWINDT21A | 1 | South | YES | -0.001696 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 94 |  |  |  |  | -0.25802 | 0 | [6 empty] | 206 | 0
80081 | GWINDT21A | 3 | South | YES | -0.001696 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 43 |  |  |  |  | -0.25802 | 0 | [6 empty] | 207 | 0
80081 | GWINDT21A | 2 | South | YES | -0.001696 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 36 |  |  |  |  | -0.25802 | 0 | [6 empty] | 208 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.001696 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 50 |  |  |  |  | -0.25802 | 0 | [6 empty] | 209 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.001696 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 148 |  |  |  |  | -0.25802 | 0 | [6 empty] | 210 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.001696 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 50 |  |  |  |  | -0.25802 | 0 | [6 empty] | 211 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.001696 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 55 |  |  |  |  | -0.25802 | 0 | [6 empty] | 212 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.001777 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.2581 | 0 | 0 |  |  |  |  | -0.2581 | 0 | [6 empty] | 213 | 0
8506 | VAL #1 | 1 | South | YES | -0.001811 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 | [6 empty] | 214 | 0
8507 | VAL #2 | 2 | South | YES | -0.001811 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 | [6 empty] | 215 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.001811 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 | [6 empty] | 216 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.001863 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.25819 | 0 | 0 |  |  |  |  | -0.25819 | 0 | [6 empty] | 217 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.001863 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.25819 | 0 | 0 |  |  |  |  | -0.25819 | 0 | [6 empty] | 218 | 0
80263 | B_DAVIS31A | 3 | South | YES | -0.001863 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.25819 | 180 | 180 |  |  |  |  | -0.25819 | -46.4741 | [6 empty] | 219 | 0
80264 | B_DAVIS41A | 4 | South | YES | -0.001863 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.25819 | 180 | 180 |  |  |  |  | -0.25819 | -46.4741 | [6 empty] | 220 | 0
8456 | COSW#1 | 1 | South | YES | -0.001877 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.2582 | 0 | 0 |  |  |  |  | -0.2582 | 0 | [6 empty] | 221 | 0
8457 | COSW#2 | 2 | South | YES | -0.001877 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.2582 | 0 | 0 |  |  |  |  | -0.2582 | 0 | [6 empty] | 222 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.001889 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 | [6 empty] | 223 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.001889 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 | [6 empty] | 224 | 0
8562 | CNOPST1 | 3 | South | YES | -0.001889 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 | [6 empty] | 225 | 0
8442 | NBEC7 | 7 | South | YES | -0.001892 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.25822 | 367 | 367 |  |  |  |  | -0.25822 | -94.7661 | [6 empty] | 226 | 0
8442 | NBEC7 | MB | South | YES | -0.001892 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 | [6 empty] | 227 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.001991 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.25832 | 0 | 0 |  |  |  |  | -0.25832 | 0 | [6 empty] | 228 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.002067 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.25839 | 0 | 0 |  |  |  |  | -0.25839 | 0 | [6 empty] | 229 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.002126 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | [6 empty] | 230 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.002126 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | [6 empty] | 231 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.002126 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | [6 empty] | 232 | 0
8930 | ICPGN10A | 1 | South | YES | -0.002126 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | [6 empty] | 233 | 0
8931 | ICPGN20A | 2 | South | YES | -0.002126 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | [6 empty] | 234 | 0
8932 | ICPGN30A | 3 | South | YES | -0.002126 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | [6 empty] | 235 | 0
80223 | REYSHR G | 1 | South | YES | -0.002126 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | [6 empty] | 236 | 0
8161 | COLETO0A | 1 | South | YES | -0.002182 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.25851 | 0 | 633 |  |  |  |  | -0.25851 | 0 | [6 empty] | 237 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.002314 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.25864 | 147 | 147 |  |  |  |  | -0.25864 | -38.0201 | [6 empty] | 238 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.002314 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.25864 | 138 | 138 |  |  |  |  | -0.25864 | -35.6923 | [6 empty] | 239 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.002314 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.25864 | 146 | 146 |  |  |  |  | -0.25864 | -37.7615 | [6 empty] | 240 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.002314 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.25864 | 149 | 149 |  |  |  |  | -0.25864 | -38.5374 | [6 empty] | 241 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.002314 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.25864 | 182 | 182 |  |  |  |  | -0.25864 | -47.0725 | [6 empty] | 242 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.002314 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.25864 | 203 | 203 |  |  |  |  | -0.25864 | -52.504 | [6 empty] | 243 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.0024 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 | [6 empty] | 244 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.0024 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 | [6 empty] | 245 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.0024 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 | [6 empty] | 246 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.002549 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.25888 | 148 | 148 |  |  |  |  | -0.25888 | -38.3135 | [6 empty] | 247 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.002549 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.25888 | 148 | 148 |  |  |  |  | -0.25888 | -38.3135 | [6 empty] | 248 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.002549 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.25888 | 154 | 154 |  |  |  |  | -0.25888 | -39.8668 | [6 empty] | 249 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.002549 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.25888 | 293 | 293 |  |  |  |  | -0.25888 | -75.8504 | [6 empty] | 250 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.002697 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.25902 | 0 | 0 |  |  |  |  | -0.25902 | 0 | [6 empty] | 251 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.002697 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.25902 | 0 | 0 |  |  |  |  | -0.25902 | 0 | [6 empty] | 252 | 0
8189 | CUECPL2A | 1 | South | YES | -0.00272 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.25905 | 0 | 0 |  |  |  |  | -0.25905 | 0 | [6 empty] | 253 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.002752 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.25908 | 22 | 22 |  |  |  |  | -0.25908 | -5.6997 | [6 empty] | 254 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | -0.002752 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.25908 | 11 | 11 |  |  |  |  | -0.25908 | -2.8499 | [6 empty] | 255 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | -0.002752 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.25908 | 11 | 11 |  |  |  |  | -0.25908 | -2.8499 | [6 empty] | 256 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.00278 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.25911 | 223.9 | 223.9 |  |  |  |  | -0.25911 | -58.0139 | [6 empty] | 257 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.00278 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.25911 | 225 | 225 |  |  |  |  | -0.25911 | -58.2989 | [6 empty] | 258 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.00278 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.25911 | 224.6 | 224.6 |  |  |  |  | -0.25911 | -58.1953 | [6 empty] | 259 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.00278 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.25911 | 226.7 | 226.7 |  |  |  |  | -0.25911 | -58.7394 | [6 empty] | 260 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.002955 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.25928 | 47.7 | 47.7 |  |  |  |  | -0.25928 | -12.3677 | [6 empty] | 261 | 0
5509 | RAYBURNCC10 | 1 | South | YES | -0.002955 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.25928 | 37.3 | 37.3 |  |  |  |  | -0.25928 | -9.6712 | [6 empty] | 262 | 0
5511 | RAYBURNCC7 | 1 | South | YES | -0.002955 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.25928 | 47.5 | 47.5 |  |  |  |  | -0.25928 | -12.3159 | [6 empty] | 263 | 0
5512 | RAYBURNCC8 | 1 | South | YES | -0.002955 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.25928 | 49.3 | 49.3 |  |  |  |  | -0.25928 | -12.7826 | [6 empty] | 264 | 0
8173 | VICEC51A | 5 | South | YES | -0.002999 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.25933 | 144 | 144 |  |  |  |  | -0.25933 | -37.3428 | [6 empty] | 265 | 0
8174 | VICEC61A | 6 | South | YES | -0.002999 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.25933 | 188 | 188 |  |  |  |  | -0.25933 | -48.7531 | [6 empty] | 266 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.003094 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.25942 | 0 | 0 |  |  |  |  | -0.25942 | 0 | [6 empty] | 267 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.00321 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.25954 | 0 | 0 |  |  |  |  | -0.25954 | 0 | [6 empty] | 268 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.00321 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.25954 | 0 | 0 |  |  |  |  | -0.25954 | 0 | [6 empty] | 269 | 0
80227 | AIRCO G | 1 | South | YES | -0.003228 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.25955 | 0 | 0 |  |  |  |  | -0.25955 | 0 | [6 empty] | 270 | 0
8147 | UCAR #2 | 10 | South | YES | -0.003309 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | [6 empty] | 271 | 0
8148 | UCAR #1 | 2 | South | YES | -0.003309 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | [6 empty] | 272 | 0
80137 | CSDR89 | 9 | South | YES | -0.003309 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | [6 empty] | 273 | 0
80137 | CSDR89 | 8 | South | YES | -0.003309 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | [6 empty] | 274 | 0
80138 | CSDR7 | 7 | South | YES | -0.003309 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | [6 empty] | 275 | 0
80139 | CSDR56 | 6 | South | YES | -0.003309 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | [6 empty] | 276 | 0
80139 | CSDR56 | 5 | South | YES | -0.003309 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | [6 empty] | 277 | 0
80140 | CSDR11 | 11 | South | YES | -0.003309 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | [6 empty] | 278 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.00335 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.25968 | 0 | 0 |  |  |  |  | -0.25968 | 0 | [6 empty] | 279 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.00335 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.25968 | 0 | 0 |  |  |  |  | -0.25968 | 0 | [6 empty] | 280 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.003618 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.25994 | 49 | 49 |  |  |  |  | -0.25994 | -12.7373 | [6 empty] | 281 | 0
9017 | SANDH_G2 | 2 | South | YES | -0.003618 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.25994 | 46 | 46 |  |  |  |  | -0.25994 | -11.9574 | [6 empty] | 282 | 0
9018 | SANDH_G3 | 3 | South | YES | -0.003618 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.25994 | 46 | 46 |  |  |  |  | -0.25994 | -11.9574 | [6 empty] | 283 | 0
9019 | SANDH_G4 | 4 | South | YES | -0.003618 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.25994 | 47 | 47 |  |  |  |  | -0.25994 | -12.2174 | [6 empty] | 284 | 0
9020 | SANDHG5A | 5A | South | YES | -0.003618 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.25994 | 155 | 155 |  |  |  |  | -0.25994 | -40.2914 | [6 empty] | 285 | 0
9021 | SANDHG5C | 5C | South | YES | -0.003618 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.25994 | 148 | 148 |  |  |  |  | -0.25994 | -38.4717 | [6 empty] | 286 | 0
9000 | DECKR_G1 | 1 | South | YES | -0.003627 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.25995 | 321 | 321 |  |  |  |  | -0.25995 | -83.445 | [6 empty] | 287 | 0
9001 | DECKR_G2 | 2 | South | YES | -0.003627 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.25995 | 426 | 426 |  |  |  |  | -0.25995 | -110.7401 | [6 empty] | 288 | 0
80226 | ALCOA G | 1 | South | YES | -0.003687 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.26001 | 0 | 0 |  |  |  |  | -0.26001 | 0 | [6 empty] | 289 | 0
8134 | FOR #1 | 1 | South | YES | -0.003787 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 290 | 0
8138 | FOR #2 | 2 | South | YES | -0.003787 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 291 | 0
8153 | FOR #3 | 3 | South | YES | -0.003787 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 292 | 0
8154 | FOR #4 | 4 | South | YES | -0.003787 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 293 | 0
8155 | FOR #5 | 5 | South | YES | -0.003787 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 294 | 0
8156 | FOR #6 | 6 | South | YES | -0.003787 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 295 | 0
8157 | FOR #7 | 7 | South | YES | -0.003787 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 296 | 0
80051 | FOR #8 | 8 | South | YES | -0.003787 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 297 | 0
80052 | FOR #9 | 9 | South | YES | -0.003787 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 298 | 0
80053 | FOR #10 | 10 | South | YES | -0.003787 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | [6 empty] | 299 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.003822 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.26015 | 42 | 42 |  |  |  |  | -0.26015 | -10.9262 | [6 empty] | 300 | 0
9003 | DECKR_G4 | 4 | South | YES | -0.003822 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.26015 | 44 | 44 |  |  |  |  | -0.26015 | -11.4465 | [6 empty] | 301 | 0
9004 | DECKR_G5 | 5 | South | YES | -0.003822 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.26015 | 44 | 44 |  |  |  |  | -0.26015 | -11.4465 | [6 empty] | 302 | 0
9005 | DECKR_G6 | 6 | South | YES | -0.003822 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.26015 | 47 | 47 |  |  |  |  | -0.26015 | -12.227 | [6 empty] | 303 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.004292 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.26062 | 132 | 132 |  |  |  |  | -0.26062 | -34.4016 | [6 empty] | 304 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.004292 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.26062 | 139 | 139 |  |  |  |  | -0.26062 | -36.2259 | [6 empty] | 305 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.004292 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.26062 | 329 | 329 |  |  |  |  | -0.26062 | -85.7434 | [6 empty] | 306 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.004759 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.26109 | 152.5 | 152.5 |  |  |  |  | -0.26109 | -39.8155 | [6 empty] | 307 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.004759 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.26109 | 149.5 | 149.5 |  |  |  |  | -0.26109 | -39.0322 | [6 empty] | 308 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.004759 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.26109 | 232.6 | 232.6 |  |  |  |  | -0.26109 | -60.7284 | [6 empty] | 309 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 | [6 empty] | 310 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 | [6 empty] | 311 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 | [6 empty] | 312 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 | [6 empty] | 313 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.005252 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.26158 | 158 | 158 |  |  |  |  | -0.26158 | -41.3294 | [6 empty] | 314 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.005252 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.26158 | 160 | 160 |  |  |  |  | -0.26158 | -41.8525 | [6 empty] | 315 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.005252 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.26158 | 175 | 175 |  |  |  |  | -0.26158 | -45.7762 | [6 empty] | 316 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.005273 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 436 |  |  |  |  | -0.2616 | 0 | [6 empty] | 317 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.005275 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 606 |  |  |  |  | -0.2616 | 0 | [6 empty] | 318 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.005275 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 598 |  |  |  |  | -0.2616 | 0 | [6 empty] | 319 | 0
3432 | SANDOW_4G | 4 | South | YES | -0.006951 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.26328 | 0 | 580 |  |  |  |  | -0.26328 | 0 | [6 empty] | 320 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.007142 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.26347 | 0 | 0 |  |  |  |  | -0.26347 | 0 | [6 empty] | 321 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.007142 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.26347 | 0 | 0 |  |  |  |  | -0.26347 | 0 | [6 empty] | 322 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 | [6 empty] | 323 | 0
48732 | CBE_GT2 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 | [6 empty] | 324 | 0
48733 | CBE_ST12 | 1 | Houston | YES | -0.007274 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.2636 | 105 | 105 |  |  |  |  | -0.2636 | -27.678 | [6 empty] | 325 | 0
48734 | CBE_GT3 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 | [6 empty] | 326 | 0
48735 | CBE_GT4 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 | [6 empty] | 327 | 0
48736 | CBE_ST34 | 1 | Houston | YES | -0.007274 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.2636 | 105 | 105 |  |  |  |  | -0.2636 | -27.678 | [6 empty] | 328 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.007407 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.26373 | 0 | 0 |  |  |  |  | -0.26373 | 0 | [6 empty] | 329 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.008243 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 330 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.008243 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 331 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.008243 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 332 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.008243 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 333 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.008243 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 334 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.008243 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 335 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.008243 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 336 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.008243 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 337 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.008243 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 338 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.008243 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 339 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.008243 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 340 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.008243 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 341 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.008243 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 342 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.008243 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 343 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.008243 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 344 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.008243 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 345 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.008243 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 346 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.008243 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 347 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.008243 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 348 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.008243 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | [6 empty] | 349 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.008279 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.26461 | 0 | 581 |  |  |  |  | -0.26461 | 0 | [6 empty] | 350 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.008444 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.26477 | 0 | 0 |  |  |  |  | -0.26477 | 0 | [6 empty] | 351 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.008444 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.26477 | 0 | 0 |  |  |  |  | -0.26477 | 0 | [6 empty] | 352 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.008613 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 | [6 empty] | 353 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.008613 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 | [6 empty] | 354 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.008613 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 | [6 empty] | 355 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.008613 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 | [6 empty] | 356 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.009168 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.26549 | 0 | 0 |  |  |  |  | -0.26549 | 0 | [6 empty] | 357 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.009208 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 651 |  |  |  |  | -0.26553 | 0 | [6 empty] | 358 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.009208 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 564 |  |  |  |  | -0.26553 | 0 | [6 empty] | 359 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.009208 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 603 |  |  |  |  | -0.26553 | 0 | [6 empty] | 360 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.009212 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.26554 | 167.7 | 167.7 |  |  |  |  | -0.26554 | -44.5308 | [6 empty] | 361 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.009212 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.26554 | 166.4 | 166.4 |  |  |  |  | -0.26554 | -44.1856 | [6 empty] | 362 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.009212 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.26554 | 252.4 | 252.4 |  |  |  |  | -0.26554 | -67.0218 | [6 empty] | 363 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.009252 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.26558 | 0 | 0 |  |  |  |  | -0.26558 | 0 | [6 empty] | 364 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.009316 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.26564 | 166 | 166 |  |  |  |  | -0.26564 | -44.0966 | [6 empty] | 365 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.009316 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.26564 | 166 | 166 |  |  |  |  | -0.26564 | -44.0966 | [6 empty] | 366 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.009316 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.26564 | 248 | 248 |  |  |  |  | -0.26564 | -65.8793 | [6 empty] | 367 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.009316 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.26564 | 546 | 546 |  |  |  |  | -0.26564 | -145.0406 | [6 empty] | 368 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.009316 | 620.4 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.26564 | 0 | 654 |  |  |  |  | -0.26564 | 0 | [6 empty] | 369 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.009316 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.26564 | 13 | 13 |  |  |  |  | -0.26564 | -3.4533 | [6 empty] | 370 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.009621 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 371 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.009621 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 372 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.009621 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 373 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.009621 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 374 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.009621 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 375 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.009621 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 376 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.009621 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 377 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.009621 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 378 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.009621 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 379 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.009621 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 380 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.009621 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 381 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.009621 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 382 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.009621 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 383 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.009621 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 384 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.009621 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | [6 empty] | 385 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.009768 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.26609 | 0 | 0 |  |  |  |  | -0.26609 | 0 | [6 empty] | 386 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.009872 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | [6 empty] | 387 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.009872 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | [6 empty] | 388 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.009872 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | [6 empty] | 389 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.009872 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | [6 empty] | 390 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.009872 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.009911 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.009911 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.009911 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.009911 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161
48691 | GBY_73741085 | A | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161
48692 | GBY_81821075 | D | Houston | YES | -0.009973 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.2663 | 55 | 55 |  |  |  |  | -0.2663 | -14.6465
48692 | GBY_81821075 | C | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161
48693 | GBY_83841065 | F | Houston | YES | -0.009973 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.2663 | 54 | 54 |  |  |  |  | -0.2663 | -14.3802
48693 | GBY_83841065 | E | Houston | YES | -0.009973 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.2663 | 57 | 57 |  |  |  |  | -0.2663 | -15.1791
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.009986 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.26631 | 0 | 0 |  |  |  |  | -0.26631 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.009986 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.26631 | 0 | 0 |  |  |  |  | -0.26631 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.010001 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.26633 | 163.2 | 163.2 |  |  |  |  | -0.26633 | -43.4646
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.010001 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.26633 | 157.1 | 157.1 |  |  |  |  | -0.26633 | -41.84
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.010001 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.26633 | 157.5 | 157.5 |  |  |  |  | -0.26633 | -41.9465
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.010001 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.26633 | 157 | 157 |  |  |  |  | -0.26633 | -41.8134
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.010001 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.26633 | 282 | 282 |  |  |  |  | -0.26633 | -75.1043
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.010025 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.26635 | 0 | 0 |  |  |  |  | -0.26635 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.010042 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.26637 | 18 | 18 |  |  |  |  | -0.26637 | -4.7946
48855 | SRB_GT211035 | B2 | Houston | YES | -0.010042 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.26637 | 12 | 12 |  |  |  |  | -0.26637 | -3.1964
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.010043 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.26637 | 176 | 176 |  |  |  |  | -0.26637 | -46.881
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.010044 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.26637 | 165 | 165 |  |  |  |  | -0.26637 | -43.9511
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.010045 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.26637 | 0 | 0 |  |  |  |  | -0.26637 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.010045 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.26637 | 0 | 0 |  |  |  |  | -0.26637 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.010049 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.26638 | 16.2 | 16.2 |  |  |  |  | -0.26638 | -4.3153
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.010049 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.26638 | 213 | 213 |  |  |  |  | -0.26638 | -56.7379
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.01005 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.01005 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.01005 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.01005 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.01005 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.26638 | 228 | 228 |  |  |  |  | -0.26638 | -60.7338
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.010051 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.010051 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.010051 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.010076 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.010076 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.010076 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.010076 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.010116 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.26644 | 0 | 0 |  |  |  |  | -0.26644 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.010119 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.26645 | 42 | 42 |  |  |  |  | -0.26645 | -11.1907
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.010119 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.26645 | 42 | 42 |  |  |  |  | -0.26645 | -11.1907
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.010119 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.26645 | 39 | 39 |  |  |  |  | -0.26645 | -10.3914
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.010119 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.26645 | 39 | 39 |  |  |  |  | -0.26645 | -10.3914
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.010129 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.26646 | 0 | 0 |  |  |  |  | -0.26646 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.010129 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.26646 | 0 | 0 |  |  |  |  | -0.26646 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.010189 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.26652 | 107 | 107 |  |  |  |  | -0.26652 | -28.5171
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.010189 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.26652 | 108 | 108 |  |  |  |  | -0.26652 | -28.7836
48875 | THW_3132 | A | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583
48875 | THW_3132 | B | Houston | YES | -0.010189 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.26652 | 53 | 53 |  |  |  |  | -0.26652 | -14.1253
48877 | THW_3334 | C | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583
48877 | THW_3334 | D | Houston | YES | -0.010189 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.26652 | 57 | 57 |  |  |  |  | -0.26652 | -15.1914
48879 | THW_4142 | E | Houston | YES | -0.010189 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.26652 | 56 | 56 |  |  |  |  | -0.26652 | -14.9249
48879 | THW_4142 | F | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583
48881 | THW_4344 | G | Houston | YES | -0.010189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.26652 | 58 | 58 |  |  |  |  | -0.26652 | -15.4579
48881 | THW_4344 | H | Houston | YES | -0.010189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.26652 | 58 | 58 |  |  |  |  | -0.26652 | -15.4579
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.010218 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.26654 | 746 | 746 |  |  |  |  | -0.26654 | -198.842
49803 | EXN_15GT | 1 | Houston | YES | -0.010247 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.010247 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.010247 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.010247 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.010247 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.010247 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.010247 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.010247 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.010247 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.010247 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.010247 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.01025 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.26658 | 12 | 12 |  |  |  |  | -0.26658 | -3.1989
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.010275 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.2666 | 744 | 744 |  |  |  |  | -0.2666 | -198.3513
48651 | EP_1_2 | 1 | Houston | YES | -0.010275 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.010275 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.010275 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.010279 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.010279 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.010279 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.010279 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.010279 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.010279 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.010279 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.010295 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.26662 | 0 | 0 |  |  |  |  | -0.26662 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.010346 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.26667 | 162.8 | 162.8 |  |  |  |  | -0.26667 | -43.4142
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.010346 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.26667 | 161.4 | 161.4 |  |  |  |  | -0.26667 | -43.0409
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.010346 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.26667 | 158.9 | 158.9 |  |  |  |  | -0.26667 | -42.3742
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.010346 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.26667 | 269.2 | 269.2 |  |  |  |  | -0.26667 | -71.7882
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.010366 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.26669 | 398 | 398 |  |  |  |  | -0.26669 | -106.1435
48885 | THW_5152 | B | Houston | YES | -0.010389 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.26672 | 59 | 59 |  |  |  |  | -0.26672 | -15.7362
48885 | THW_5152 | A | Houston | YES | -0.010389 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.26672 | 58 | 58 |  |  |  |  | -0.26672 | -15.4695
48886 | THW_5354 | D | Houston | YES | -0.010389 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.26672 | 58 | 58 |  |  |  |  | -0.26672 | -15.4695
48886 | THW_5354 | C | Houston | YES | -0.010389 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.26672 | 57 | 57 |  |  |  |  | -0.26672 | -15.2028
48887 | THW_5556 | E | Houston | YES | -0.010389 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.26672 | 59 | 59 |  |  |  |  | -0.26672 | -15.7362
48887 | THW_5556 | F | Houston | YES | -0.010389 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.26672 | 57 | 57 |  |  |  |  | -0.26672 | -15.2028
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.010673 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.010673 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.010673 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.010673 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.010673 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0
332 | RWMILLER01 | 1 | North | YES | -0.010926 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | -1 | 0.26725 | 73 | 73 |  |  | -0.7976 | 73 | -0.26725 | -19.5094
333 | RWMILLER02 | 2 | North | YES | -0.010926 | 95.2 | 37 | 119 | 0 | 1.04 | GST | -1 | 0.26725 | 119 | 119 |  |  | -1.3002 | 119 | -0.26725 | -31.803
334 | RWMILLER03 | 3 | North | YES | -0.010926 | 166.4 | 65 | 208 | 0 | 1.04 | GST | -1 | 0.26725 | 208 | 208 |  |  | -2.2726 | 208 | -0.26725 | -55.5885
335 | RWMILLER04 | 4 | North | YES | -0.010926 | 81.6 | 0 | 102 | 0 | 1.04 | GST | -1 | 0.26725 | 102 | 102 |  |  | -1.1145 | 102 | -0.26725 | -27.2597
336 | RWMILLER05 | 5 | North | YES | -0.010926 | 80.8 | 0 | 101 | 0 | 1.04 | GST | -1 | 0.26725 | 101 | 101 |  |  | -1.1035 | 101 | -0.26725 | -26.9925
251 | BOSQUESW803 | 2 | North | YES | -0.01188 | 150 | 0 | 150 | 0 | 1.032 | CC | -1 | 0.26821 | 150 | 150 |  |  | -1.782 | 150 | -0.26821 | -40.2309
253 | BOSQUESW804 | 2 | North | YES | -0.01188 | 80 | 0 | 80 | 0 | 1.032 | CC | -1 | 0.26821 | 80 | 80 |  |  | -0.9504 | 80 | -0.26821 | -21.4565
244 | WHITNYDM01 | 1 | North | YES | -0.012393 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.26872 | 0 | 0 |  |  | 0 | 0 | -0.26872 | 0
245 | WHITNYDM02 | 2 | North | YES | -0.012393 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.26872 | 0 | 0 |  |  | 0 | 0 | -0.26872 | 0
238 | BOSQUESW505 | 1 | North | YES | -0.013117 | 255 | 0 | 255 | 0 | 1.02 | CC | -1 | 0.26944 | 255 | 255 |  |  | -3.3448 | 255 | -0.26944 | -68.708
239 | BOSQUESW502 | 1 | North | YES | -0.013117 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | -1 | 0.26944 | 149 | 149 |  |  | -1.9544 | 149 | -0.26944 | -40.147
247 | BOSQUESW501 | 2 | North | YES | -0.013117 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | -1 | 0.26944 | 156 | 156 |  |  | -2.0463 | 156 | -0.26944 | -42.0331
48671 | FTR_GT1_5105 | 1 | North | YES | -0.013223 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | -1 | 0.26955 | 154.2 | 154.2 |  |  | -2.039 | 154.2 | -0.26955 | -41.5645
48672 | FTR_GT2_5110 | 2 | North | YES | -0.013223 | 159 | 0 | 159 | 0 | 1.0319 | CC | -1 | 0.26955 | 159 | 159 |  |  | -2.1025 | 159 | -0.26955 | -42.8583
48673 | FTR_GT3_5085 | 3 | North | YES | -0.013223 | 158 | 0 | 158 | 0 | 1.0319 | CC | -1 | 0.26955 | 158 | 158 |  |  | -2.0892 | 158 | -0.26955 | -42.5888
48674 | FTR_CN4_5095 | 4 | North | YES | -0.013223 | 380 | 0 | 380 | 0 | 1.0319 | CC | -1 | 0.26955 | 380 | 380 |  |  | -5.0247 | 380 | -0.26955 | -102.4287
3416 | LAKE_CRK1_G | 1 | North | YES | -0.013262 | 60 | 33 | 75 |  | 1.029 | GST | -1 | 0.26959 | 75 | 75 |  |  | -0.99465 | 75 | -0.26959 | -20.2191
3417 | LAKE_CRK2_G | 2 | North | YES | -0.013262 | 177.6 | 40 | 222 | 0 | 1.029 | GST | -1 | 0.26959 | 222 | 222 |  |  | -2.9442 | 222 | -0.26959 | -59.8486
1898 | COMCHEPK_1G | 1 | North | YES | -0.013425 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | -1 | 0.26975 | 0 | 0 |  |  | 0 | 0 | -0.26975 | 0
1899 | COMCHEPK_2G | 2 | North | YES | -0.013425 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | -1 | 0.26975 | 0 | 0 |  |  | 0 | 0 | -0.26975 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | -0.013678 | 0 | 2 | 48 |  | 1.015 | GST | -1 | 0.27 | 48 | 48 |  |  | -0.65654 | 48 | -0.27 | -12.9602
32884 | BRYN_DNSBY13 | 1 | North | YES | -0.013678 | 46 | 2 | 46 | 0 | 1.015 | GST | -1 | 0.27 | 46 | 46 |  |  | -0.62919 | 46 | -0.27 | -12.4202
32892 | BRYN_DNSBY14 | 1 | North | YES | -0.013678 | 84 | 25 | 105 | 0 | 1.035 | GST | -1 | 0.27 | 105 | 105 |  |  | -1.4362 | 105 | -0.27 | -28.3504
32886 | BRYN_ATKINS3 | MB | North | YES | -0.013721 | 0 | 5 | 12 |  | 1 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | -0.013721 | 0 | 12 | 51 |  | 1.028 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | -0.013721 | 13.6 | 4 | 17 |  | 1.028 | GGT | -1 | 0.27005 | 17 | 17 |  |  | -0.23326 | 17 | -0.27005 | -4.5908
32890 | BRYN_ATKINS4 | MB | North | YES | -0.013721 | 0 | 5 | 22 |  | 1.031 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | -0.013721 | 0 | 5 | 25 |  | 1.031 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | -0.013737 | 32 | 0 | 32 |  | 1.02 | GST | -1 | 0.27006 | 32 | 32 |  |  | -0.43958 | 32 | -0.27006 | -8.642
990 | GIBN_CREK_G1 | 1 | North | YES | -0.013752 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | -1 | 0.27008 | 0 | 463 |  |  | 0 | 0 | -0.27008 | 0
3403 | THOUSE_1G | 1 | North | YES | -0.013971 | 563 | 200 | 563 | 0 | 1.012 | GSC | -1 | 0.2703 | 563 | 563 |  |  | -7.8657 | 563 | -0.2703 | -152.1773
3404 | THOUSE_2G | 2 | North | YES | -0.013971 | 807 | 250 | 807 | 0 | 1.012 | GSC | -1 | 0.2703 | 807 | 807 |  |  | -11.2746 | 807 | -0.2703 | -218.1298
1877 | WLFHOLW_1G | 1 | North | YES | -0.014527 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | -1 | 0.27085 | 217.3 | 217.3 |  |  | -3.1567 | 217.3 | -0.27085 | -58.8564
1878 | WLFHOLW_2G | 2 | North | YES | -0.014527 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | -1 | 0.27085 | 215.7 | 215.7 |  |  | -3.1335 | 215.7 | -0.27085 | -58.423
1879 | WLFHOLW_3G | 3 | North | YES | -0.014527 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | -1 | 0.27085 | 272.4 | 272.4 |  |  | -3.9572 | 272.4 | -0.27085 | -73.7804
344 | MRSSHPRD | 1 | North | YES | -0.014638 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.27096 | 0 | 0 |  |  | 0 | 0 | -0.27096 | 0
345 | MRSSHPRD01 | 2 | North | YES | -0.014638 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.27096 | 0 | 0 |  |  | 0 | 0 | -0.27096 | 0
39960 | TNTNPONE_18 | 1 | North | YES | -0.015463 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | -1 | 0.27179 | 0 | 152.3 |  |  | 0 | 0 | -0.27179 | 0
39970 | TNTNPONE_28 | 1 | North | YES | -0.015463 | 153 | 30 | 153 |  | 1.04 | LIGCO | -1 | 0.27179 | 0 | 153 |  |  | 0 | 0 | -0.27179 | 0
366 | JNSNCNTY802 | 1 | North | YES | -0.015703 | 168 | 20 | 168 | 0 | 1.02 | Cogen | -1 | 0.27203 | 0 | 0 |  |  | 0 | 0 | -0.27203 | 0
367 | JNSNCNTY802 | 2 | North | YES | -0.015703 | 90 | 20 | 90 | 0 | 1.02 | Cogen | -1 | 0.27203 | 0 | 0 |  |  | 0 | 0 | -0.27203 | 0
1892 | DECRDOVA_2G | A | North | YES | -0.015865 | 65 | 65 | 70 | 0 | 1.025 | GGT | -1 | 0.27219 | 70 | 70 |  |  | -1.1105 | 70 | -0.27219 | -19.0534
1893 | DECRDOVA_3G | B | North | YES | -0.015865 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.27219 | 69 | 69 |  |  | -1.0947 | 69 | -0.27219 | -18.7812
1894 | DECRDOVA_4G | C | North | YES | -0.015865 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.27219 | 69 | 69 |  |  | -1.0947 | 69 | -0.27219 | -18.7812
1895 | DECRDOVA_5G | D | North | YES | -0.015865 | 65 | 65 | 68 | 0 | 1.025 | GGT | -1 | 0.27219 | 68 | 68 |  |  | -1.0788 | 68 | -0.27219 | -18.509
48721 | LEG_1___1 | 1 | North | YES | -0.016148 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | -1 | 0.27247 | 0 | 827 |  |  | 0 | 0 | -0.27247 | 0
48722 | LEG_2___2 | 2 | North | YES | -0.016148 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | -1 | 0.27247 | 0 | 819 |  |  | 0 | 0 | -0.27247 | 0
3381 | BBRN_1G | 1 | North | YES | -0.018042 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | -1 | 0.27437 | 0 | 618 |  |  | 0 | 0 | -0.27437 | 0
3382 | BBRN_2G | 2 | North | YES | -0.018042 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | -1 | 0.27437 | 0 | 589 |  |  | 0 | 0 | -0.27437 | 0
13131 | CALFREST_1G | 1 | North | YES | -0.018346 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | -1 | 0.27467 | 150.7 | 150.7 |  |  | -2.7647 | 150.7 | -0.27467 | -41.3931
13132 | CALFREST_2G | 2 | North | YES | -0.018346 | 151 | 57 | 151 | 0 | 1.031 | CC | -1 | 0.27467 | 151 | 151 |  |  | -2.7702 | 151 | -0.27467 | -41.4755
13133 | CALFREST_3G | 3 | North | YES | -0.018346 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | -1 | 0.27467 | 177.4 | 177.4 |  |  | -3.2546 | 177.4 | -0.27467 | -48.7268
13134 | CALFREST_4G | 4 | North | YES | -0.018414 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | -1 | 0.27474 | 151.5 | 151.5 |  |  | -2.7897 | 151.5 | -0.27474 | -41.6231
13135 | CALFREST_5G | 5 | North | YES | -0.018414 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | -1 | 0.27474 | 152.3 | 152.3 |  |  | -2.8045 | 152.3 | -0.27474 | -41.8429
13136 | CALFREST_6G | 6 | North | YES | -0.018414 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | -1 | 0.27474 | 177.5 | 177.5 |  |  | -3.2685 | 177.5 | -0.27474 | -48.7664
503 | NTHTEXAS01 | 1 | North | YES | -0.018619 | 0 | 5 | 18 |  | 1.015 | GST | -1 | 0.27495 | 18 | 18 |  |  | -0.33514 | 18 | -0.27495 | -4.949
504 | NTHTEXAS02 | 2 | North | YES | -0.018619 | 14.4 | 5 | 18 |  | 1.015 | GST | -1 | 0.27495 | 18 | 18 |  |  | -0.33514 | 18 | -0.27495 | -4.949
505 | NTHTEXAS03 | 3 | North | YES | -0.018619 | 30.4 | 15 | 38 |  | 1.015 | GST | -1 | 0.27495 | 38 | 38 |  |  | -0.70752 | 38 | -0.27495 | -10.4479
1889 | DECRDOVA_1G | 1 | North | YES | -0.018709 | 779 | 255 | 779 | 0 | 1.02 | GSC | -1 | 0.27504 | 779 | 779 |  |  | -14.5743 | 779 | -0.27504 | -214.2524
3126 | TRINIDAD_6G | 1 | North | YES | -0.019257 | 179.2 | 46 | 224 | 0 | 1 | GST | -1 | 0.27558 | 224 | 224 |  |  | -4.3136 | 224 | -0.27558 | -61.7306
1937 | MDLTHELP_5G | 5 | North | YES | -0.019338 | 224 | 74 | 224 | 0 | 1 | CC | -1 | 0.27566 | 224 | 224 |  |  | -4.3317 | 224 | -0.27566 | -61.7488
1938 | MDLTHELP_6G | 6 | North | YES | -0.019338 | 226 | 74 | 226 | 0 | 1 | CC | -1 | 0.27566 | 226 | 226 |  |  | -4.3704 | 226 | -0.27566 | -62.3001
1943 | MDLTHELP_3G | 3 | North | YES | -0.019338 | 212 | 74 | 212 | 0 | 1 | CC | -1 | 0.27566 | 212 | 212 |  |  | -4.0997 | 212 | -0.27566 | -58.4408
1944 | MDLTHELP_4G | 4 | North | YES | -0.019338 | 211 | 74 | 211 | 0 | 1 | CC | -1 | 0.27566 | 211 | 211 |  |  | -4.0803 | 211 | -0.27566 | -58.1651
12322 | ENNSTRAC_1G | 1 | North | YES | -0.01959 | 196 | 130 | 196 | 0 | 1.036 | CC | -1 | 0.27592 | 196 | 196 |  |  | -3.8396 | 196 | -0.27592 | -54.0796
12323 | ENNSTRAC_2G | 2 | North | YES | -0.01959 | 116 | 100 | 116 | 0 | 1.036 | CC | -1 | 0.27592 | 116 | 116 |  |  | -2.2724 | 116 | -0.27592 | -32.0063
3107 | STRYKER_1G | 1 | North | YES | -0.019928 | 145.6 | 45 | 182 | 0 | 1.029 | GST | -1 | 0.27625 | 182 | 182 |  |  | -3.6269 | 182 | -0.27625 | -50.2783
3108 | STRYKER_2G | 2 | North | YES | -0.019928 | 484 | 75 | 484 | 0 | 1.029 | GST | -1 | 0.27625 | 484 | 484 |  |  | -9.6452 | 484 | -0.27625 | -133.707
3309 | ASPN_G | 1 | North | YES | -0.019961 | 50 | 0 | 50 |  | 1 | Bio | -1 | 0.27629 | 50 | 50 |  |  | -0.99805 | 50 | -0.27629 | -13.8144
3348 | CHAMPION_1G | MB | North | YES | -0.019978 | 0 | 42 | 42 |  | 1 | Cogen | -1 | 0.2763 | 0 | 0 |  |  | 0 | 0 | -0.2763 | 0
1941 | MDLTHELP_1G | 1 | North | YES | -0.020066 | 216.4 | 74 | 216.4 | 0 | 1 | CC | -1 | 0.27639 | 216.4 | 216.4 |  |  | -4.3423 | 216.4 | -0.27639 | -59.8113
1942 | MDLTHELP_2G | 2 | North | YES | -0.020066 | 216.1 | 74 | 216.1 | 0 | 1 | CC | -1 | 0.27639 | 216.1 | 216.1 |  |  | -4.3363 | 216.1 | -0.27639 | -59.7284
13116 | TGATEWAY_1G | 1 | North | YES | -0.020136 | 151 | 30 | 151 | 0 | 1.0232 | CC | -1 | 0.27646 | 151 | 151 |  |  | -3.0405 | 151 | -0.27646 | -41.7458
13117 | TGATEWAY_2G | 2 | North | YES | -0.020136 | 130 | 30 | 130 | 0 | 1.0232 | CC | -1 | 0.27646 | 130 | 130 |  |  | -2.6177 | 130 | -0.27646 | -35.9401
13118 | TGATEWAY_3G | 3 | North | YES | -0.020136 | 148 | 30 | 148 | 0 | 1.0232 | CC | -1 | 0.27646 | 148 | 148 |  |  | -2.9801 | 148 | -0.27646 | -40.9164
13119 | TGATEWAY_4G | 4 | North | YES | -0.020136 | 399 | 65 | 399 | 0 | 1.0232 | CC | -1 | 0.27646 | 399 | 399 |  |  | -8.0343 | 399 | -0.27646 | -110.3084
3097 | MARTLAKE_1G | 1 | North | YES | -0.020319 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 790 |  |  | 0 | 0 | -0.27665 | 0
3098 | MARTLAKE_2G | 2 | North | YES | -0.020319 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 795 |  |  | 0 | 0 | -0.27665 | 0
3099 | MARTLAKE_3G | 3 | North | YES | -0.020319 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 804 |  |  | 0 | 0 | -0.27665 | 0
1600 | BARTNWND_1G | 1 | North | YES | -0.020887 | 12 | 0 | 120 | 0 | 1.022 | Wind | -1 | 0.27721 | 0 | 120 |  |  | 0 | 0 | -0.27721 | 0
2413 | MTCK6_G | 6 | North | YES | -0.021359 | 0 | 30 | 118 |  | 1.022 | GST | -1 | 0.27769 | 118 | 118 |  |  | -2.5204 | 118 | -0.27769 | -32.7669
2414 | MTCK7_G | 7 | North | YES | -0.021359 | 0 | 30 | 115 |  | 1.022 | GST | -1 | 0.27769 | 115 | 115 |  |  | -2.4563 | 115 | -0.27769 | -31.9338
2417 | MTCK8_G | 8 | North | YES | -0.021359 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | -1 | 0.27769 | 556 | 556 |  |  | -11.8756 | 556 | -0.27769 | -154.393
12440 | PARKD_1SVC8 | 1 | North | YES | -0.02162 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.27795 | 0 | 0 |  |  | 0 | 0 | -0.27795 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | -0.02162 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.27795 | 0 | 0 |  |  | 0 | 0 | -0.27795 | 0
12411 | FPLEFR1A_G | 1 | North | YES | -0.021673 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.278 | 161 | 161 |  |  | -3.4894 | 161 | -0.278 | -44.7579
12412 | FPLEFR1B_G | 2 | North | YES | -0.021673 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.278 | 164 | 164 |  |  | -3.5544 | 164 | -0.278 | -45.5919
12413 | FPLEFR1C_G | 3 | North | YES | -0.021673 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.278 | 164 | 164 |  |  | -3.5544 | 164 | -0.278 | -45.5919
12414 | FPLEFR1S_G | 4 | North | YES | -0.021673 | 414 | 191 | 414 | 0 | 1 | CC | -1 | 0.278 | 414 | 414 |  |  | -8.9726 | 414 | -0.278 | -115.0917
12421 | FPLEFR2A_G | 1 | North | YES | -0.021673 | 162 | 72 | 162 | 0 | 1 | CC | -1 | 0.278 | 162 | 162 |  |  | -3.511 | 162 | -0.278 | -45.0359
12422 | FPLEFR2B_G | 2 | North | YES | -0.021673 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.278 | 161 | 161 |  |  | -3.4894 | 161 | -0.278 | -44.7579
12423 | FPLEFR2C_G | 3 | North | YES | -0.021673 | 163 | 72 | 163 | 0 | 1 | CC | -1 | 0.278 | 163 | 163 |  |  | -3.5327 | 163 | -0.278 | -45.3139
12424 | FPLEFR2S_G | 4 | North | YES | -0.021673 | 415 | 191 | 415 | 0 | 1 | CC | -1 | 0.278 | 415 | 415 |  |  | -8.9943 | 415 | -0.278 | -115.3697
2451 | LKHB1_G | 1 | North | YES | -0.021772 | 0 | 80 | 391 |  | 1.022 | GST | -1 | 0.2781 | 391 | 391 |  |  | -8.5129 | 391 | -0.2781 | -108.7364
2452 | LKHB2_G | 2 | North | YES | -0.021772 | 516 | 80 | 516 | 0 | 1.022 | GST | -1 | 0.2781 | 516 | 516 |  |  | -11.2344 | 516 | -0.2781 | -143.4987
948 | STEAM1 | 1 | North | YES | -0.022215 | 0 | 12 | 20 |  | 1.02 | GST | -1 | 0.27854 | 20 | 20 |  |  | -0.4443 | 20 | -0.27854 | -5.5708
949 | STEAM2 | 1 | North | YES | -0.022215 | 26 | 8 | 26 | 0 | 0.99 | GST | -1 | 0.27854 | 26 | 26 |  |  | -0.57759 | 26 | -0.27854 | -7.2421
950 | STEAM3 | 1 | North | YES | -0.022215 | 41 | 13 | 42 | 0 | 1.02 | GST | -1 | 0.27854 | 42 | 42 |  |  | -0.93303 | 42 | -0.27854 | -11.6987
837 | NEWMAN_G5 | 1 | North | YES | -0.022234 | 0 | 15 | 40 |  | 1.01 | GST | -1 | 0.27856 | 40 | 40 |  |  | -0.88936 | 40 | -0.27856 | -11.1424
842 | OLINGER_G1 | 1 | North | YES | -0.02231 | 55.4 | 20 | 79 | 0 | 1.03 | GST | -1 | 0.27864 | 79 | 79 |  |  | -1.7625 | 79 | -0.27864 | -22.0123
843 | OLINGER_G2 | 1 | North | YES | -0.02231 | 76.2 | 25 | 110 | 0 | 1.03 | GST | -1 | 0.27864 | 110 | 110 |  |  | -2.4541 | 110 | -0.27864 | -30.65
844 | OLINGER_G3 | 1 | North | YES | -0.02231 | 103.9 | 45 | 150 | 0 | 1.03 | GST | -1 | 0.27864 | 150 | 150 |  |  | -3.3465 | 150 | -0.27864 | -41.7954
845 | OLINGER_G4 | 1 | North | YES | -0.02231 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | -1 | 0.27864 | 76 | 76 |  |  | -1.6956 | 76 | -0.27864 | -21.1764
1701 | MOSES_1G | 1 | North | YES | -0.022662 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 558 |  |  | 0 | 0 | -0.27899 | 0
1702 | MOSES_2G | 2 | North | YES | -0.022662 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 579 |  |  | 0 | 0 | -0.27899 | 0
1703 | MOSES_3G | 3 | North | YES | -0.022662 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 808 |  |  | 0 | 0 | -0.27899 | 0
5925 | DCEAST | EQ | North | YES | -0.022662 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | -1 | 0.27899 | 0 | 0 |  |  | 0 | 0 | -0.27899 | 0
580 | JCKCNTY801 | 1 | North | YES | -0.02276 | 288 | 0 | 288 | 0 | 1.022 | CC | -1 | 0.27909 | 288 | 288 |  |  | -6.5549 | 288 | -0.27909 | -80.3768
581 | JCKCNTY802 | 2 | North | YES | -0.02276 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.27909 | 147 | 147 |  |  | -3.3457 | 147 | -0.27909 | -41.0257
582 | JCKCNTY803 | 3 | North | YES | -0.02276 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.27909 | 147 | 147 |  |  | -3.3457 | 147 | -0.27909 | -41.0257
1675 | PEC_1G | 1 | North | YES | -0.022769 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0
1676 | PEC_2G | 2 | North | YES | -0.022769 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0
1677 | PEC_3G | 3 | North | YES | -0.022769 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0
1678 | LAMARPWR_1G | 1 | North | YES | -0.022815 | 160 | 67.7 | 160 | 0 | 1.038 | CC | -1 | 0.27914 | 160 | 160 |  |  | -3.6504 | 160 | -0.27914 | -44.6626
1679 | LAMARPWR_2G | 2 | North | YES | -0.022815 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.27914 | 156 | 156 |  |  | -3.5591 | 156 | -0.27914 | -43.546
1680 | LAMARPWR_3G | 3 | North | YES | -0.022815 | 196 | 129.1 | 196 | 0 | 1.038 | CC | -1 | 0.27914 | 196 | 196 |  |  | -4.4717 | 196 | -0.27914 | -54.7117
1681 | LAMARPWR_4G | 4 | North | YES | -0.022815 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.27914 | 156 | 156 |  |  | -3.5591 | 156 | -0.27914 | -43.546
1682 | LAMARPWR_5G | 5 | North | YES | -0.022815 | 157 | 67.7 | 157 | 0 | 1.038 | CC | -1 | 0.27914 | 157 | 157 |  |  | -3.582 | 157 | -0.27914 | -43.8252
1683 | LAMARPWR_6G | 6 | North | YES | -0.022815 | 198 | 129.1 | 198 | 0 | 1.038 | CC | -1 | 0.27914 | 198 | 198 |  |  | -4.5174 | 198 | -0.27914 | -55.27
1948 | HANDLEY_4G | 4 | North | YES | -0.022866 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.27919 | 435 | 435 |  |  | -9.9467 | 435 | -0.27919 | -121.4486
1689 | VALLEY_3G | 3 | North | YES | -0.022897 | 0 | 25 | 375 |  | 1.003 | GST | -1 | 0.27922 | 375 | 375 |  |  | -8.5864 | 375 | -0.27922 | -104.7087
11691 | KMICHICT1_G | 1 | North | YES | -0.022897 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.27922 | 144 | 144 |  |  | -3.2972 | 144 | -0.27922 | -40.2081
11692 | KMICHICT2_G | 2 | North | YES | -0.022897 | 146 | 80 | 146 | 0 | 1.026 | CC | -1 | 0.27922 | 146 | 146 |  |  | -3.343 | 146 | -0.27922 | -40.7666
11693 | KMICHIST3_G | 3 | North | YES | -0.022897 | 312 | 60 | 312 | 0 | 1.026 | CC | -1 | 0.27922 | 312 | 312 |  |  | -7.1439 | 312 | -0.27922 | -87.1176
11694 | KMICHICT4_G | 4 | North | YES | -0.022897 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.27922 | 144 | 144 |  |  | -3.2972 | 144 | -0.27922 | -40.2081
11695 | KMICHICT5_G | 5 | North | YES | -0.022897 | 148 | 80 | 148 | 0 | 1.026 | CC | -1 | 0.27922 | 148 | 148 |  |  | -3.3888 | 148 | -0.27922 | -41.325
11696 | KMICHIST6_G | 6 | North | YES | -0.022897 | 310 | 60 | 310 | 0 | 1.026 | CC | -1 | 0.27922 | 310 | 310 |  |  | -7.0981 | 310 | -0.27922 | -86.5592
1947 | HANDLEY_3G | 3 | North | YES | -0.02294 | 316 | 100 | 395 | 0 | 1.022 | GST | -1 | 0.27927 | 395 | 395 |  |  | -9.0613 | 395 | -0.27927 | -110.3101
1949 | HANDLEY_5G | 5 | North | YES | -0.02294 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.27927 | 435 | 435 |  |  | -9.9789 | 435 | -0.27927 | -121.4808
2381 | NTHLK1_G | 1 | North | YES | -0.023087 | 0 | 35 | 156 |  | 1.022 | GST | -1 | 0.27941 | 156 | 156 |  |  | -3.6016 | 156 | -0.27941 | -43.5885
2382 | NTHLK2_G | 2 | North | YES | -0.023087 | 0 | 35 | 181 |  | 1.022 | GST | -1 | 0.27941 | 181 | 181 |  |  | -4.1787 | 181 | -0.27941 | -50.5738
2383 | NTHLK3_G | 3 | North | YES | -0.023087 | 0 | 50 | 329 |  | 1.022 | GST | -1 | 0.27941 | 329 | 329 |  |  | -7.5956 | 329 | -0.27941 | -91.9269
1687 | VALLEY_1G | 1 | North | YES | -0.023102 | 136 | 15 | 170 | 0 | 1.029 | GST | -1 | 0.27943 | 170 | 170 |  |  | -3.9273 | 170 | -0.27943 | -47.5028
1688 | VALLEY_2G | 2 | North | YES | -0.023102 | 527 | 90 | 527 | 0 | 1.029 | GSC | -1 | 0.27943 | 527 | 527 |  |  | -12.1748 | 527 | -0.27943 | -147.2587
6948 | DENISNDM | 1 | North | YES | -0.023261 | 40 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.27959 | 0 | 0 |  |  | 0 | 0 | -0.27959 | 0
6948 | DENISNDM | 2 | North | YES | -0.023261 | 31 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.27959 | 0 | 0 |  |  | 0 | 0 | -0.27959 | 0
1479 | WFCOGEN_1G | 1 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0
1479 | WFCOGEN_1G | 2 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0
1482 | WFCOGEN_2G | 2 | North | YES | -0.023726 | 13.6 | 12 | 17 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0
1482 | WFCOGEN_2G | 1 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0
2371 | COLLIN_1G | MB | North | YES | -0.02385 | 0 | 40 | 138 |  | 1.022 | GST | -1 | 0.28018 | 0 | 0 |  |  | 0 | 0 | -0.28018 | 0
728 | WOLFRIDGE801 | 1 | North | YES | -0.024491 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | -1 | 0.28082 | 0 | 112.5 |  |  | 0 | 0 | -0.28082 | 0
1433 | GRHAMSES_1G | 1 | North | YES | -0.026119 | 242 | 60 | 242 | 0 | 1.038 | GST | -1 | 0.28245 | 242 | 242 |  |  | -6.3208 | 242 | -0.28245 | -68.3517
1861 | EAGLEMNT_1G | MB | North | YES | -0.026521 | 0 | 30 | 112 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0
1862 | EAGLEMNT_2G | MB | North | YES | -0.026521 | 0 | 40 | 100 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0
1863 | EAGLEMNT_3G | MB | North | YES | -0.026521 | 0 | 50 | 378 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0
923 | SPENCER_G4 | 1 | North | YES | -0.028142 | 48 | 20 | 61 | 0 | 1.03 | GST | -1 | 0.28447 | 61 | 61 |  |  | -1.7167 | 61 | -0.28447 | -17.3526
924 | SPENCER_G5 | 1 | North | YES | -0.028142 | 52 | 20 | 66 | 0 | 1.03 | GST | -1 | 0.28447 | 66 | 66 |  |  | -1.8574 | 66 | -0.28447 | -18.7749
1453 | WCPWRCO_1G | 1 | North | YES | -0.041156 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.29748 | 204 | 204 |  |  | -8.3958 | 204 | -0.29748 | -60.6864
1454 | WCPWRCO_2G | 2 | North | YES | -0.041156 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.29748 | 204 | 204 |  |  | -8.3958 | 204 | -0.29748 | -60.6864
1455 | WCPWRCO_3G | 3 | North | YES | -0.041156 | 242 | 50 | 242 |  | 1.02 | CC | -1 | 0.29748 | 242 | 242 |  |  | -9.9598 | 242 | -0.29748 | -71.9907
1432 | GRHAMSES_2G | 2 | North | YES | -0.07511 | 294.9 | 90 | 366 | 0 | 1.014 | GST | -1 | 0.33144 | 366 | 366 |  |  | -27.4903 | 366 | -0.33144 | -121.3056
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Share of Zonal Cap | Cumulative Share of Zonal Impact | Cont_ Cokfield to GrahamSES and LongCreek to GrahamSES1_5 OL_ TonkawawI_5 to GrahamSES |  | i_PTDF_INC_pt | 543 |  | BOSQUESW501 | Unit at max
1432 | GRHAMSES_2G | 2 | North | YES | -0.07511 | 294.9 | 90 | 366 | 0 | 1.014 | GST | -1 | 0.33144 | 366 | 366 |  |  | -27.4903 | 366 | -0.33144 | -121.3056 | 0.0085623 | 0.010533 |  |  | i_10pctunit | 29 |  | 143 | # units @ max
1453 | WCPWRCO_1G | 1 | North | YES | -0.041156 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.29748 | 204 | 204 |  |  | -8.3958 | 204 | -0.29748 | -60.6864 | 0.013335 | 0.015802 | [5 empty] | 0.015067 | delta max
1454 | WCPWRCO_2G | 2 | North | YES | -0.041156 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.29748 | 204 | 204 |  |  | -8.3958 | 204 | -0.29748 | -60.6864 | 0.018107 | 0.021071 | [5 empty] | Delta
1455 | WCPWRCO_3G | 3 | North | YES | -0.041156 | 242 | 50 | 242 |  | 1.02 | CC | -1 | 0.29748 | 242 | 242 |  |  | -9.9598 | 242 | -0.29748 | -71.9907 | 0.023768 | 0.027322 | Weighted Shift Factors |  |  |  | 1 | 0.0019705
923 | SPENCER_G4 | 1 | North | YES | -0.028142 | 48 | 20 | 61 | 0 | 1.03 | GST | -1 | 0.28447 | 61 | 61 |  |  | -1.7167 | 61 | -0.28447 | -17.3526 | 0.025196 | 0.028829 | West | 0.25633 |  |  | 2 | 0.0024674
924 | SPENCER_G5 | 1 | North | YES | -0.028142 | 52 | 20 | 66 | 0 | 1.03 | GST | -1 | 0.28447 | 66 | 66 |  |  | -1.8574 | 66 | -0.28447 | -18.7749 | 0.02674 | 0.030459 | North | -0.021071 |  |  | 3 | 0.0029643
1861 | EAGLEMNT_1G | MB | North | YES | -0.026521 | 0 | 30 | 112 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0 | 0.02674 | 0.030459 |  |  |  |  | 4 | 0.0035538
1862 | EAGLEMNT_2G | MB | North | YES | -0.026521 | 0 | 40 | 100 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0 | 0.02674 | 0.030459 |  |  |  |  | 5 | 0.0036334
1863 | EAGLEMNT_3G | MB | North | YES | -0.026521 | 0 | 50 | 378 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0 | 0.02674 | 0.030459 |  |  |  |  | 6 | 0.0037196
1433 | GRHAMSES_1G | 1 | North | YES | -0.026119 | 242 | 60 | 242 | 0 | 1.038 | GST | -1 | 0.28245 | 242 | 242 |  |  | -6.3208 | 242 | -0.28245 | -68.3517 | 0.032401 | 0.036394 |  |  |  |  | 7 | 0.0037196
728 | WOLFRIDGE801 | 1 | North | YES | -0.024491 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | -1 | 0.28082 | 0 | 112.5 |  |  | 0 | 0 | -0.28082 | 0 | 0.032401 | 0.036394 |  |  |  |  | 8 | 0.0037196
2371 | COLLIN_1G | MB | North | YES | -0.02385 | 0 | 40 | 138 |  | 1.022 | GST | -1 | 0.28018 | 0 | 0 |  |  | 0 | 0 | -0.28018 | 0 | 0.032401 | 0.036394 |  |  |  |  | 9 | 0.0037196
1479 | WFCOGEN_1G | 1 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0 | 0.032401 | 0.036394 |  |  |  |  | 10 | 0.0039931
1479 | WFCOGEN_1G | 2 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0 | 0.032401 | 0.036394 |  |  |  |  | 11 | 0.0039931
1482 | WFCOGEN_2G | 2 | North | YES | -0.023726 | 13.6 | 12 | 17 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0 | 0.032401 | 0.036394 |  |  |  |  | 12 | 0.0039931
1482 | WFCOGEN_2G | 1 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0 | 0.032401 | 0.036394 |  |  |  |  | 13 | 0.0039931
6948 | DENISNDM | 1 | North | YES | -0.023261 | 40 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.27959 | 0 | 0 |  |  | 0 | 0 | -0.27959 | 0 | 0.032401 | 0.036394 |  |  |  |  | 14 | 0.0039931
6948 | DENISNDM | 2 | North | YES | -0.023261 | 31 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.27959 | 0 | 0 |  |  | 0 | 0 | -0.27959 | 0 | 0.032401 | 0.036394 |  |  |  |  | 15 | 0.0039931
1687 | VALLEY_1G | 1 | North | YES | -0.023102 | 136 | 15 | 170 | 0 | 1.029 | GST | -1 | 0.27943 | 170 | 170 |  |  | -3.9273 | 170 | -0.27943 | -47.5028 | 0.036378 | 0.040519 |  |  |  |  | 16 | 0.0039931
1688 | VALLEY_2G | 2 | North | YES | -0.023102 | 527 | 90 | 527 | 0 | 1.029 | GSC | -1 | 0.27943 | 527 | 527 |  |  | -12.1748 | 527 | -0.27943 | -147.2587 | 0.048707 | 0.053305 |  |  |  |  | 17 | 0.0039931
2381 | NTHLK1_G | 1 | North | YES | -0.023087 | 0 | 35 | 156 |  | 1.022 | GST | -1 | 0.27941 | 156 | 156 |  |  | -3.6016 | 156 | -0.27941 | -43.5885 | 0.052356 | 0.05709 |  |  |  |  | 18 | 0.0039931
2382 | NTHLK2_G | 2 | North | YES | -0.023087 | 0 | 35 | 181 |  | 1.022 | GST | -1 | 0.27941 | 181 | 181 |  |  | -4.1787 | 181 | -0.27941 | -50.5738 | 0.05659 | 0.061481 |  |  |  |  | 19 | 0.0041407
2383 | NTHLK3_G | 3 | North | YES | -0.023087 | 0 | 50 | 329 |  | 1.022 | GST | -1 | 0.27941 | 329 | 329 |  |  | -7.5956 | 329 | -0.27941 | -91.9269 | 0.064287 | 0.069463 |  |  |  |  | 20 | 0.0045982
1947 | HANDLEY_3G | 3 | North | YES | -0.02294 | 316 | 100 | 395 | 0 | 1.022 | GST | -1 | 0.27927 | 395 | 395 |  |  | -9.0613 | 395 | -0.27927 | -110.3101 | 0.073528 | 0.079041 |  |  |  |  | 21 | 0.0047335
1949 | HANDLEY_5G | 5 | North | YES | -0.02294 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.27927 | 435 | 435 |  |  | -9.9789 | 435 | -0.27927 | -121.4808 | 0.083704 | 0.089589 |  |  |  |  | 22 | 0.0048904
1689 | VALLEY_3G | 3 | North | YES | -0.022897 | 0 | 25 | 375 |  | 1.003 | GST | -1 | 0.27922 | 375 | 375 |  |  | -8.5864 | 375 | -0.27922 | -104.7087 | 0.092477 | 0.098681 |  |  |  |  | 23 | 0.0051756
11691 | KMICHICT1_G | 1 | North | YES | -0.022897 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.27922 | 144 | 144 |  |  | -3.2972 | 144 | -0.27922 | -40.2081 | 0.095846 | 0.10217 |  |  |  |  | 24 | 0.0055129
11692 | KMICHICT2_G | 2 | North | YES | -0.022897 | 146 | 80 | 146 | 0 | 1.026 | CC | -1 | 0.27922 | 146 | 146 |  |  | -3.343 | 146 | -0.27922 | -40.7666 | 0.099261 | 0.10571 |  |  |  |  | 25 | 0.0058845
11693 | KMICHIST3_G | 3 | North | YES | -0.022897 | 312 | 60 | 312 | 0 | 1.026 | CC | -1 | 0.27922 | 312 | 312 |  |  | -7.1439 | 312 | -0.27922 | -87.1176 | 0.10656 | 0.11328 |  |  |  |  | 26 | 0.0062034
11694 | KMICHICT4_G | 4 | North | YES | -0.022897 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.27922 | 144 | 144 |  |  | -3.2972 | 144 | -0.27922 | -40.2081 | 0.10993 | 0.11677 |  |  |  |  | 27 | 0.0063258
11695 | KMICHICT5_G | 5 | North | YES | -0.022897 | 148 | 80 | 148 | 0 | 1.026 | CC | -1 | 0.27922 | 148 | 148 |  |  | -3.3888 | 148 | -0.27922 | -41.325 | 0.11339 | 0.12036 |  |  |  |  | 28 | 0.00645
11696 | KMICHIST6_G | 6 | North | YES | -0.022897 | 310 | 60 | 310 | 0 | 1.026 | CC | -1 | 0.27922 | 310 | 310 |  |  | -7.0981 | 310 | -0.27922 | -86.5592 | 0.12064 | 0.12787 |  |  |  |  | 29 | 0.0067153
1948 | HANDLEY_4G | 4 | North | YES | -0.022866 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.27919 | 435 | 435 |  |  | -9.9467 | 435 | -0.27919 | -121.4486 | 0.13082 | 0.13842 |  |  |  |  | 30 | 0.0068377
1678 | LAMARPWR_1G | 1 | North | YES | -0.022815 | 160 | 67.7 | 160 | 0 | 1.038 | CC | -1 | 0.27914 | 160 | 160 |  |  | -3.6504 | 160 | -0.27914 | -44.6626 | 0.13456 | 0.14229 |  |  |  |  | 31 | 0.0069636
1679 | LAMARPWR_2G | 2 | North | YES | -0.022815 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.27914 | 156 | 156 |  |  | -3.5591 | 156 | -0.27914 | -43.546 | 0.13821 | 0.14608 |  |  |  |  | 32 | 0.0072272
1680 | LAMARPWR_3G | 3 | North | YES | -0.022815 | 196 | 129.1 | 196 | 0 | 1.038 | CC | -1 | 0.27914 | 196 | 196 |  |  | -4.4717 | 196 | -0.27914 | -54.7117 | 0.1428 | 0.15083 |  |  |  |  | 33 | 0.007596
1681 | LAMARPWR_4G | 4 | North | YES | -0.022815 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.27914 | 156 | 156 |  |  | -3.5591 | 156 | -0.27914 | -43.546 | 0.14645 | 0.15461 |  |  |  |  | 34 | 0.0077309
1682 | LAMARPWR_5G | 5 | North | YES | -0.022815 | 157 | 67.7 | 157 | 0 | 1.038 | CC | -1 | 0.27914 | 157 | 157 |  |  | -3.582 | 157 | -0.27914 | -43.8252 | 0.15012 | 0.15841 |  |  |  |  | 35 | 0.0078624
1683 | LAMARPWR_6G | 6 | North | YES | -0.022815 | 198 | 129.1 | 198 | 0 | 1.038 | CC | -1 | 0.27914 | 198 | 198 |  |  | -4.5174 | 198 | -0.27914 | -55.27 | 0.15475 | 0.16321 |  |  |  |  | 36 | 0.0080277
1675 | PEC_1G | 1 | North | YES | -0.022769 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0 | 0.15475 | 0.16321 |  |  |  |  | 37 | 0.0081593
1676 | PEC_2G | 2 | North | YES | -0.022769 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0 | 0.15475 | 0.16321 |  |  |  |  | 38 | 0.0082916
1677 | PEC_3G | 3 | North | YES | -0.022769 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0 | 0.15475 | 0.16321 |  |  |  |  | 39 | 0.0084586
580 | JCKCNTY801 | 1 | North | YES | -0.02276 | 288 | 0 | 288 | 0 | 1.022 | CC | -1 | 0.27909 | 288 | 288 |  |  | -6.5549 | 288 | -0.27909 | -80.3768 | 0.16149 | 0.17019 |  |  |  |  | 40 | 0.0084586
581 | JCKCNTY802 | 2 | North | YES | -0.02276 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.27909 | 147 | 147 |  |  | -3.3457 | 147 | -0.27909 | -41.0257 | 0.16493 | 0.17375 |  |  |  |  | 41 | 0.0084586
582 | JCKCNTY803 | 3 | North | YES | -0.02276 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.27909 | 147 | 147 |  |  | -3.3457 | 147 | -0.27909 | -41.0257 | 0.16837 | 0.17731 |  |  |  |  | 42 | 0.0084586
1701 | MOSES_1G | 1 | North | YES | -0.022662 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 558 |  |  | 0 | 0 | -0.27899 | 0 | 0.16837 | 0.17731 |  |  |  |  | 43 | 0.0087001
1702 | MOSES_2G | 2 | North | YES | -0.022662 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 579 |  |  | 0 | 0 | -0.27899 | 0 | 0.16837 | 0.17731 |  |  |  |  | 44 | 0.0088234
1703 | MOSES_3G | 3 | North | YES | -0.022662 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 808 |  |  | 0 | 0 | -0.27899 | 0 | 0.16837 | 0.17731 |  |  |  |  | 45 | 0.0089466
5925 | DCEAST | EQ | North | YES | -0.022662 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | -1 | 0.27899 | 0 | 0 |  |  | 0 | 0 | -0.27899 | 0 | 0.16837 | 0.17731 |  |  |  |  | 46 | 0.0089466
842 | OLINGER_G1 | 1 | North | YES | -0.02231 | 55.4 | 20 | 79 | 0 | 1.03 | GST | -1 | 0.27864 | 79 | 79 |  |  | -1.7625 | 79 | -0.27864 | -22.0123 | 0.17022 | 0.17923 |  |  |  |  | 47 | 0.0089466
843 | OLINGER_G2 | 1 | North | YES | -0.02231 | 76.2 | 25 | 110 | 0 | 1.03 | GST | -1 | 0.27864 | 110 | 110 |  |  | -2.4541 | 110 | -0.27864 | -30.65 | 0.17279 | 0.18189 |  |  |  |  | 48 | 0.0089466
844 | OLINGER_G3 | 1 | North | YES | -0.02231 | 103.9 | 45 | 150 | 0 | 1.03 | GST | -1 | 0.27864 | 150 | 150 |  |  | -3.3465 | 150 | -0.27864 | -41.7954 | 0.1763 | 0.18552 |  |  |  |  | 49 | 0.0089466
845 | OLINGER_G4 | 1 | North | YES | -0.02231 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | -1 | 0.27864 | 76 | 76 |  |  | -1.6956 | 76 | -0.27864 | -21.1764 | 0.17808 | 0.18735 |  |  |  |  | 50 | 0.0090098
837 | NEWMAN_G5 | 1 | North | YES | -0.022234 | 0 | 15 | 40 |  | 1.01 | GST | -1 | 0.27856 | 40 | 40 |  |  | -0.88936 | 40 | -0.27856 | -11.1424 | 0.17901 | 0.18832 |  |  |  |  | 51 | 0.0090977
948 | STEAM1 | 1 | North | YES | -0.022215 | 0 | 12 | 20 |  | 1.02 | GST | -1 | 0.27854 | 20 | 20 |  |  | -0.4443 | 20 | -0.27854 | -5.5708 | 0.17948 | 0.18881 |  |  |  |  | 52 | 0.0092176
949 | STEAM2 | 1 | North | YES | -0.022215 | 26 | 8 | 26 | 0 | 0.99 | GST | -1 | 0.27854 | 26 | 26 |  |  | -0.57759 | 26 | -0.27854 | -7.2421 | 0.18009 | 0.18943 |  |  |  |  | 53 | 0.0092784
950 | STEAM3 | 1 | North | YES | -0.022215 | 41 | 13 | 42 | 0 | 1.02 | GST | -1 | 0.27854 | 42 | 42 |  |  | -0.93303 | 42 | -0.27854 | -11.6987 | 0.18107 | 0.19045 |  |  |  |  | 54 | 0.0093101
2451 | LKHB1_G | 1 | North | YES | -0.021772 | 0 | 80 | 391 |  | 1.022 | GST | -1 | 0.2781 | 391 | 391 |  |  | -8.5129 | 391 | -0.2781 | -108.7364 | 0.19022 | 0.19989 |  |  |  |  | 55 | 0.0093259
2452 | LKHB2_G | 2 | North | YES | -0.021772 | 516 | 80 | 516 | 0 | 1.022 | GST | -1 | 0.2781 | 516 | 516 |  |  | -11.2344 | 516 | -0.2781 | -143.4987 | 0.20229 | 0.21235 |  |  |  |  | 56 | 0.0093465
12411 | FPLEFR1A_G | 1 | North | YES | -0.021673 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.278 | 161 | 161 |  |  | -3.4894 | 161 | -0.278 | -44.7579 | 0.20606 | 0.21624 |  |  |  |  | 57 | 0.0093797
12412 | FPLEFR1B_G | 2 | North | YES | -0.021673 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.278 | 164 | 164 |  |  | -3.5544 | 164 | -0.278 | -45.5919 | 0.20989 | 0.2202 |  |  |  |  | 58 | 0.009674
12413 | FPLEFR1C_G | 3 | North | YES | -0.021673 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.278 | 164 | 164 |  |  | -3.5544 | 164 | -0.278 | -45.5919 | 0.21373 | 0.22416 |  |  |  |  | 59 | 0.010062
12414 | FPLEFR1S_G | 4 | North | YES | -0.021673 | 414 | 191 | 414 | 0 | 1 | CC | -1 | 0.278 | 414 | 414 |  |  | -8.9726 | 414 | -0.278 | -115.0917 | 0.22341 | 0.23415 |  |  |  |  | 60 | 0.010182
12421 | FPLEFR2A_G | 1 | North | YES | -0.021673 | 162 | 72 | 162 | 0 | 1 | CC | -1 | 0.278 | 162 | 162 |  |  | -3.511 | 162 | -0.278 | -45.0359 | 0.2272 | 0.23806 |  |  |  |  | 61 | 0.010304
12422 | FPLEFR2B_G | 2 | North | YES | -0.021673 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.278 | 161 | 161 |  |  | -3.4894 | 161 | -0.278 | -44.7579 | 0.23097 | 0.24195 |  |  |  |  | 62 | 0.010426
12423 | FPLEFR2C_G | 3 | North | YES | -0.021673 | 163 | 72 | 163 | 0 | 1 | CC | -1 | 0.278 | 163 | 163 |  |  | -3.5327 | 163 | -0.278 | -45.3139 | 0.23478 | 0.24588 |  |  |  |  | 63 | 0.010734
12424 | FPLEFR2S_G | 4 | North | YES | -0.021673 | 415 | 191 | 415 | 0 | 1 | CC | -1 | 0.278 | 415 | 415 |  |  | -8.9943 | 415 | -0.278 | -115.3697 | 0.24449 | 0.2559 |  |  |  |  | 64 | 0.010855
12440 | PARKD_1SVC8 | 1 | North | YES | -0.02162 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.27795 | 0 | 0 |  |  | 0 | 0 | -0.27795 | 0 | 0.24449 | 0.2559 |  |  |  |  | 65 | 0.010975
12449 | PARKD_2SVC8 | 1 | North | YES | -0.02162 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.27795 | 0 | 0 |  |  | 0 | 0 | -0.27795 | 0 | 0.24449 | 0.2559 |  |  |  |  | 66 | 0.011096
2413 | MTCK6_G | 6 | North | YES | -0.021359 | 0 | 30 | 118 |  | 1.022 | GST | -1 | 0.27769 | 118 | 118 |  |  | -2.5204 | 118 | -0.27769 | -32.7669 | 0.24725 | 0.25874 |  |  |  |  | 67 | 0.011405
2414 | MTCK7_G | 7 | North | YES | -0.021359 | 0 | 30 | 115 |  | 1.022 | GST | -1 | 0.27769 | 115 | 115 |  |  | -2.4563 | 115 | -0.27769 | -31.9338 | 0.24994 | 0.26152 |  |  |  |  | 68 | 0.011405
2417 | MTCK8_G | 8 | North | YES | -0.021359 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | -1 | 0.27769 | 556 | 556 |  |  | -11.8756 | 556 | -0.27769 | -154.393 | 0.26295 | 0.27492 |  |  |  |  | 69 | 0.011405
1600 | BARTNWND_1G | 1 | North | YES | -0.020887 | 12 | 0 | 120 | 0 | 1.022 | Wind | -1 | 0.27721 | 0 | 120 |  |  | 0 | 0 | -0.27721 | 0 | 0.26295 | 0.27492 |  |  |  |  | 70 | 0.011489
3097 | MARTLAKE_1G | 1 | North | YES | -0.020319 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 790 |  |  | 0 | 0 | -0.27665 | 0 | 0.26295 | 0.27492 |  |  |  |  | 71 | 0.011572
3098 | MARTLAKE_2G | 2 | North | YES | -0.020319 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 795 |  |  | 0 | 0 | -0.27665 | 0 | 0.26295 | 0.27492 |  |  |  |  | 72 | 0.01197
3099 | MARTLAKE_3G | 3 | North | YES | -0.020319 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 804 |  |  | 0 | 0 | -0.27665 | 0 | 0.26295 | 0.27492 |  |  |  |  | 73 | 0.01197
13116 | TGATEWAY_1G | 1 | North | YES | -0.020136 | 151 | 30 | 151 | 0 | 1.0232 | CC | -1 | 0.27646 | 151 | 151 |  |  | -3.0405 | 151 | -0.27646 | -41.7458 | 0.26648 | 0.27855 |  |  |  |  | 74 | 0.01197
13117 | TGATEWAY_2G | 2 | North | YES | -0.020136 | 130 | 30 | 130 | 0 | 1.0232 | CC | -1 | 0.27646 | 130 | 130 |  |  | -2.6177 | 130 | -0.27646 | -35.9401 | 0.26952 | 0.28167 |  |  |  |  | 75 | 0.01197
13118 | TGATEWAY_3G | 3 | North | YES | -0.020136 | 148 | 30 | 148 | 0 | 1.0232 | CC | -1 | 0.27646 | 148 | 148 |  |  | -2.9801 | 148 | -0.27646 | -40.9164 | 0.27299 | 0.28522 |  |  |  |  | 76 | 0.01197
13119 | TGATEWAY_4G | 4 | North | YES | -0.020136 | 399 | 65 | 399 | 0 | 1.0232 | CC | -1 | 0.27646 | 399 | 399 |  |  | -8.0343 | 399 | -0.27646 | -110.3084 | 0.28232 | 0.2948 |  |  |  |  | 77 | 0.012063
1941 | MDLTHELP_1G | 1 | North | YES | -0.020066 | 216.4 | 74 | 216.4 | 0 | 1 | CC | -1 | 0.27639 | 216.4 | 216.4 |  |  | -4.3423 | 216.4 | -0.27639 | -59.8113 | 0.28738 | 0.29999 |  |  |  |  | 78 | 0.012142
1942 | MDLTHELP_2G | 2 | North | YES | -0.020066 | 216.1 | 74 | 216.1 | 0 | 1 | CC | -1 | 0.27639 | 216.1 | 216.1 |  |  | -4.3363 | 216.1 | -0.27639 | -59.7284 | 0.29244 | 0.30518 |  |  |  |  | 79 | 0.012232
3348 | CHAMPION_1G | MB | North | YES | -0.019978 | 0 | 42 | 42 |  | 1 | Cogen | -1 | 0.2763 | 0 | 0 |  |  | 0 | 0 | -0.2763 | 0 | 0.29244 | 0.30518 |  |  |  |  | 80 | 0.012476
3309 | ASPN_G | 1 | North | YES | -0.019961 | 50 | 0 | 50 |  | 1 | Bio | -1 | 0.27629 | 50 | 50 |  |  | -0.99805 | 50 | -0.27629 | -13.8144 | 0.29361 | 0.30638 |  |  |  |  | 81 | 0.012607
3107 | STRYKER_1G | 1 | North | YES | -0.019928 | 145.6 | 45 | 182 | 0 | 1.029 | GST | -1 | 0.27625 | 182 | 182 |  |  | -3.6269 | 182 | -0.27625 | -50.2783 | 0.29787 | 0.31074 |  |  |  |  | 82 | 0.012737
3108 | STRYKER_2G | 2 | North | YES | -0.019928 | 484 | 75 | 484 | 0 | 1.029 | GST | -1 | 0.27625 | 484 | 484 |  |  | -9.6452 | 484 | -0.27625 | -133.707 | 0.30919 | 0.32235 |  |  |  |  | 83 | 0.012737
12322 | ENNSTRAC_1G | 1 | North | YES | -0.01959 | 196 | 130 | 196 | 0 | 1.036 | CC | -1 | 0.27592 | 196 | 196 |  |  | -3.8396 | 196 | -0.27592 | -54.0796 | 0.31377 | 0.32705 |  |  |  |  | 84 | 0.012767
12323 | ENNSTRAC_2G | 2 | North | YES | -0.01959 | 116 | 100 | 116 | 0 | 1.036 | CC | -1 | 0.27592 | 116 | 116 |  |  | -2.2724 | 116 | -0.27592 | -32.0063 | 0.31649 | 0.32983 |  |  |  |  | 85 | 0.012875
1937 | MDLTHELP_5G | 5 | North | YES | -0.019338 | 224 | 74 | 224 | 0 | 1 | CC | -1 | 0.27566 | 224 | 224 |  |  | -4.3317 | 224 | -0.27566 | -61.7488 | 0.32173 | 0.33519 |  |  |  |  | 86 | 0.013162
1938 | MDLTHELP_6G | 6 | North | YES | -0.019338 | 226 | 74 | 226 | 0 | 1 | CC | -1 | 0.27566 | 226 | 226 |  |  | -4.3704 | 226 | -0.27566 | -62.3001 | 0.32702 | 0.3406 |  |  |  |  | 87 | 0.013272
1943 | MDLTHELP_3G | 3 | North | YES | -0.019338 | 212 | 74 | 212 | 0 | 1 | CC | -1 | 0.27566 | 212 | 212 |  |  | -4.0997 | 212 | -0.27566 | -58.4408 | 0.33197 | 0.34567 |  |  |  |  | 88 | 0.013338
1944 | MDLTHELP_4G | 4 | North | YES | -0.019338 | 211 | 74 | 211 | 0 | 1 | CC | -1 | 0.27566 | 211 | 211 |  |  | -4.0803 | 211 | -0.27566 | -58.1651 | 0.33691 | 0.35072 |  |  |  |  | 89 | 0.013459
3126 | TRINIDAD_6G | 1 | North | YES | -0.019257 | 179.2 | 46 | 224 | 0 | 1 | GST | -1 | 0.27558 | 224 | 224 |  |  | -4.3136 | 224 | -0.27558 | -61.7306 | 0.34215 | 0.35608 |  |  |  |  | 90 | 0.013581
1889 | DECRDOVA_1G | 1 | North | YES | -0.018709 | 779 | 255 | 779 | 0 | 1.02 | GSC | -1 | 0.27504 | 779 | 779 |  |  | -14.5743 | 779 | -0.27504 | -214.2524 | 0.36038 | 0.37468 |  |  |  |  | 91 | 0.013696
503 | NTHTEXAS01 | 1 | North | YES | -0.018619 | 0 | 5 | 18 |  | 1.015 | GST | -1 | 0.27495 | 18 | 18 |  |  | -0.33514 | 18 | -0.27495 | -4.949 | 0.3608 | 0.37511 |  |  |  |  | 92 | 0.01381
504 | NTHTEXAS02 | 2 | North | YES | -0.018619 | 14.4 | 5 | 18 |  | 1.015 | GST | -1 | 0.27495 | 18 | 18 |  |  | -0.33514 | 18 | -0.27495 | -4.949 | 0.36122 | 0.37554 |  |  |  |  | 93 | 0.01393
505 | NTHTEXAS03 | 3 | North | YES | -0.018619 | 30.4 | 15 | 38 |  | 1.015 | GST | -1 | 0.27495 | 38 | 38 |  |  | -0.70752 | 38 | -0.27495 | -10.4479 | 0.36211 | 0.37645 |  |  |  |  | 94 | 0.014309
13134 | CALFREST_4G | 4 | North | YES | -0.018414 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | -1 | 0.27474 | 151.5 | 151.5 |  |  | -2.7897 | 151.5 | -0.27474 | -41.6231 | 0.36565 | 0.38007 |  |  |  |  | 95 | 0.014318
13135 | CALFREST_5G | 5 | North | YES | -0.018414 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | -1 | 0.27474 | 152.3 | 152.3 |  |  | -2.8045 | 152.3 | -0.27474 | -41.8429 | 0.36921 | 0.3837 |  |  |  |  | 96 | 0.014326
13136 | CALFREST_6G | 6 | North | YES | -0.018414 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | -1 | 0.27474 | 177.5 | 177.5 |  |  | -3.2685 | 177.5 | -0.27474 | -48.7664 | 0.37337 | 0.38793 |  |  |  |  | 97 | 0.014344
13131 | CALFREST_1G | 1 | North | YES | -0.018346 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | -1 | 0.27467 | 150.7 | 150.7 |  |  | -2.7647 | 150.7 | -0.27467 | -41.3931 | 0.37689 | 0.39153 |  |  |  |  | 98 | 0.014414
13132 | CALFREST_2G | 2 | North | YES | -0.018346 | 151 | 57 | 151 | 0 | 1.031 | CC | -1 | 0.27467 | 151 | 151 |  |  | -2.7702 | 151 | -0.27467 | -41.4755 | 0.38042 | 0.39513 |  |  |  |  | 99 | 0.014485
13133 | CALFREST_3G | 3 | North | YES | -0.018346 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | -1 | 0.27467 | 177.4 | 177.4 |  |  | -3.2546 | 177.4 | -0.27467 | -48.7268 | 0.38457 | 0.39936 |  |  |  |  | 100 | 0.014566
3381 | BBRN_1G | 1 | North | YES | -0.018042 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | -1 | 0.27437 | 0 | 618 |  |  | 0 | 0 | -0.27437 | 0 | 0.38457 | 0.39936 |  |  |  |  | 101 | 0.014635
3382 | BBRN_2G | 2 | North | YES | -0.018042 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | -1 | 0.27437 | 0 | 589 |  |  | 0 | 0 | -0.27437 | 0 | 0.38457 | 0.39936 |  |  |  |  | 102 | 0.014704
48721 | LEG_1___1 | 1 | North | YES | -0.016148 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | -1 | 0.27247 | 0 | 827 |  |  | 0 | 0 | -0.27247 | 0 | 0.38457 | 0.39936 |  |  |  |  | 103 | 0.014784
48722 | LEG_2___2 | 2 | North | YES | -0.016148 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | -1 | 0.27247 | 0 | 819 |  |  | 0 | 0 | -0.27247 | 0 | 0.38457 | 0.39936 |  |  |  |  | 104 | 0.014784
1892 | DECRDOVA_2G | A | North | YES | -0.015865 | 65 | 65 | 70 | 0 | 1.025 | GGT | -1 | 0.27219 | 70 | 70 |  |  | -1.1105 | 70 | -0.27219 | -19.0534 | 0.38621 | 0.40101 |  |  |  |  | 105 | 0.014784
1893 | DECRDOVA_3G | B | North | YES | -0.015865 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.27219 | 69 | 69 |  |  | -1.0947 | 69 | -0.27219 | -18.7812 | 0.38783 | 0.40264 |  |  |  |  | 106 | 0.014784
1894 | DECRDOVA_4G | C | North | YES | -0.015865 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.27219 | 69 | 69 |  |  | -1.0947 | 69 | -0.27219 | -18.7812 | 0.38944 | 0.40427 |  |  |  |  | 107 | 0.014784
1895 | DECRDOVA_5G | D | North | YES | -0.015865 | 65 | 65 | 68 | 0 | 1.025 | GGT | -1 | 0.27219 | 68 | 68 |  |  | -1.0788 | 68 | -0.27219 | -18.509 | 0.39103 | 0.40588 |  |  |  |  | 108 | 0.014801
366 | JNSNCNTY802 | 1 | North | YES | -0.015703 | 168 | 20 | 168 | 0 | 1.02 | Cogen | -1 | 0.27203 | 0 | 0 |  |  | 0 | 0 | -0.27203 | 0 | 0.39103 | 0.40588 |  |  |  |  | 109 | 0.014818
367 | JNSNCNTY802 | 2 | North | YES | -0.015703 | 90 | 20 | 90 | 0 | 1.02 | Cogen | -1 | 0.27203 | 0 | 0 |  |  | 0 | 0 | -0.27203 | 0 | 0.39103 | 0.40588 |  |  |  |  | 110 | 0.014834
39960 | TNTNPONE_18 | 1 | North | YES | -0.015463 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | -1 | 0.27179 | 0 | 152.3 |  |  | 0 | 0 | -0.27179 | 0 | 0.39103 | 0.40588 |  |  |  |  | 111 | 0.014851
39970 | TNTNPONE_28 | 1 | North | YES | -0.015463 | 153 | 30 | 153 |  | 1.04 | LIGCO | -1 | 0.27179 | 0 | 153 |  |  | 0 | 0 | -0.27179 | 0 | 0.39103 | 0.40588 |  |  |  |  | 112 | 0.014851
344 | MRSSHPRD | 1 | North | YES | -0.014638 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.27096 | 0 | 0 |  |  | 0 | 0 | -0.27096 | 0 | 0.39103 | 0.40588 |  |  |  |  | 113 | 0.014851
345 | MRSSHPRD01 | 2 | North | YES | -0.014638 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.27096 | 0 | 0 |  |  | 0 | 0 | -0.27096 | 0 | 0.39103 | 0.40588 |  |  |  |  | 114 | 0.014851
1877 | WLFHOLW_1G | 1 | North | YES | -0.014527 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | -1 | 0.27085 | 217.3 | 217.3 |  |  | -3.1567 | 217.3 | -0.27085 | -58.8564 | 0.39611 | 0.41099 |  |  |  |  | 115 | 0.014851
1878 | WLFHOLW_2G | 2 | North | YES | -0.014527 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | -1 | 0.27085 | 215.7 | 215.7 |  |  | -3.1335 | 215.7 | -0.27085 | -58.423 | 0.40116 | 0.41607 |  |  |  |  | 116 | 0.014851
1879 | WLFHOLW_3G | 3 | North | YES | -0.014527 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | -1 | 0.27085 | 272.4 | 272.4 |  |  | -3.9572 | 272.4 | -0.27085 | -73.7804 | 0.40753 | 0.42247 |  |  |  |  | 117 | 0.014851
3403 | THOUSE_1G | 1 | North | YES | -0.013971 | 563 | 200 | 563 | 0 | 1.012 | GSC | -1 | 0.2703 | 563 | 563 |  |  | -7.8657 | 563 | -0.2703 | -152.1773 | 0.4207 | 0.43568 |  |  |  |  | 118 | 0.014878
3404 | THOUSE_2G | 2 | North | YES | -0.013971 | 807 | 250 | 807 | 0 | 1.012 | GSC | -1 | 0.2703 | 807 | 807 |  |  | -11.2746 | 807 | -0.2703 | -218.1298 | 0.43958 | 0.45462 |  |  |  |  | 119 | 0.014904
990 | GIBN_CREK_G1 | 1 | North | YES | -0.013752 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | -1 | 0.27008 | 0 | 463 |  |  | 0 | 0 | -0.27008 | 0 | 0.43958 | 0.45462 |  |  |  |  | 120 | 0.014938
32798 | BRYN_TAMUGEN | 1 | North | YES | -0.013737 | 32 | 0 | 32 |  | 1.02 | GST | -1 | 0.27006 | 32 | 32 |  |  | -0.43958 | 32 | -0.27006 | -8.642 | 0.44033 | 0.45537 |  |  |  |  | 121 | 0.01498
32886 | BRYN_ATKINS3 | MB | North | YES | -0.013721 | 0 | 5 | 12 |  | 1 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0 | 0.44033 | 0.45537 |  |  |  |  | 122 | 0.015041
32887 | BRYN_ATKINS6 | MB | North | YES | -0.013721 | 0 | 12 | 51 |  | 1.028 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0 | 0.44033 | 0.45537 |  |  |  |  | 123 | 0.015041
32888 | BRYN_ATKINS7 | 1 | North | YES | -0.013721 | 13.6 | 4 | 17 |  | 1.028 | GGT | -1 | 0.27005 | 17 | 17 |  |  | -0.23326 | 17 | -0.27005 | -4.5908 | 0.44073 | 0.45577 |  |  |  |  | 124 | 0.015043
32890 | BRYN_ATKINS4 | MB | North | YES | -0.013721 | 0 | 5 | 22 |  | 1.031 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0 | 0.44073 | 0.45577 |  |  |  |  | 125 | 0.015043
32891 | BRYN_ATKINS5 | MB | North | YES | -0.013721 | 0 | 5 | 25 |  | 1.031 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0 | 0.44073 | 0.45577 |  |  |  |  | 126 | 0.015043
32883 | BRYN_DNSBY3 | 1 | North | YES | -0.013678 | 0 | 2 | 48 |  | 1.015 | GST | -1 | 0.27 | 48 | 48 |  |  | -0.65654 | 48 | -0.27 | -12.9602 | 0.44185 | 0.4569 |  |  |  |  | 127 | 0.015044
32884 | BRYN_DNSBY13 | 1 | North | YES | -0.013678 | 46 | 2 | 46 | 0 | 1.015 | GST | -1 | 0.27 | 46 | 46 |  |  | -0.62919 | 46 | -0.27 | -12.4202 | 0.44293 | 0.45798 |  |  |  |  | 128 | 0.015044
32892 | BRYN_DNSBY14 | 1 | North | YES | -0.013678 | 84 | 25 | 105 | 0 | 1.035 | GST | -1 | 0.27 | 105 | 105 |  |  | -1.4362 | 105 | -0.27 | -28.3504 | 0.44539 | 0.46044 |  |  |  |  | 129 | 0.015044
1898 | COMCHEPK_1G | 1 | North | YES | -0.013425 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | -1 | 0.26975 | 0 | 0 |  |  | 0 | 0 | -0.26975 | 0 | 0.44539 | 0.46044 |  |  |  |  | 130 | 0.015046
1899 | COMCHEPK_2G | 2 | North | YES | -0.013425 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | -1 | 0.26975 | 0 | 0 |  |  | 0 | 0 | -0.26975 | 0 | 0.44539 | 0.46044 |  |  |  |  | 131 | 0.015048
3416 | LAKE_CRK1_G | 1 | North | YES | -0.013262 | 60 | 33 | 75 |  | 1.029 | GST | -1 | 0.26959 | 75 | 75 |  |  | -0.99465 | 75 | -0.26959 | -20.2191 | 0.44714 | 0.46219 |  |  |  |  | 132 | 0.015054
3417 | LAKE_CRK2_G | 2 | North | YES | -0.013262 | 177.6 | 40 | 222 | 0 | 1.029 | GST | -1 | 0.26959 | 222 | 222 |  |  | -2.9442 | 222 | -0.26959 | -59.8486 | 0.45233 | 0.46739 |  |  |  |  | 133 | 0.015054
48671 | FTR_GT1_5105 | 1 | North | YES | -0.013223 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | -1 | 0.26955 | 154.2 | 154.2 |  |  | -2.039 | 154.2 | -0.26955 | -41.5645 | 0.45594 | 0.471 |  |  |  |  | 134 | 0.015054
48672 | FTR_GT2_5110 | 2 | North | YES | -0.013223 | 159 | 0 | 159 | 0 | 1.0319 | CC | -1 | 0.26955 | 159 | 159 |  |  | -2.1025 | 159 | -0.26955 | -42.8583 | 0.45966 | 0.47472 |  |  |  |  | 135 | 0.015055
48673 | FTR_GT3_5085 | 3 | North | YES | -0.013223 | 158 | 0 | 158 | 0 | 1.0319 | CC | -1 | 0.26955 | 158 | 158 |  |  | -2.0892 | 158 | -0.26955 | -42.5888 | 0.46336 | 0.47842 |  |  |  |  | 136 | 0.015058
48674 | FTR_CN4_5095 | 4 | North | YES | -0.013223 | 380 | 0 | 380 | 0 | 1.0319 | CC | -1 | 0.26955 | 380 | 380 |  |  | -5.0247 | 380 | -0.26955 | -102.4287 | 0.47225 | 0.48731 |  |  |  |  | 137 | 0.015059
238 | BOSQUESW505 | 1 | North | YES | -0.013117 | 255 | 0 | 255 | 0 | 1.02 | CC | -1 | 0.26944 | 255 | 255 |  |  | -3.3448 | 255 | -0.26944 | -68.708 | 0.47821 | 0.49328 |  |  |  |  | 138 | 0.015061
239 | BOSQUESW502 | 1 | North | YES | -0.013117 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | -1 | 0.26944 | 149 | 149 |  |  | -1.9544 | 149 | -0.26944 | -40.147 | 0.4817 | 0.49676 |  |  |  |  | 139 | 0.015063
247 | BOSQUESW501 | 2 | North | YES | -0.013117 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | -1 | 0.26944 | 156 | 156 |  |  | -2.0463 | 156 | -0.26944 | -42.0331 | 0.48535 | 0.50041 |  |  |  |  | 140 | 0.015067
244 | WHITNYDM01 | 1 | North | YES | -0.012393 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.26872 | 0 | 0 |  |  | 0 | 0 | -0.26872 | 0 | 0.48535 | 0.50041 |  |  |  |  | 141 | 0.015067
245 | WHITNYDM02 | 2 | North | YES | -0.012393 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.26872 | 0 | 0 |  |  | 0 | 0 | -0.26872 | 0 | 0.48535 | 0.50041 |  |  |  |  | 142 | 0.015067
251 | BOSQUESW803 | 2 | North | YES | -0.01188 | 150 | 0 | 150 | 0 | 1.032 | CC | -1 | 0.26821 | 150 | 150 |  |  | -1.782 | 150 | -0.26821 | -40.2309 | 0.48886 | 0.50391 |  |  |  |  | 143 | 0.015067
253 | BOSQUESW804 | 2 | North | YES | -0.01188 | 80 | 0 | 80 | 0 | 1.032 | CC | -1 | 0.26821 | 80 | 80 |  |  | -0.9504 | 80 | -0.26821 | -21.4565 | 0.49073 | 0.50577 |  |  |  |  | 144 | 0.015067
332 | RWMILLER01 | 1 | North | YES | -0.010926 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | -1 | 0.26725 | 73 | 73 |  |  | -0.7976 | 73 | -0.26725 | -19.5094 | 0.49244 | 0.50746 |  |  |  |  | 145 | 0.015067
333 | RWMILLER02 | 2 | North | YES | -0.010926 | 95.2 | 37 | 119 | 0 | 1.04 | GST | -1 | 0.26725 | 119 | 119 |  |  | -1.3002 | 119 | -0.26725 | -31.803 | 0.49522 | 0.51023 |  |  |  |  | 146 | 0.015051
334 | RWMILLER03 | 3 | North | YES | -0.010926 | 166.4 | 65 | 208 | 0 | 1.04 | GST | -1 | 0.26725 | 208 | 208 |  |  | -2.2726 | 208 | -0.26725 | -55.5885 | 0.50009 | 0.51505 |  |  |  |  | 147 | 0.015043
335 | RWMILLER04 | 4 | North | YES | -0.010926 | 81.6 | 0 | 102 | 0 | 1.04 | GST | -1 | 0.26725 | 102 | 102 |  |  | -1.1145 | 102 | -0.26725 | -27.2597 | 0.50247 | 0.51742 |  |  |  |  | 148 | 0.015029
336 | RWMILLER05 | 5 | North | YES | -0.010926 | 80.8 | 0 | 101 | 0 | 1.04 | GST | -1 | 0.26725 | 101 | 101 |  |  | -1.1035 | 101 | -0.26725 | -26.9925 | 0.50483 | 0.51976 |  |  |  |  | 149 | 0.015007
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.010673 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 | 0.50483 | 0.51976 |  |  |  |  | 150 | 0.014967
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.010673 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 | 0.50483 | 0.51976 |  |  |  |  | 151 | 0.014948
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.010673 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 | 0.50483 | 0.51976 |  |  |  |  | 152 | 0.014929
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.010673 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 | 0.50483 | 0.51976 |  |  |  |  | 153 | 0.014929
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.010673 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 | 0.50483 | 0.51976 |  |  |  |  | 154 | 0.014929
48885 | THW_5152 | B | Houston | YES | -0.010389 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.26672 | 59 | 59 |  |  |  |  | -0.26672 | -15.7362 | 0.50621 | 0.52113 |  |  |  |  | 155 | 0.014929
48885 | THW_5152 | A | Houston | YES | -0.010389 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.26672 | 58 | 58 |  |  |  |  | -0.26672 | -15.4695 | 0.50757 | 0.52247 |  |  |  |  | 156 | 0.014929
48886 | THW_5354 | D | Houston | YES | -0.010389 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.26672 | 58 | 58 |  |  |  |  | -0.26672 | -15.4695 | 0.50893 | 0.52382 |  |  |  |  | 157 | 0.014929
48886 | THW_5354 | C | Houston | YES | -0.010389 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.26672 | 57 | 57 |  |  |  |  | -0.26672 | -15.2028 | 0.51026 | 0.52514 |  |  |  |  | 158 | 0.014915
48887 | THW_5556 | E | Houston | YES | -0.010389 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.26672 | 59 | 59 |  |  |  |  | -0.26672 | -15.7362 | 0.51164 | 0.5265 |  |  |  |  | 159 | 0.014901
48887 | THW_5556 | F | Houston | YES | -0.010389 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.26672 | 57 | 57 |  |  |  |  | -0.26672 | -15.2028 | 0.51298 | 0.52782 |  |  |  |  | 160 | 0.014888
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.010366 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.26669 | 398 | 398 |  |  |  |  | -0.26669 | -106.1435 | 0.52229 | 0.53704 |  |  |  |  | 161 | 0.014874
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.010346 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.26667 | 162.8 | 162.8 |  |  |  |  | -0.26667 | -43.4142 | 0.5261 | 0.54081 |  |  |  |  | 162 | 0.01486
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.010346 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.26667 | 161.4 | 161.4 |  |  |  |  | -0.26667 | -43.0409 | 0.52987 | 0.54455 |  |  |  |  | 163 | 0.014847
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.010346 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.26667 | 158.9 | 158.9 |  |  |  |  | -0.26667 | -42.3742 | 0.53359 | 0.54822 |  |  |  |  | 164 | 0.014752
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.010346 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.26667 | 269.2 | 269.2 |  |  |  |  | -0.26667 | -71.7882 | 0.53989 | 0.55446 |  |  |  |  | 165 | 0.014713
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595 | 0.54391 | 0.55844 |  |  |  |  | 166 | 0.014675
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595 | 0.54793 | 0.56242 |  |  |  |  | 167 | 0.014637
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595 | 0.55196 | 0.5664 |  |  |  |  | 168 | 0.014572
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.010295 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.26662 | 0 | 0 |  |  |  |  | -0.26662 | 0 | 0.55196 | 0.5664 |  |  |  |  | 169 | 0.01453
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.010279 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 | 0.55196 | 0.5664 |  |  |  |  | 170 | 0.014488
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.010279 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 | 0.55196 | 0.5664 |  |  |  |  | 171 | 0.014447
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.010279 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 | 0.55196 | 0.5664 |  |  |  |  | 172 | 0.014447
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.010279 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 | 0.55196 | 0.5664 |  |  |  |  | 173 | 0.014447
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.010279 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 | 0.55196 | 0.5664 |  |  |  |  | 174 | 0.014447
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.010279 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 | 0.55196 | 0.5664 |  |  |  |  | 175 | 0.014447
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.010279 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 | 0.55196 | 0.5664 |  |  |  |  | 176 | 0.014447
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.010275 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.2666 | 744 | 744 |  |  |  |  | -0.2666 | -198.3513 | 0.56936 | 0.58363 |  |  |  |  | 177 | 0.014447
48651 | EP_1_2 | 1 | Houston | YES | -0.010275 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0 | 0.56936 | 0.58363 |  |  |  |  | 178 | 0.014447
48651 | EP_1_2 | 2 | Houston | YES | -0.010275 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0 | 0.56936 | 0.58363 |  |  |  |  | 179 | 0.014447
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.010275 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0 | 0.56936 | 0.58363 |  |  |  |  | 180 | 0.014264
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.01025 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.26658 | 12 | 12 |  |  |  |  | -0.26658 | -3.1989 | 0.56964 | 0.5839 |  |  |  |  | 181 | 0.014264
49803 | EXN_15GT | 1 | Houston | YES | -0.010247 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 182 | 0.014264
49804 | EXN_16GT | 2 | Houston | YES | -0.010247 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 183 | 0.014264
49805 | EXN_17GT | 3 | Houston | YES | -0.010247 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 184 | 0.014261
49826 | EXN938GT | 5 | Houston | YES | -0.010247 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 185 | 0.014261
49828 | EXN941GT | 10 | Houston | YES | -0.010247 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 186 | 0.014261
49829 | EXN942GT | 11 | Houston | YES | -0.010247 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 187 | 0.014261
49830 | EXN943GT | 12 | Houston | YES | -0.010247 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 188 | 0.014261
49831 | EXN944GT | 13 | Houston | YES | -0.010247 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 189 | 0.014261
49832 | EXN945GT | 9 | Houston | YES | -0.010247 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 190 | 0.014261
49837 | EXN_GT | 4 | Houston | YES | -0.010247 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 191 | 0.014261
49838 | EXN_14GT | 14 | Houston | YES | -0.010247 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 | 0.56964 | 0.5839 |  |  |  |  | 192 | 0.014261
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.010218 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.26654 | 746 | 746 |  |  |  |  | -0.26654 | -198.842 | 0.5871 | 0.60117 |  |  |  |  | 193 | 0.014261
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.010189 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.26652 | 107 | 107 |  |  |  |  | -0.26652 | -28.5171 | 0.5896 | 0.60365 |  |  |  |  | 194 | 0.014261
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.010189 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.26652 | 108 | 108 |  |  |  |  | -0.26652 | -28.7836 | 0.59213 | 0.60614 |  |  |  |  | 195 | 0.014261
48875 | THW_3132 | A | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583 | 0.59341 | 0.60742 |  |  |  |  | 196 | 0.014074
48875 | THW_3132 | B | Houston | YES | -0.010189 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.26652 | 53 | 53 |  |  |  |  | -0.26652 | -14.1253 | 0.59465 | 0.60864 |  |  |  |  | 197 | 0.014047
48877 | THW_3334 | C | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583 | 0.59594 | 0.60992 |  |  |  |  | 198 | 0.01402
48877 | THW_3334 | D | Houston | YES | -0.010189 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.26652 | 57 | 57 |  |  |  |  | -0.26652 | -15.1914 | 0.59727 | 0.61124 |  |  |  |  | 199 | 0.014006
48879 | THW_4142 | E | Houston | YES | -0.010189 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.26652 | 56 | 56 |  |  |  |  | -0.26652 | -14.9249 | 0.59858 | 0.61253 |  |  |  |  | 200 | 0.013992
48879 | THW_4142 | F | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583 | 0.59987 | 0.6138 |  |  |  |  | 201 | 0.013978
48881 | THW_4344 | G | Houston | YES | -0.010189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.26652 | 58 | 58 |  |  |  |  | -0.26652 | -15.4579 | 0.60123 | 0.61515 |  |  |  |  | 202 | 0.013964
48881 | THW_4344 | H | Houston | YES | -0.010189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.26652 | 58 | 58 |  |  |  |  | -0.26652 | -15.4579 | 0.60258 | 0.61649 |  |  |  |  | 203 | 0.01395
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.010129 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.26646 | 0 | 0 |  |  |  |  | -0.26646 | 0 | 0.60258 | 0.61649 |  |  |  |  | 204 | 0.013936
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.010129 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.26646 | 0 | 0 |  |  |  |  | -0.26646 | 0 | 0.60258 | 0.61649 |  |  |  |  | 205 | 0.013921
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.010119 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.26645 | 42 | 42 |  |  |  |  | -0.26645 | -11.1907 | 0.60356 | 0.61746 |  |  |  |  | 206 | 0.013906
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.010119 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.26645 | 42 | 42 |  |  |  |  | -0.26645 | -11.1907 | 0.60455 | 0.61843 |  |  |  |  | 207 | 0.013906
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.010119 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.26645 | 39 | 39 |  |  |  |  | -0.26645 | -10.3914 | 0.60546 | 0.61933 |  |  |  |  | 208 | 0.013906
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.010119 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.26645 | 39 | 39 |  |  |  |  | -0.26645 | -10.3914 | 0.60637 | 0.62024 |  |  |  |  | 209 | 0.013896
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.010116 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.26644 | 0 | 0 |  |  |  |  | -0.26644 | 0 | 0.60637 | 0.62024 |  |  |  |  | 210 | 0.013885
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.010076 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0 | 0.60637 | 0.62024 |  |  |  |  | 211 | 0.013875
48821 | SHELLG2 | 2 | Houston | YES | -0.010076 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0 | 0.60637 | 0.62024 |  |  |  |  | 212 | 0.013864
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.010076 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0 | 0.60637 | 0.62024 |  |  |  |  | 213 | 0.013864
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.010076 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0 | 0.60637 | 0.62024 |  |  |  |  | 214 | 0.013864
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.010051 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 | 0.60637 | 0.62024 |  |  |  |  | 215 | 0.013864
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.010051 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 | 0.60637 | 0.62024 |  |  |  |  | 216 | 0.013864
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.010051 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 | 0.60637 | 0.62024 |  |  |  |  | 217 | 0.013864
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.01005 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 | 0.60637 | 0.62024 |  |  |  |  | 218 | 0.013864
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.01005 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 | 0.60637 | 0.62024 |  |  |  |  | 219 | 0.013864
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.01005 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 | 0.60637 | 0.62024 |  |  |  |  | 220 | 0.013864
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.01005 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 | 0.60637 | 0.62024 |  |  |  |  | 221 | 0.013864
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.01005 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.26638 | 228 | 228 |  |  |  |  | -0.26638 | -60.7338 | 0.61171 | 0.62551 |  |  |  |  | 222 | 0.013864
48845 | SOL_GT1 | 1 | Houston | YES | -0.010049 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.26638 | 16.2 | 16.2 |  |  |  |  | -0.26638 | -4.3153 | 0.61208 | 0.62588 |  |  |  |  | 223 | 0.013864
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.010049 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.26638 | 213 | 213 |  |  |  |  | -0.26638 | -56.7379 | 0.61707 | 0.63081 |  |  |  |  | 224 | 0.013864
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.010045 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.26637 | 0 | 0 |  |  |  |  | -0.26637 | 0 | 0.61707 | 0.63081 |  |  |  |  | 225 | 0.013804
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.010045 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.26637 | 0 | 0 |  |  |  |  | -0.26637 | 0 | 0.61707 | 0.63081 |  |  |  |  | 226 | 0.0138
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.010044 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.26637 | 165 | 165 |  |  |  |  | -0.26637 | -43.9511 | 0.62093 | 0.63463 |  |  |  |  | 227 | 0.013743
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.010043 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.26637 | 176 | 176 |  |  |  |  | -0.26637 | -46.881 | 0.62505 | 0.6387 |  |  |  |  | 228 | 0.013743
48855 | SRB_GT211035 | B1 | Houston | YES | -0.010042 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.26637 | 18 | 18 |  |  |  |  | -0.26637 | -4.7946 | 0.62547 | 0.63911 |  |  |  |  | 229 | 0.013743
48855 | SRB_GT211035 | B2 | Houston | YES | -0.010042 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.26637 | 12 | 12 |  |  |  |  | -0.26637 | -3.1964 | 0.62575 | 0.63939 |  |  |  |  | 230 | 0.013699
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.010025 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.26635 | 0 | 0 |  |  |  |  | -0.26635 | 0 | 0.62575 | 0.63939 |  |  |  |  | 231 | 0.013653
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.010001 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.26633 | 163.2 | 163.2 |  |  |  |  | -0.26633 | -43.4646 | 0.62957 | 0.64317 |  |  |  |  | 232 | 0.013648
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.010001 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.26633 | 157.1 | 157.1 |  |  |  |  | -0.26633 | -41.84 | 0.63324 | 0.6468 |  |  |  |  | 233 | 0.013645
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.010001 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.26633 | 157.5 | 157.5 |  |  |  |  | -0.26633 | -41.9465 | 0.63692 | 0.65044 |  |  |  |  | 234 | 0.013645
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.010001 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.26633 | 157 | 157 |  |  |  |  | -0.26633 | -41.8134 | 0.6406 | 0.65407 |  |  |  |  | 235 | 0.013601
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.010001 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.26633 | 282 | 282 |  |  |  |  | -0.26633 | -75.1043 | 0.64719 | 0.66059 |  |  |  |  | 236 | 0.013558
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.009986 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.26631 | 0 | 0 |  |  |  |  | -0.26631 | 0 | 0.64719 | 0.66059 |  |  |  |  | 237 | 0.013516
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.009986 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.26631 | 0 | 0 |  |  |  |  | -0.26631 | 0 | 0.64719 | 0.66059 |  |  |  |  | 238 | 0.013474
48691 | GBY_73741085 | B | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161 | 0.64829 | 0.66168 |  |  |  |  | 239 | 0.013398
48691 | GBY_73741085 | A | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161 | 0.64939 | 0.66277 |  |  |  |  | 240 | 0.013398
48692 | GBY_81821075 | D | Houston | YES | -0.009973 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.2663 | 55 | 55 |  |  |  |  | -0.2663 | -14.6465 | 0.65068 | 0.66404 |  |  |  |  | 241 | 0.013398
48692 | GBY_81821075 | C | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161 | 0.65178 | 0.66512 |  |  |  |  | 242 | 0.013385
48693 | GBY_83841065 | F | Houston | YES | -0.009973 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.2663 | 54 | 54 |  |  |  |  | -0.2663 | -14.3802 | 0.65304 | 0.66637 |  |  |  |  | 243 | 0.013372
48693 | GBY_83841065 | E | Houston | YES | -0.009973 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.2663 | 57 | 57 |  |  |  |  | -0.2663 | -15.1791 | 0.65438 | 0.66769 |  |  |  |  | 244 | 0.013357
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.009911 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0 | 0.65438 | 0.66769 |  |  |  |  | 245 | 0.013344
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.009911 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0 | 0.65438 | 0.66769 |  |  |  |  | 246 | 0.01333
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.009911 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0 | 0.65438 | 0.66769 |  |  |  |  | 247 | 0.013314
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.009911 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0 | 0.65438 | 0.66769 |  |  |  |  | 248 | 0.013314
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.009872 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | 0.65438 | 0.66769 |  |  |  |  | 249 | 0.013314
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.009872 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | 0.65438 | 0.66769 |  |  |  |  | 250 | 0.013314
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.009872 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | 0.65438 | 0.66769 |  |  |  |  | 251 | 0.013314
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.009872 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | 0.65438 | 0.66769 |  |  |  |  | 252 | 0.013314
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.009872 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 | 0.65438 | 0.66769 |  |  |  |  | 253 | 0.013314
48772 | PHR_GN2_2 | MB | Houston | YES | -0.009768 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.26609 | 0 | 0 |  |  |  |  | -0.26609 | 0 | 0.65438 | 0.66769 |  |  |  |  | 254 | 0.013314
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.009621 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 255 | 0.013314
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.009621 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 256 | 0.013314
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.009621 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 257 | 0.013314
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.009621 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 258 | 0.013314
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.009621 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 259 | 0.013314
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.009621 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 260 | 0.013314
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.009621 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 261 | 0.013314
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.009621 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 262 | 0.013314
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.009621 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 263 | 0.013314
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.009621 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 264 | 0.013314
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.009621 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 265 | 0.013314
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.009621 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 266 | 0.013314
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.009621 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 267 | 0.013314
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.009621 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 268 | 0.013314
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.009621 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 | 0.65438 | 0.66769 |  |  |  |  | 269 | 0.013314
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.009316 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.26564 | 166 | 166 |  |  |  |  | -0.26564 | -44.0966 | 0.65826 | 0.67152 |  |  |  |  | 270 | 0.013314
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.009316 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.26564 | 166 | 166 |  |  |  |  | -0.26564 | -44.0966 | 0.66214 | 0.67535 |  |  |  |  | 271 | 0.013314
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.009316 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.26564 | 248 | 248 |  |  |  |  | -0.26564 | -65.8793 | 0.66795 | 0.68107 |  |  |  |  | 272 | 0.013314
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.009316 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.26564 | 546 | 546 |  |  |  |  | -0.26564 | -145.0406 | 0.68072 | 0.69366 |  |  |  |  | 273 | 0.01326
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.009316 | 620.4 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.26564 | 0 | 654 |  |  |  |  | -0.26564 | 0 | 0.68072 | 0.69366 |  |  |  |  | 274 | 0.013205
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.009316 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.26564 | 13 | 13 |  |  |  |  | -0.26564 | -3.4533 | 0.68102 | 0.69396 |  |  |  |  | 275 | 0.013124
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.009252 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.26558 | 0 | 0 |  |  |  |  | -0.26558 | 0 | 0.68102 | 0.69396 |  |  |  |  | 276 | 0.012944
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.009212 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.26554 | 167.7 | 167.7 |  |  |  |  | -0.26554 | -44.5308 | 0.68495 | 0.69783 |  |  |  |  | 277 | 0.012944
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.009212 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.26554 | 166.4 | 166.4 |  |  |  |  | -0.26554 | -44.1856 | 0.68884 | 0.70167 |  |  |  |  | 278 | 0.01294
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.009212 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.26554 | 252.4 | 252.4 |  |  |  |  | -0.26554 | -67.0218 | 0.69474 | 0.70749 |  |  |  |  | 279 | 0.01294
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.009208 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 651 |  |  |  |  | -0.26553 | 0 | 0.69474 | 0.70749 |  |  |  |  | 280 | 0.012883
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.009208 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 564 |  |  |  |  | -0.26553 | 0 | 0.69474 | 0.70749 |  |  |  |  | 281 | 0.012827
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.009208 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 603 |  |  |  |  | -0.26553 | 0 | 0.69474 | 0.70749 |  |  |  |  | 282 | 0.012742
48730 | MNS_GT | 1 | Houston | YES | -0.009168 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.26549 | 0 | 0 |  |  |  |  | -0.26549 | 0 | 0.69474 | 0.70749 |  |  |  |  | 283 | 0.012742
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.008613 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 | 0.69474 | 0.70749 |  |  |  |  | 284 | 0.012742
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.008613 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 | 0.69474 | 0.70749 |  |  |  |  | 285 | 0.012742
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.008613 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 | 0.69474 | 0.70749 |  |  |  |  | 286 | 0.012742
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.008613 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 | 0.69474 | 0.70749 |  |  |  |  | 287 | 0.012742
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.008444 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.26477 | 0 | 0 |  |  |  |  | -0.26477 | 0 | 0.69474 | 0.70749 |  |  |  |  | 288 | 0.012742
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.008444 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.26477 | 0 | 0 |  |  |  |  | -0.26477 | 0 | 0.69474 | 0.70749 |  |  |  |  | 289 | 0.012742
13432 | SANDOW_5G | 5 | South | YES | -0.008279 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.26461 | 0 | 581 |  |  |  |  | -0.26461 | 0 | 0.69474 | 0.70749 |  |  |  |  | 290 | 0.012742
49851 | DOW17000 | 37 | Houston | YES | -0.008243 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 291 | 0.012742
49858 | DOW38100 | 31 | Houston | YES | -0.008243 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 292 | 0.012742
49859 | DOW38200 | 33 | Houston | YES | -0.008243 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 293 | 0.012742
49860 | DOW38300 | 32 | Houston | YES | -0.008243 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 294 | 0.012742
49862 | DOW39100 | 36 | Houston | YES | -0.008243 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 295 | 0.012742
49863 | DOW39200 | 35 | Houston | YES | -0.008243 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 296 | 0.012742
49865 | DOW41000 | 41 | Houston | YES | -0.008243 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 297 | 0.012742
49866 | DOW42000 | 42 | Houston | YES | -0.008243 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 298 | 0.012742
49869 | DOW49000 | 45 | Houston | YES | -0.008243 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 299 | 0.012742
49870 | DOW61000 | 61 | Houston | YES | -0.008243 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 300 | 0.012742
49871 | DOW62000 | 62 | Houston | YES | -0.008243 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 301 | 0.012742
49872 | DOW63000 | 63 | Houston | YES | -0.008243 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 302 | 0.012742
49873 | DOW64000 | 64 | Houston | YES | -0.008243 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 303 | 0.012742
49876 | DOW65000 | 65 | Houston | YES | -0.008243 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 304 | 0.012742
49877 | DOW66000 | 66 | Houston | YES | -0.008243 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 305 | 0.012742
49878 | DOW67000 | 67 | Houston | YES | -0.008243 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 306 | 0.012742
49882 | DOW81000 | 81 | Houston | YES | -0.008243 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 307 | 0.012742
49884 | DOW82000 | 82 | Houston | YES | -0.008243 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 308 | 0.012742
49885 | DOW83000 | 83 | Houston | YES | -0.008243 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 309 | 0.012742
49886 | DOW84000 | 84 | Houston | YES | -0.008243 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 | 0.69474 | 0.70749 |  |  |  |  | 310 | 0.012742
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.007407 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.26373 | 0 | 0 |  |  |  |  | -0.26373 | 0 | 0.69474 | 0.70749 |  |  |  |  | 311 | 0.012742
48731 | CBE_GT1 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 | 0.69652 | 0.70922 |  |  |  |  | 312 | 0.012742
48732 | CBE_GT2 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 | 0.6983 | 0.71096 |  |  |  |  | 313 | 0.012742
48733 | CBE_ST12 | 1 | Houston | YES | -0.007274 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.2636 | 105 | 105 |  |  |  |  | -0.2636 | -27.678 | 0.70076 | 0.71337 |  |  |  |  | 314 | 0.012742
48734 | CBE_GT3 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 | 0.70253 | 0.71511 |  |  |  |  | 315 | 0.012703
48735 | CBE_GT4 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 | 0.70431 | 0.71685 |  |  |  |  | 316 | 0.012665
48736 | CBE_ST34 | 1 | Houston | YES | -0.007274 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.2636 | 105 | 105 |  |  |  |  | -0.2636 | -27.678 | 0.70677 | 0.71925 |  |  |  |  | 317 | 0.012611
5911 | STP_GN1___1 | 1 | Houston | YES | -0.007142 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.26347 | 0 | 0 |  |  |  |  | -0.26347 | 0 | 0.70677 | 0.71925 |  |  |  |  | 318 | 0.012573
5912 | STP_GN2___2 | 2 | Houston | YES | -0.007142 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.26347 | 0 | 0 |  |  |  |  | -0.26347 | 0 | 0.70677 | 0.71925 |  |  |  |  | 319 | 0.012535
3432 | SANDOW_4G | 4 | South | YES | -0.006951 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.26328 | 0 | 580 |  |  |  |  | -0.26328 | 0 | 0.70677 | 0.71925 |  |  |  |  | 320 | 0.012481
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.005275 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 606 |  |  |  |  | -0.2616 | 0 | 0.70677 | 0.71925 |  |  |  |  | 321 | 0.012481
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.005275 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 598 |  |  |  |  | -0.2616 | 0 | 0.70677 | 0.71925 |  |  |  |  | 322 | 0.012481
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.005273 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 436 |  |  |  |  | -0.2616 | 0 | 0.70677 | 0.71925 |  |  |  |  | 323 | 0.012481
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.005252 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.26158 | 158 | 158 |  |  |  |  | -0.26158 | -41.3294 | 0.71046 | 0.72284 |  |  |  |  | 324 | 0.012481
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.005252 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.26158 | 160 | 160 |  |  |  |  | -0.26158 | -41.8525 | 0.71421 | 0.72647 |  |  |  |  | 325 | 0.012481
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.005252 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.26158 | 175 | 175 |  |  |  |  | -0.26158 | -45.7762 | 0.7183 | 0.73045 |  |  |  |  | 326 | 0.012481
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 | 0.71947 | 0.73158 |  |  |  |  | 327 | 0.012374
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 | 0.72064 | 0.73271 |  |  |  |  | 328 | 0.012265
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 | 0.72181 | 0.73385 |  |  |  |  | 329 | 0.012145
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 | 0.72298 | 0.73498 |  |  |  |  | 330 | 0.012109
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.004759 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.26109 | 152.5 | 152.5 |  |  |  |  | -0.26109 | -39.8155 | 0.72655 | 0.73844 |  |  |  |  | 331 | 0.012073
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.004759 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.26109 | 149.5 | 149.5 |  |  |  |  | -0.26109 | -39.0322 | 0.73005 | 0.74183 |  |  |  |  | 332 | 0.012038
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.004759 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.26109 | 232.6 | 232.6 |  |  |  |  | -0.26109 | -60.7284 | 0.73549 | 0.7471 |  |  |  |  | 333 | 0.012002
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.004292 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.26062 | 132 | 132 |  |  |  |  | -0.26062 | -34.4016 | 0.73857 | 0.75009 |  |  |  |  | 334 | 0.011891
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.004292 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.26062 | 139 | 139 |  |  |  |  | -0.26062 | -36.2259 | 0.74183 | 0.75323 |  |  |  |  | 335 | 0.011783
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.004292 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.26062 | 329 | 329 |  |  |  |  | -0.26062 | -85.7434 | 0.74952 | 0.76068 |  |  |  |  | 336 | 0.011614
9002 | DECKR_G3 | 3 | South | YES | -0.003822 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.26015 | 42 | 42 |  |  |  |  | -0.26015 | -10.9262 | 0.75051 | 0.76163 |  |  |  |  | 337 | 0.011513
9003 | DECKR_G4 | 4 | South | YES | -0.003822 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.26015 | 44 | 44 |  |  |  |  | -0.26015 | -11.4465 | 0.75154 | 0.76262 |  |  |  |  | 338 | 0.011407
9004 | DECKR_G5 | 5 | South | YES | -0.003822 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.26015 | 44 | 44 |  |  |  |  | -0.26015 | -11.4465 | 0.75256 | 0.76362 |  |  |  |  | 339 | 0.011155
9005 | DECKR_G6 | 6 | South | YES | -0.003822 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.26015 | 47 | 47 |  |  |  |  | -0.26015 | -12.227 | 0.75366 | 0.76468 |  |  |  |  | 340 | 0.011121
8134 | FOR #1 | 1 | South | YES | -0.003787 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 341 | 0.011086
8138 | FOR #2 | 2 | South | YES | -0.003787 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 342 | 0.01105
8153 | FOR #3 | 3 | South | YES | -0.003787 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 343 | 0.011013
8154 | FOR #4 | 4 | South | YES | -0.003787 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 344 | 0.011013
8155 | FOR #5 | 5 | South | YES | -0.003787 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 345 | 0.011013
8156 | FOR #6 | 6 | South | YES | -0.003787 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 346 | 0.011013
8157 | FOR #7 | 7 | South | YES | -0.003787 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 347 | 0.011013
80051 | FOR #8 | 8 | South | YES | -0.003787 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 348 | 0.011013
80052 | FOR #9 | 9 | South | YES | -0.003787 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 349 | 0.011013
80053 | FOR #10 | 10 | South | YES | -0.003787 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 | 0.75366 | 0.76468 |  |  |  |  | 350 | 0.011013
80226 | ALCOA G | 1 | South | YES | -0.003687 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.26001 | 0 | 0 |  |  |  |  | -0.26001 | 0 | 0.75366 | 0.76468 |  |  |  |  | 351 | 0.011013
9000 | DECKR_G1 | 1 | South | YES | -0.003627 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.25995 | 321 | 321 |  |  |  |  | -0.25995 | -83.445 | 0.76117 | 0.77192 |  |  |  |  | 352 | 0.011013
9001 | DECKR_G2 | 2 | South | YES | -0.003627 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.25995 | 426 | 426 |  |  |  |  | -0.25995 | -110.7401 | 0.77114 | 0.78154 |  |  |  |  | 353 | 0.011013
9016 | SANDH_G1 | 1 | South | YES | -0.003618 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.25994 | 49 | 49 |  |  |  |  | -0.25994 | -12.7373 | 0.77229 | 0.78264 |  |  |  |  | 354 | 0.011013
9017 | SANDH_G2 | 2 | South | YES | -0.003618 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.25994 | 46 | 46 |  |  |  |  | -0.25994 | -11.9574 | 0.77336 | 0.78368 |  |  |  |  | 355 | 0.010748
9018 | SANDH_G3 | 3 | South | YES | -0.003618 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.25994 | 46 | 46 |  |  |  |  | -0.25994 | -11.9574 | 0.77444 | 0.78472 |  |  |  |  | 356 | 0.010398
9019 | SANDH_G4 | 4 | South | YES | -0.003618 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.25994 | 47 | 47 |  |  |  |  | -0.25994 | -12.2174 | 0.77554 | 0.78578 |  |  |  |  | 357 | 0.010358
9020 | SANDHG5A | 5A | South | YES | -0.003618 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.25994 | 155 | 155 |  |  |  |  | -0.25994 | -40.2914 | 0.77916 | 0.78928 |  |  |  |  | 358 | 0.01032
9021 | SANDHG5C | 5C | South | YES | -0.003618 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.25994 | 148 | 148 |  |  |  |  | -0.25994 | -38.4717 | 0.78263 | 0.79262 |  |  |  |  | 359 | 0.010282
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.00335 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.25968 | 0 | 0 |  |  |  |  | -0.25968 | 0 | 0.78263 | 0.79262 |  |  |  |  | 360 | 0.010243
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.00335 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.25968 | 0 | 0 |  |  |  |  | -0.25968 | 0 | 0.78263 | 0.79262 |  |  |  |  | 361 | 0.010115
8147 | UCAR #2 | 10 | South | YES | -0.003309 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | 0.78263 | 0.79262 |  |  |  |  | 362 | 0.0099936
8148 | UCAR #1 | 2 | South | YES | -0.003309 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | 0.78263 | 0.79262 |  |  |  |  | 363 | 0.0099936
80137 | CSDR89 | 9 | South | YES | -0.003309 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | 0.78263 | 0.79262 |  |  |  |  | 364 | 0.0099936
80137 | CSDR89 | 8 | South | YES | -0.003309 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | 0.78263 | 0.79262 |  |  |  |  | 365 | 0.0099936
80138 | CSDR7 | 7 | South | YES | -0.003309 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | 0.78263 | 0.79262 |  |  |  |  | 366 | 0.0099936
80139 | CSDR56 | 6 | South | YES | -0.003309 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | 0.78263 | 0.79262 |  |  |  |  | 367 | 0.0099936
80139 | CSDR56 | 5 | South | YES | -0.003309 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | 0.78263 | 0.79262 |  |  |  |  | 368 | 0.0099936
80140 | CSDR11 | 11 | South | YES | -0.003309 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 | 0.78263 | 0.79262 |  |  |  |  | 369 | 0.0099936
80227 | AIRCO G | 1 | South | YES | -0.003228 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.25955 | 0 | 0 |  |  |  |  | -0.25955 | 0 | 0.78263 | 0.79262 |  |  |  |  | 370 | 0.0099936
80224 | VISTRONG1 | 1 | South | YES | -0.00321 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.25954 | 0 | 0 |  |  |  |  | -0.25954 | 0 | 0.78263 | 0.79262 |  |  |  |  | 371 | 0.0099936
80225 | VISTRONG2 | 2 | South | YES | -0.00321 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.25954 | 0 | 0 |  |  |  |  | -0.25954 | 0 | 0.78263 | 0.79262 |  |  |  |  | 372 | 0.0099936
8066 | DUP1V#1 | 1 | South | YES | -0.003094 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.25942 | 0 | 0 |  |  |  |  | -0.25942 | 0 | 0.78263 | 0.79262 |  |  |  |  | 373 | 0.0099936
8173 | VICEC51A | 5 | South | YES | -0.002999 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.25933 | 144 | 144 |  |  |  |  | -0.25933 | -37.3428 | 0.78599 | 0.79586 |  |  |  |  | 374 | 0.0099936
8174 | VICEC61A | 6 | South | YES | -0.002999 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.25933 | 188 | 188 |  |  |  |  | -0.25933 | -48.7531 | 0.79039 | 0.8001 |  |  |  |  | 375 | 0.0099936
5508 | RAYBURNCC9 | 1 | South | YES | -0.002955 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.25928 | 47.7 | 47.7 |  |  |  |  | -0.25928 | -12.3677 | 0.79151 | 0.80117 |  |  |  |  | 376 | 0.0099936
5509 | RAYBURNCC10 | 1 | South | YES | -0.002955 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.25928 | 37.3 | 37.3 |  |  |  |  | -0.25928 | -9.6712 | 0.79238 | 0.80201 |  |  |  |  | 377 | 0.0098672
5511 | RAYBURNCC7 | 1 | South | YES | -0.002955 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.25928 | 47.5 | 47.5 |  |  |  |  | -0.25928 | -12.3159 | 0.79349 | 0.80308 |  |  |  |  | 378 | 0.0097023
5512 | RAYBURNCC8 | 1 | South | YES | -0.002955 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.25928 | 49.3 | 49.3 |  |  |  |  | -0.25928 | -12.7826 | 0.79465 | 0.80419 |  |  |  |  | 379 | 0.0096603
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.00278 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.25911 | 223.9 | 223.9 |  |  |  |  | -0.25911 | -58.0139 | 0.79988 | 0.80923 |  |  |  |  | 380 | 0.0096274
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.00278 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.25911 | 225 | 225 |  |  |  |  | -0.25911 | -58.2989 | 0.80515 | 0.81429 |  |  |  |  | 381 | 0.0095855
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.00278 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.25911 | 224.6 | 224.6 |  |  |  |  | -0.25911 | -58.1953 | 0.8104 | 0.81934 |  |  |  |  | 382 | 0.0095421
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.00278 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.25911 | 226.7 | 226.7 |  |  |  |  | -0.25911 | -58.7394 | 0.81571 | 0.82444 |  |  |  |  | 383 | 0.0093414
5503 | RAYBURNGEN3 | 1 | South | YES | -0.002752 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.25908 | 22 | 22 |  |  |  |  | -0.25908 | -5.6997 | 0.81622 | 0.82494 |  |  |  |  | 384 | 0.0091397
5505 | RAYBURNGEN1 | 1 | South | YES | -0.002752 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.25908 | 11 | 11 |  |  |  |  | -0.25908 | -2.8499 | 0.81648 | 0.82518 |  |  |  |  | 385 | 0.0089384
5506 | RAYBURNGEN2 | 1 | South | YES | -0.002752 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.25908 | 11 | 11 |  |  |  |  | -0.25908 | -2.8499 | 0.81673 | 0.82543 |  |  |  |  | 386 | 0.0087352
8189 | CUECPL2A | 1 | South | YES | -0.00272 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.25905 | 0 | 0 |  |  |  |  | -0.25905 | 0 | 0.81673 | 0.82543 |  |  |  |  | 387 | 0.0087154
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.002697 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.25902 | 0 | 0 |  |  |  |  | -0.25902 | 0 | 0.81673 | 0.82543 |  |  |  |  | 388 | 0.0087055
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.002697 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.25902 | 0 | 0 |  |  |  |  | -0.25902 | 0 | 0.81673 | 0.82543 |  |  |  |  | 389 | 0.0086956
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.002549 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.25888 | 148 | 148 |  |  |  |  | -0.25888 | -38.3135 | 0.8202 | 0.82876 |  |  |  |  | 390 | 0.0086956
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.002549 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.25888 | 148 | 148 |  |  |  |  | -0.25888 | -38.3135 | 0.82366 | 0.83208
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.002549 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.25888 | 154 | 154 |  |  |  |  | -0.25888 | -39.8668 | 0.82726 | 0.83555
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.002549 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.25888 | 293 | 293 |  |  |  |  | -0.25888 | -75.8504 | 0.83412 | 0.84213
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.0024 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 | 0.83412 | 0.84213
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.0024 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 | 0.83412 | 0.84213
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.0024 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 | 0.83412 | 0.84213
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.002314 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.25864 | 147 | 147 |  |  |  |  | -0.25864 | -38.0201 | 0.83756 | 0.84543
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.002314 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.25864 | 138 | 138 |  |  |  |  | -0.25864 | -35.6923 | 0.84078 | 0.84853
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.002314 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.25864 | 146 | 146 |  |  |  |  | -0.25864 | -37.7615 | 0.8442 | 0.85181
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.002314 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.25864 | 149 | 149 |  |  |  |  | -0.25864 | -38.5374 | 0.84769 | 0.85516
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.002314 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.25864 | 182 | 182 |  |  |  |  | -0.25864 | -47.0725 | 0.85194 | 0.85924
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.002314 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.25864 | 203 | 203 |  |  |  |  | -0.25864 | -52.504 | 0.85669 | 0.8638
8161 | COLETO0A | 1 | South | YES | -0.002182 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.25851 | 0 | 633 |  |  |  |  | -0.25851 | 0 | 0.85669 | 0.8638
8926 | LGE_GT10A | 1 | South | YES | -0.002126 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | 0.85669 | 0.8638
8927 | LGE_GT20A | 2 | South | YES | -0.002126 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | 0.85669 | 0.8638
8928 | LGE_STG0A | 3 | South | YES | -0.002126 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | 0.85669 | 0.8638
8930 | ICPGN10A | 1 | South | YES | -0.002126 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | 0.85669 | 0.8638
8931 | ICPGN20A | 2 | South | YES | -0.002126 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | 0.85669 | 0.8638
8932 | ICPGN30A | 3 | South | YES | -0.002126 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | 0.85669 | 0.8638
80223 | REYSHR G | 1 | South | YES | -0.002126 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 | 0.85669 | 0.8638
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.002067 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.25839 | 0 | 0 |  |  |  |  | -0.25839 | 0 | 0.85669 | 0.8638
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.001991 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.25832 | 0 | 0 |  |  |  |  | -0.25832 | 0 | 0.85669 | 0.8638
8442 | NBEC7 | 7 | South | YES | -0.001892 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.25822 | 367 | 367 |  |  |  |  | -0.25822 | -94.7661 | 0.86528 | 0.87203
8442 | NBEC7 | MB | South | YES | -0.001892 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 | 0.86528 | 0.87203
8560 | CNOPGT1 | 1 | South | YES | -0.001889 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 | 0.86528 | 0.87203
8561 | CNOPGT2 | 2 | South | YES | -0.001889 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 | 0.86528 | 0.87203
8562 | CNOPST1 | 3 | South | YES | -0.001889 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 | 0.86528 | 0.87203
8456 | COSW#1 | 1 | South | YES | -0.001877 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.2582 | 0 | 0 |  |  |  |  | -0.2582 | 0 | 0.86528 | 0.87203
8457 | COSW#2 | 2 | South | YES | -0.001877 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.2582 | 0 | 0 |  |  |  |  | -0.2582 | 0 | 0.86528 | 0.87203
8459 | B_DAVIS0B | MB | South | YES | -0.001863 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.25819 | 0 | 0 |  |  |  |  | -0.25819 | 0 | 0.86528 | 0.87203
8460 | B_DAVIS0A | MB | South | YES | -0.001863 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.25819 | 0 | 0 |  |  |  |  | -0.25819 | 0 | 0.86528 | 0.87203
80263 | B_DAVIS31A | 3 | South | YES | -0.001863 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.25819 | 180 | 180 |  |  |  |  | -0.25819 | -46.4741 | 0.86949 | 0.87607
80264 | B_DAVIS41A | 4 | South | YES | -0.001863 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.25819 | 180 | 180 |  |  |  |  | -0.25819 | -46.4741 | 0.8737 | 0.8801
8506 | VAL #1 | 1 | South | YES | -0.001811 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 | 0.8737 | 0.8801
8507 | VAL #2 | 2 | South | YES | -0.001811 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 | 0.8737 | 0.8801
8511 | OXY_CC0A | 1 | South | YES | -0.001811 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 | 0.8737 | 0.8801
8461 | KOCH_UP0A | 1 | South | YES | -0.001777 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.2581 | 0 | 0 |  |  |  |  | -0.2581 | 0 | 0.8737 | 0.8801
80080 | GWINDT11A | 3 | South | YES | -0.001696 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 38 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80080 | GWINDT11A | 4 | South | YES | -0.001696 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 19 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80080 | GWINDT11A | 2 | South | YES | -0.001696 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 41 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80080 | GWINDT11A | 1 | South | YES | -0.001696 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 94 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80081 | GWINDT21A | 4 | South | YES | -0.001696 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 22 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80081 | GWINDT21A | 1 | South | YES | -0.001696 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 94 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80081 | GWINDT21A | 3 | South | YES | -0.001696 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 43 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80081 | GWINDT21A | 2 | South | YES | -0.001696 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 36 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80180 | PNSCALT11A | 2 | South | YES | -0.001696 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 50 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80180 | PNSCALT11A | 1 | South | YES | -0.001696 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 148 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80181 | PNSCALT21A | 2 | South | YES | -0.001696 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 50 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
80181 | PNSCALT21A | 1 | South | YES | -0.001696 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 55 |  |  |  |  | -0.25802 | 0 | 0.8737 | 0.8801
8517 | CELANEBI0A | 1 | South | YES | -0.001676 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.258 | 0 | 0 |  |  |  |  | -0.258 | 0 | 0.8737 | 0.8801
5932 | SI_RAY9 | 9 | South | YES | -0.001567 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.25789 | 38 | 38 |  |  |  |  | -0.25789 | -9.7999 | 0.87459 | 0.88095
5933 | SI_RAY6 | 6 | South | YES | -0.001567 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.25789 | 19.3 | 19.3 |  |  |  |  | -0.25789 | -4.9773 | 0.87504 | 0.88138
5935 | SI_RAY10 | 10 | South | YES | -0.001567 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.25789 | 47 | 47 |  |  |  |  | -0.25789 | -12.121 | 0.87614 | 0.88244
80003 | MILHWYS | F | South | YES | -0.001567 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.25789 | 0 | 0 |  |  |  |  | -0.25789 | 0 | 0.87614 | 0.88244
5401 | CALAVER_JKS1 | 1 | South | YES | -0.001502 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.25783 | 0 | 562 |  |  |  |  | -0.25783 | 0 | 0.87614 | 0.88244
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.001366 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.25769 | 155 | 155 |  |  |  |  | -0.25769 | -39.9423 | 0.87977 | 0.88591
5477 | BRA_AVR1_ST | 1 | South | YES | -0.001366 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.25769 | 174 | 174 |  |  |  |  | -0.25769 | -44.8384 | 0.88384 | 0.8898
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.001366 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.25769 | 155 | 155 |  |  |  |  | -0.25769 | -39.9423 | 0.88746 | 0.89327
8936 | MVGN#1 | 1 | South | YES | -0.00136 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.25769 | 216.6 | 216.6 |  |  |  |  | -0.25769 | -55.8148 | 0.89253 | 0.89811
8937 | MVGN#2 | 2 | South | YES | -0.00136 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.25769 | 216.7 | 216.7 |  |  |  |  | -0.25769 | -55.8406 | 0.8976 | 0.90296
8938 | MVGN#3 | 3 | South | YES | -0.00136 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.25769 | 250.9 | 250.9 |  |  |  |  | -0.25769 | -64.6535 | 0.90347 | 0.90858
8981 | HECN1 | 1 | South | YES | -0.001359 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.25769 | 144.8 | 144.8 |  |  |  |  | -0.25769 | -37.3128 | 0.90686 | 0.91182
8982 | HECN2 | 2 | South | YES | -0.001359 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.25769 | 144.1 | 144.1 |  |  |  |  | -0.25769 | -37.1324 | 0.91023 | 0.91504
8983 | HECN3 | 3 | South | YES | -0.001359 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.25769 | 171.9 | 171.9 |  |  |  |  | -0.25769 | -44.2961 | 0.91425 | 0.91889
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.001247 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.25757 | 61 | 61 |  |  |  |  | -0.25757 | -15.712 | 0.91568 | 0.92025
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.001247 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.25757 | 95 | 95 |  |  |  |  | -0.25757 | -24.4695 | 0.9179 | 0.92237
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.001247 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.25757 | 151 | 151 |  |  |  |  | -0.25757 | -38.8936 | 0.92143 | 0.92575
5903 | SANMIGUELGEN | 1 | South | YES | -0.001181 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.25751 | 0 | 396.3 |  |  |  |  | -0.25751 | 0 | 0.92143 | 0.92575
5111 | CALAVER_JTD1 | 1 | South | YES | -0.00095 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.25728 | 0 | 430 |  |  |  |  | -0.25728 | 0 | 0.92143 | 0.92575
5112 | CALAVER_JTD2 | 2 | South | YES | -0.00095 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.25728 | 0 | 430 |  |  |  |  | -0.25728 | 0 | 0.92143 | 0.92575
88198 | BEEVILLE | F | South | YES | -0.000901 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.25723 | 0 | 0 |  |  |  |  | -0.25723 | 0 | 0.92143 | 0.92575
8933 | FGNTS001 | 1 | South | YES | -0.000871 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.2572 | 146.5 | 146.5 |  |  |  |  | -0.2572 | -37.6794 | 0.92486 | 0.92902
8934 | FGNTS101 | 2 | South | YES | -0.000871 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.2572 | 147.9 | 147.9 |  |  |  |  | -0.2572 | -38.0395 | 0.92832 | 0.93233
8935 | FGNTS201 | 3 | South | YES | -0.000871 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.2572 | 173 | 173 |  |  |  |  | -0.2572 | -44.4951 | 0.93237 | 0.93619
5396 | CALAVER_OWS1 | 1 | South | YES | -0.000864 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.25719 | 418 | 418 |  |  |  |  | -0.25719 | -107.5055 | 0.94214 | 0.94552
5397 | CALAVER_OWS2 | 2 | South | YES | -0.000864 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.25719 | 400 | 400 |  |  |  |  | -0.25719 | -102.8761 | 0.9515 | 0.95446
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.000856 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.25718 | 215 | 215 |  |  |  |  | -0.25718 | -55.2942 | 0.95653 | 0.95926
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.000856 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.25718 | 216 | 216 |  |  |  |  | -0.25718 | -55.5514 | 0.96158 | 0.96408
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.000795 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 | 0.96158 | 0.96408
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.000795 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 | 0.96158 | 0.96408
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.000795 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 | 0.96158 | 0.96408
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.000719 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.25705 | 407 | 407 |  |  |  |  | -0.25705 | -104.6174 | 0.97111 | 0.97316
5264 | LEON_LCP3G3 | 3 | South | YES | -0.000265 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.25659 | 58 | 58 |  |  |  |  | -0.25659 | -14.8823 | 0.97246 | 0.97446
5265 | LEON_LCP4G4 | 4 | South | YES | -0.000265 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.25659 | 89 | 89 |  |  |  |  | -0.25659 | -22.8366 | 0.97454 | 0.97644
5266 | LEON_LCPCT1 | 1 | South | YES | -0.000265 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.25659 | 44 | 44 |  |  |  |  | -0.25659 | -11.29 | 0.97557 | 0.97742
5267 | LEON_LCPCT2 | 2 | South | YES | -0.000265 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.25659 | 44 | 44 |  |  |  |  | -0.25659 | -11.29 | 0.9766 | 0.9784
5268 | LEON_LCPCT3 | 3 | South | YES | -0.000265 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.25659 | 43 | 43 |  |  |  |  | -0.25659 | -11.0334 | 0.97761 | 0.97936
5269 | LEON_LCPCT4 | 4 | South | YES | -0.000265 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.25659 | 45 | 45 |  |  |  |  | -0.25659 | -11.5466 | 0.97866 | 0.98036
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.25633 | 15 | 15 |  |  |  |  | -0.25633 | -3.8449 | 0.97901 | 0.9807
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 | 0.97901 | 0.9807
88508 | FALFURRI | F | South | YES | 0.001585 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.25474 | 0 | 0 |  |  |  |  | -0.25474 | 0 | 0.97901 | 0.9807
5728 | FALCONHYDRO2 | 2 | South | YES | 0.002028 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 | 0.97901 | 0.9807
5729 | FALCONHYDRO3 | 3 | South | YES | 0.002028 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 | 0.97901 | 0.9807
8048 | FALCONHYDRO1 | 1 | South | YES | 0.002028 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 | 0.97901 | 0.9807
7028 | L_MARBFA1_1Y | 1 | South | YES | 0.004572 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.25175 | 0 | 0 |  |  |  |  | -0.25175 | 0 | 0.97901 | 0.9807
7029 | L_MARBFA1_2Y | 2 | South | YES | 0.004572 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.25175 | 0 | 0 |  |  |  |  | -0.25175 | 0 | 0.97901 | 0.9807
88299 | ZAPATA | F | South | YES | 0.004802 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.25152 | 0 | 0 |  |  |  |  | -0.25152 | 0 | 0.97901 | 0.9807
7035 | L_WIRTZ_1G1Y | 1 | South | YES | 0.006511 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.24982 | 0 | 0 |  |  |  |  | -0.24982 | 0 | 0.97901 | 0.9807
7036 | L_WIRTZ_1G2Y | 2 | South | YES | 0.006511 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.24982 | 0 | 0 |  |  |  |  | -0.24982 | 0 | 0.97901 | 0.9807
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.007137 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 | 0.97901 | 0.9807
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.007137 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 | 0.97901 | 0.9807
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.007137 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 | 0.97901 | 0.9807
7000 | L_FERGUS1_1Y | 1 | South | YES | 0.007166 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.24916 | 423.3 | 423.3 |  |  |  |  | -0.24916 | -105.4695 | 0.98892 | 0.98985
5890 | PEARSALLGEN1 | 1 | South | YES | 0.008293 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.24803 | 24 | 24 |  |  |  |  | -0.24803 | -5.9528 | 0.98948 | 0.99037
5891 | PEARSALLGEN2 | 1 | South | YES | 0.008293 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.24803 | 24.3 | 24.3 |  |  |  |  | -0.24803 | -6.0272 | 0.99005 | 0.99089
5892 | PEARSALLGEN3 | 1 | South | YES | 0.008293 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.24803 | 23.9 | 23.9 |  |  |  |  | -0.24803 | -5.928 | 0.9906 | 0.99141
80012 | LAR | F | South | YES | 0.008892 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.24743 | 0 | 0 |  |  |  |  | -0.24743 | 0 | 0.9906 | 0.99141
80265 | LARECU40A | 4 | South | YES | 0.008895 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.24743 | 100 | 100 |  |  |  |  | -0.24743 | -24.7431 | 0.99294 | 0.99356
80266 | LARECU50A | 5 | South | YES | 0.008895 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.24743 | 100 | 100 |  |  |  |  | -0.24743 | -24.7431 | 0.99528 | 0.9957
58909 | PEARSALLSCG1 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99548 | 0.99588
58909 | PEARSALLSCG1 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99568 | 0.99606
58909 | PEARSALLSCG1 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99587 | 0.99624
58909 | PEARSALLSCG1 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99607 | 0.99642
58909 | PEARSALLSCG1 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99627 | 0.9966
58909 | PEARSALLSCG1 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99646 | 0.99678
58919 | PEARSALLSCG2 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99666 | 0.99696
58919 | PEARSALLSCG2 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99686 | 0.99714
58919 | PEARSALLSCG2 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99705 | 0.99732
58919 | PEARSALLSCG2 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99725 | 0.99749
58919 | PEARSALLSCG2 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99745 | 0.99767
58919 | PEARSALLSCG2 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99764 | 0.99785
58929 | PEARSALLSCG3 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99784 | 0.99803
58929 | PEARSALLSCG3 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99803 | 0.99821
58929 | PEARSALLSCG3 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99823 | 0.99839
58929 | PEARSALLSCG3 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99843 | 0.99857
58929 | PEARSALLSCG3 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99862 | 0.99875
58929 | PEARSALLSCG3 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99882 | 0.99893
58949 | PEARSALLSCG4 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99902 | 0.99911
58949 | PEARSALLSCG4 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99921 | 0.99928
58949 | PEARSALLSCG4 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99941 | 0.99946
58949 | PEARSALLSCG4 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.99961 | 0.99964
58949 | PEARSALLSCG4 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 0.9998 | 0.99982
58949 | PEARSALLSCG4 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 | 1 | 1
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.011136 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.24519 | 0 | 0 |  |  |  |  | -0.24519 | 0 | 1 | 1
1643 | SLSTR1PP_1G | 1 | North | YES | 0.019601 | 6 | 0 | 60 | 0 | 1.022 | Wind | -1 | 0.23673 | 0 | 60 |  |  | 0 | 0 | -0.23673 | 0 | 1 | 1
8262 | ELPS | 1 | South | YES | 0.050982 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.20534 | 0 | 0 |  |  |  |  | -0.20534 | 0 | 1 | 1
8032 | AMISTADHYD1 | 1 | South | YES | 0.070288 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 | 1 | 1
8033 | AMISTADHYD2 | 2 | South | YES | 0.070288 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 | 1 | 1
88253 | HAMILTON | F | South | YES | 0.070288 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 | 1 | 1
1437 | MESQUITW_1G | 1 | North | YES | 0.23258 | 40 | 0 | 400 | 0 | 1.023 | Wind | -1 | 0.023741 | 0 | 400 |  |  | 0 | 0 | -0.023741 | 0 | 1 | 1
1438 | MESQUITW_2G | 1 | North | YES | 0.23272 | 23.6 | 0 | 236 |  | 1.017 | Wind | -1 | 0.023604 | 0 | 236 |  |  | 0 | 0 | -0.023604 | 0 | 1 | 1
1442 | COKFIELD_5 | 1 | North | YES | 0.23272 | 16.5 | 0 | 165 |  | 1.029 | Wind | -1 | 0.023604 | 0 | 165 |  |  | 0 | 0 | -0.023604 | 0 | 1 | 1
6100 | OKLA7A | EQ | West | YES | 0.065172 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.086243 | 0 | 0 | 0 | 0 |  |  | 0.086243 | 0
6752 | OKLA0A | 1 | West | YES | 0.065172 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.086243 | 0 | 649.7 | 42.3422 | 649.7 |  |  | 0.086243 | 56.0319
60081 | WHRLWIND1A | 1 | West | YES | 0.16067 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.18174 | 0 | 60 | 9.6403 | 60 |  |  | 0.18174 | 10.9046
6407 | TURKTRAK1A | 1 | West | YES | 0.17738 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.19846 | 0 | 169.5 | 30.0668 | 169.5 |  |  | 0.19846 | 33.6383
60057 | CALLAHAN1A | 1 | West | YES | 0.1794 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.20047 | 0 | 114 | 20.4511 | 114 |  |  | 0.20047 | 22.8532
6144 | MCADOO1A | 1 | West | YES | 0.20699 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.22806 | 0 | 150 | 31.0488 | 150 |  |  | 0.22806 | 34.2094
60058 | BUFF_GAP1A | 1 | West | YES | 0.20991 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.23098 | 0 | 120 | 25.189 | 120 |  |  | 0.23098 | 27.7175
60060 | CIRELLO | 1 | West | YES | 0.20991 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.23098 | 0 | 233 | 48.9086 | 233 |  |  | 0.23098 | 53.8181
60063 | BUFF_GAP1B | 1 | West | YES | 0.20991 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.23098 | 0 | 170.2 | 35.7263 | 170.2 |  |  | 0.23098 | 39.3126
60066 | H_HOLLOW1A | 1 | West | YES | 0.20991 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.23098 | 0 | 222 | 46.5996 | 222 |  |  | 0.23098 | 51.2773
60068 | HHOLLOW21A | 1 | West | YES | 0.20991 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 184 | 38.6231 | 184 |  |  | 0.23098 | 42.5001
60070 | HHOLLOW31A | 1 | West | YES | 0.20991 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 224 | 47.0194 | 224 |  |  | 0.23098 | 51.7393
60072 | HHOLLOW41A | 1 | West | YES | 0.20991 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 115 | 24.1394 | 115 |  |  | 0.23098 | 26.5626
60202 | FRNDDRCS | F | West | YES | 0.21035 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.23142 | 0 | 0 | 0 | 0 |  |  | 0.23142 | 0
1343 | TRENTIPP_8 | 1 | West | YES | 0.2173 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.23837 | 0 | 150 | 32.5951 | 150 |  |  | 0.23837 | 35.7558
1354 | AEPWIND_8 | 1 | West | YES | 0.2173 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.23837 | 0 | 101 | 21.9474 | 101 |  |  | 0.23837 | 24.0756
60000 | DSKY2 | 1 | West | YES | 0.24668 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.26775 | 0 | 76.5 | 18.8706 | 76.5 |  |  | 0.26775 | 20.4826
60018 | DSKY1 | 1 | West | YES | 0.24737 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.26844 | 0 | 84 | 20.7789 | 84 |  |  | 0.26844 | 22.5489
60017 | ORNNWP1 | 1 | West | YES | 0.24984 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.27091 | 0 | 80 | 19.987 | 80 |  |  | 0.27091 | 21.6726
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.25162 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.27269 | 0 | 112.5 | 28.3074 | 112.5 |  |  | 0.27269 | 30.6778
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.25162 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 149.5 | 37.6173 | 149.5 |  |  | 0.27269 | 40.7674
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.25162 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 186 | 46.8015 | 186 |  |  | 0.27269 | 50.7207
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.25162 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 214.5 | 53.9727 | 214.5 |  |  | 0.27269 | 58.4924
36998 | RDCNYNG1 | 1 | West | YES | 0.25225 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.27332 | 0 | 84 | 21.1888 | 84 |  |  | 0.27332 | 22.9588
71051 | L_BITTCR1_1N | W1 | West | YES | 0.25649 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 37.5 | 9.6182 | 37.5 |  |  | 0.27756 | 10.4084
71054 | L_SWEETW1_1N | W1 | West | YES | 0.25649 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 107.5 | 27.5722 | 107.5 |  |  | 0.27756 | 29.8374
71057 | L_SWEETW1_2N | W1 | West | YES | 0.25649 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 135 | 34.6256 | 135 |  |  | 0.27756 | 37.4702
71059 | L_SWEETW1_3N | W1 | West | YES | 0.25649 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 119 | 30.5218 | 119 |  |  | 0.27756 | 33.0293
71060 | L_SWEETW1_4N | W1 | West | YES | 0.25649 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 105 | 26.931 | 105 |  |  | 0.27756 | 29.1435
71061 | L_SWEETW1_5N | W1 | West | YES | 0.25649 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 80.5 | 20.6471 | 80.5 |  |  | 0.27756 | 22.3433
38437 | TNSRBNMESA9 | 1 | West | YES | 0.25715 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.27822 | 0 | 150 | 38.5729 | 150 |  |  | 0.27822 | 41.7336
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.25739 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.27846 | 0 | 80 | 20.5909 | 80 |  |  | 0.27846 | 22.2765
60016 | WOODWRD11A | 1 | West | YES | 0.25744 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.27851 | 0 | 80 | 20.5951 | 80 |  |  | 0.27851 | 22.2808
6016 | SWMESA | 1 | West | YES | 0.25764 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.27871 | 0 | 75 | 19.3228 | 75 |  |  | 0.27871 | 20.9031
60003 | KING_NE1A | 1 | West | YES | 0.25764 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27871 | 0 | 80 | 20.611 | 80 |  |  | 0.27871 | 22.2966
60005 | KING_SE1A | 1 | West | YES | 0.25764 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.27871 | 0 | 40 | 10.3055 | 40 |  |  | 0.27871 | 11.1483
60201 | RIO DRCS | F | West | YES | 0.25816 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.27923 | 0 | 0 | 0 | 0 |  |  | 0.27923 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | 0.25872 | 30 | 0 | 150 |  | 1.02 | Wind | 1 | 0.27979 | 0 | 150 | 38.8074 | 150 |  |  | 0.27979 | 41.968
60007 | KING_SW1A | 1 | West | YES | 0.25893 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28 | 0 | 80 | 20.7147 | 80 |  |  | 0.28 | 22.4004
60019 | KING_NW1A | 1 | West | YES | 0.25893 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28 | 0 | 80 | 20.7147 | 80 |  |  | 0.28 | 22.4004
1349 | WESTXWIN_1G | 1 | West | YES | 0.26137 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.28244 | 0 | 6.6 | 1.725 | 6.6 |  |  | 0.28244 | 1.8641
1350 | NWPWRG1_1G | 1 | West | YES | 0.26137 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.28244 | 0 | 34.3 | 8.9649 | 34.3 |  |  | 0.28244 | 9.6876
1061 | CIELOGEN_1G | 1 | West | YES | 0.26256 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.28364 | 0 | 99 | 25.9939 | 99 |  |  | 0.28364 | 28.0799
1062 | CIELOGEN_2G | 1 | West | YES | 0.26256 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.28364 | 0 | 61 | 16.0165 | 61 |  |  | 0.28364 | 17.3018
1069 | KINDERMG_1G | 1 | West | YES | 0.26256 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.26256 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.26256 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.26283 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.28391 | 0 | 141 | 37.0597 | 141 |  |  | 0.28391 | 40.0307
1073 | SCURRYCW_2G | 2 | West | YES | 0.26283 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.28391 | 0 | 120 | 31.5402 | 120 |  |  | 0.28391 | 34.0687
6637 | SNYDERW1A | 1 | West | YES | 0.26571 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.28678 | 0 | 63 | 16.7397 | 63 |  |  | 0.28678 | 18.0672
11309 | BULLCREK_2G | 1 | West | YES | 0.26996 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.29103 | 0 | 180 | 48.5919 | 180 |  |  | 0.29103 | 52.3846
11310 | BULLCREK_1G | 1 | West | YES | 0.26996 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.29103 | 0 | 180 | 48.5919 | 180 |  |  | 0.29103 | 52.3846
11320 | COYOTE_1G | 1 | West | YES | 0.2705 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.29157 | 0 | 225 | 60.8625 | 225 |  |  | 0.29157 | 65.6034
1416 | SWETWATR_1G | 1 | West | YES | 0.27072 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.29179 | 30 | 30 | 8.1217 | 30 |  |  | 0.29179 | 8.7538
1417 | SWETWATR_2G | 2 | West | YES | 0.27072 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.29179 | 72 | 72 | 19.492 | 72 |  |  | 0.29179 | 21.0091
1418 | SWETWATR_3G | 3 | West | YES | 0.27072 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.29179 | 68 | 68 | 18.4091 | 68 |  |  | 0.29179 | 19.8419
1419 | SWETWATR_4G | 4 | West | YES | 0.27072 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.29179 | 61 | 61 | 16.514 | 61 |  |  | 0.29179 | 17.7994
1320 | BSP 1 | 1 | West | YES | 0.27101 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.29208 | 0 | 0 | 0 | 0 |  |  | 0.29208 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | 0.27338 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.29445 | 0 | 120 | 32.806 | 120 |  |  | 0.29445 | 35.3345
1327 | WILDHRSE_1G | 1 | West | YES | 0.27488 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.29595 | 0 | 120 | 32.986 | 120 |  |  | 0.29595 | 35.5145
1333 | MCDDONAL_8 | 1 | West | YES | 0.27836 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.29943 | 0 | 214.2 | 59.6254 | 214.2 |  |  | 0.29943 | 64.1387
1328 | OCOTILLO_1G | 1 | West | YES | 0.27857 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.29964 | 0 | 58 | 16.1571 | 58 |  |  | 0.29964 | 17.3792
1037 | MORGAN5G_5G | 5 | West | YES | 0.28106 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.30213 | 137 | 137 | 38.5047 | 137 |  |  | 0.30213 | 41.3914
1039 | MRGNAG_1G | A | West | YES | 0.28106 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.30213 | 69 | 69 | 19.3929 | 69 |  |  | 0.30213 | 20.8467
1040 | MRGNBG_2G | B | West | YES | 0.28106 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.30213 | 71 | 71 | 19.955 | 71 |  |  | 0.30213 | 21.451
1041 | MRGNCG_3G | C | West | YES | 0.28106 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.30213 | 70 | 70 | 19.6739 | 70 |  |  | 0.30213 | 21.1489
1042 | MRGNDG_4G | D | West | YES | 0.28106 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.30213 | 68 | 68 | 19.1118 | 68 |  |  | 0.30213 | 20.5446
1043 | MRGNEG_5G | E | West | YES | 0.28106 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.30213 | 70 | 70 | 19.6739 | 70 |  |  | 0.30213 | 21.1489
1044 | MRGNFG_6G | F | West | YES | 0.28106 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.30213 | 66 | 66 | 18.5497 | 66 |  |  | 0.30213 | 19.9404
1326 | STANTONW_8 | 1 | West | YES | 0.28117 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.30224 | 0 | 100.5 | 28.2574 | 100.5 |  |  | 0.30224 | 30.375
11147 | NOTREES_1G | 1 | West | YES | 0.28221 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.30329 | 0 | 149 | 42.05 | 149 |  |  | 0.30329 | 45.1896
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.28257 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.30364 | 0 | 35 | 9.8898 | 35 |  |  | 0.30364 | 10.6273
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.28257 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.30364 | 0 | 30 | 8.477 | 30 |  |  | 0.30364 | 9.1091
1002 | PBCTAGE_1G | A | West | YES | 0.28269 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.30376 | 66 | 66 | 18.6577 | 66 |  |  | 0.30376 | 20.0483
1003 | PBCTBGE_2G | B | West | YES | 0.28269 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.30376 | 66 | 66 | 18.6577 | 66 |  |  | 0.30376 | 20.0483
1004 | PBCTCGE_3G | C | West | YES | 0.28269 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.30376 | 67 | 67 | 18.9404 | 67 |  |  | 0.30376 | 20.3521
1005 | PBCTDGE_4G | D | West | YES | 0.28269 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.30376 | 68 | 68 | 19.2231 | 68 |  |  | 0.30376 | 20.6559
1006 | PBCTEGE_5G | E | West | YES | 0.28269 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.30376 | 67 | 67 | 18.9404 | 67 |  |  | 0.30376 | 20.3521
1007 | PB5GEN_6G | 5 | West | YES | 0.28269 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.30376 | 114 | 114 | 32.2269 | 114 |  |  | 0.30376 | 34.629
1008 | PB6GEN_7G | 6 | West | YES | 0.28269 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.30376 | 515 | 515 | 145.5864 | 515 |  |  | 0.30376 | 156.4378
11020 | TIEHVSG_1G | 1 | West | YES | 0.28801 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.30908 | 208.2 | 208.2 | 59.9641 | 208.2 |  |  | 0.30908 | 64.351
11021 | TIEHVCG_1G | 1 | West | YES | 0.28801 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.30908 | 142.1 | 142.1 | 40.9265 | 142.1 |  |  | 0.30908 | 43.9207
11022 | TIEHVCG_2G | 1 | West | YES | 0.28801 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.30908 | 132.4 | 132.4 | 38.1328 | 132.4 |  |  | 0.30908 | 40.9226
11023 | TIEHVCG_3G | 1 | West | YES | 0.28801 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.30908 | 137.4 | 137.4 | 39.5728 | 137.4 |  |  | 0.30908 | 42.468
11024 | TIEHVCG_4G | 1 | West | YES | 0.28801 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.30908 | 147 | 147 | 42.3378 | 147 |  |  | 0.30908 | 45.4352
11025 | TIEHVSG_2G | 1 | West | YES | 0.28801 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.30908 | 213.2 | 213.2 | 61.4042 | 213.2 |  |  | 0.30908 | 65.8965
11001 | NAV1CT | 1 | West | YES | 0.28807 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.30914 | 70.4 | 70.4 | 20.2803 | 70.4 |  |  | 0.30914 | 21.7637
11009 | NAV2CT | 1 | West | YES | 0.28807 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.30914 | 71.4 | 71.4 | 20.5684 | 71.4 |  |  | 0.30914 | 22.0729
11011 | NAV3ST | 1 | West | YES | 0.28807 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.30914 | 92.8 | 92.8 | 26.7332 | 92.8 |  |  | 0.30914 | 28.6885
11012 | NAV4CT | 1 | West | YES | 0.28807 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30914 | 80 | 80 | 23.0458 | 80 |  |  | 0.30914 | 24.7315
11013 | NAV5CT | 1 | West | YES | 0.28807 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30914 | 80 | 80 | 23.0458 | 80 |  |  | 0.30914 | 24.7315
11014 | NAV6ST | 1 | West | YES | 0.28807 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.30914 | 115 | 115 | 33.1284 | 115 |  |  | 0.30914 | 35.5515
1045 | CALENG1G_1G | 1 | West | YES | 0.29237 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.29237 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.29237 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0
1058 | LONGSHORE_5 | 1 | West | YES | 0.29363 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.3147 | 0 | 150 | 44.0444 | 150 |  |  | 0.3147 | 47.205
1058 | LONGSHORE_5 | 2 | West | YES | 0.29363 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.3147 | 0 | 220 | 64.5984 | 220 |  |  | 0.3147 | 69.234
11065 | ELBOWCK_1G | 1 | West | YES | 0.29363 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.3147 | 0 | 121.9 | 35.7934 | 121.9 |  |  | 0.3147 | 38.3619
11056 | ROSCOE_1G | 1 | West | YES | 0.37703 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.3981 | 0 | 209 | 78.7989 | 209 |  |  | 0.3981 | 83.2026
11057 | CHAMPION_1G | 1 | West | YES | 0.37703 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.3981 | 0 | 126.5 | 47.694 | 126.5 |  |  | 0.3981 | 50.3595
11058 | PYRON_1G | 1 | West | YES | 0.37703 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.3981 | 0 | 249 | 93.88 | 249 |  |  | 0.3981 | 99.1266
11059 | INADALE_1G | 1 | West | YES | 0.37703 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.3981 | 0 | 197 | 74.2745 | 197 |  |  | 0.3981 | 78.4255
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Bound Gen
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | max of zone correlation | 0.023604 |  |  | Neg PTDF weight | Pos PTDF weight
1438 | MESQUITW_2G | 1 | North | YES | 0.23272 | 23.6 | 0 | 236 |  | 1.017 | Wind | -1 | 0.023604 | 0 | 236 |  |  | 0 | 0 | -0.023604 | 0 |  |  |  |  | 0 | 0
1442 | COKFIELD_5 | 1 | North | YES | 0.23272 | 16.5 | 0 | 165 |  | 1.029 | Wind | -1 | 0.023604 | 0 | 165 |  |  | 0 | 0 | -0.023604 | 0 |  |  |  |  | 0 | 0
1437 | MESQUITW_1G | 1 | North | YES | 0.23258 | 40 | 0 | 400 | 0 | 1.023 | Wind | -1 | 0.023741 | 0 | 400 |  |  | 0 | 0 | -0.023741 | 0 |  |  |  |  | 0 | 0
6100 | OKLA7A | EQ | West | YES | 0.065172 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.086243 | 0 | 0 | 0 | 0 |  |  | 0.086243 | 0 |  |  | Weighted Shift Factors |  | 0 | 0
6752 | OKLA0A | 1 | West | YES | 0.065172 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.086243 | 0 | 649.7 | 42.3422 | 649.7 |  |  | 0.086243 | 56.0319 |  |  | West | 0.25633 | 0 | 0
60081 | WHRLWIND1A | 1 | West | YES | 0.16067 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.18174 | 0 | 60 | 9.6403 | 60 |  |  | 0.18174 | 10.9046 |  |  | North | -0.021071 | 0 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.070288 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 |  |  |  |  | 0 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.070288 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 | North |  |  |  | 0 | 0
88253 | HAMILTON | F | South | YES | 0.070288 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.18604 | 0 | 0 |  |  |  |  | -0.18604 | 0 | Line Rating |  | 1072 |  | 0 | 0
6407 | TURKTRAK1A | 1 | West | YES | 0.17738 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.19846 | 0 | 169.5 | 30.0668 | 169.5 |  |  | 0.19846 | 33.6383 | Impact Counter to Zone: |  | 0 |  | 0 | 0
60057 | CALLAHAN1A | 1 | West | YES | 0.1794 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.20047 | 0 | 114 | 20.4511 | 114 |  |  | 0.20047 | 22.8532 |  |  | 0% |  | 0 | 0
8262 | ELPS | 1 | South | YES | 0.050982 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.20534 | 0 | 0 |  |  |  |  | -0.20534 | 0 |  |  |  |  | 0 | 0
6144 | MCADOO1A | 1 | West | YES | 0.20699 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.22806 | 0 | 150 | 31.0488 | 150 |  |  | 0.22806 | 34.2094 | West |  |  |  | 0 | 0
60072 | HHOLLOW41A | 1 | West | YES | 0.20991 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 115 | 24.1394 | 115 |  |  | 0.23098 | 26.5626 | Line Rating |  | 1072 |  | 0 | 0
60058 | BUFF_GAP1A | 1 | West | YES | 0.20991 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.23098 | 0 | 120 | 25.189 | 120 |  |  | 0.23098 | 27.7175 | Impact Counter to Zone: |  | 0 |  | 0 | 0
60063 | BUFF_GAP1B | 1 | West | YES | 0.20991 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.23098 | 0 | 170.2 | 35.7263 | 170.2 |  |  | 0.23098 | 39.3126 |  |  | 0% |  | 0 | 0
60068 | HHOLLOW21A | 1 | West | YES | 0.20991 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 184 | 38.6231 | 184 |  |  | 0.23098 | 42.5001 |  |  |  |  | 0 | 0
60066 | H_HOLLOW1A | 1 | West | YES | 0.20991 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.23098 | 0 | 222 | 46.5996 | 222 |  |  | 0.23098 | 51.2773 |  |  |  |  | 0 | 0
60070 | HHOLLOW31A | 1 | West | YES | 0.20991 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.23098 | 0 | 224 | 47.0194 | 224 |  |  | 0.23098 | 51.7393 |  |  |  |  | 0 | 0
60060 | CIRELLO | 1 | West | YES | 0.20991 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.23098 | 0 | 233 | 48.9086 | 233 |  |  | 0.23098 | 53.8181 |  |  |  |  | 0 | 0
60202 | FRNDDRCS | F | West | YES | 0.21035 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.23142 | 0 | 0 | 0 | 0 |  |  | 0.23142 | 0 |  |  |  |  | 0 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.019601 | 6 | 0 | 60 | 0 | 1.022 | Wind | -1 | 0.23673 | 0 | 60 |  |  | 0 | 0 | -0.23673 | 0 |  |  |  |  | 0 | 0
1354 | AEPWIND_8 | 1 | West | YES | 0.2173 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.23837 | 0 | 101 | 21.9474 | 101 |  |  | 0.23837 | 24.0756 |  |  |  |  | 0 | 0
1343 | TRENTIPP_8 | 1 | West | YES | 0.2173 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.23837 | 0 | 150 | 32.5951 | 150 |  |  | 0.23837 | 35.7558 |  |  |  |  | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.011136 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.24519 | 0 | 0 |  |  |  |  | -0.24519 | 0 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58919 | PEARSALLSCG2 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58929 | PEARSALLSCG3 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 3 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 2 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 1 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 4 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 6 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
58949 | PEARSALLSCG4 | 5 | South | YES | 0.010937 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | 0.24539 | 8.4 | 8.4 |  |  |  |  | -0.24539 | -2.0613 |  |  |  |  | 0 | 0
80265 | LARECU40A | 4 | South | YES | 0.008895 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.24743 | 100 | 100 |  |  |  |  | -0.24743 | -24.7431 |  |  |  |  | 0 | 0
80266 | LARECU50A | 5 | South | YES | 0.008895 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.24743 | 100 | 100 |  |  |  |  | -0.24743 | -24.7431 |  |  |  |  | 0 | 0
80012 | LAR | F | South | YES | 0.008892 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.24743 | 0 | 0 |  |  |  |  | -0.24743 | 0 |  |  |  |  | 0 | 0
5891 | PEARSALLGEN2 | 1 | South | YES | 0.008293 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | 0.24803 | 24.3 | 24.3 |  |  |  |  | -0.24803 | -6.0272 |  |  |  |  | 0 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | 0.008293 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | 0.24803 | 24 | 24 |  |  |  |  | -0.24803 | -5.9528 |  |  |  |  | 0 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | 0.008293 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | 0.24803 | 23.9 | 23.9 |  |  |  |  | -0.24803 | -5.928 |  |  |  |  | 0 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | 0.007166 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.24916 | 423.3 | 423.3 |  |  |  |  | -0.24916 | -105.4695 |  |  |  |  | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.007137 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 |  |  |  |  | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.007137 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 |  |  |  |  | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.007137 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.24919 | 0 | 0 |  |  |  |  | -0.24919 | 0 |  |  |  |  | 0 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | 0.006511 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.24982 | 0 | 0 |  |  |  |  | -0.24982 | 0 |  |  |  |  | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | 0.006511 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | 0.24982 | 0 | 0 |  |  |  |  | -0.24982 | 0 |  |  |  |  | 0 | 0
88299 | ZAPATA | F | South | YES | 0.004802 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.25152 | 0 | 0 |  |  |  |  | -0.25152 | 0 |  |  |  |  | 0 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | 0.004572 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.25175 | 0 | 0 |  |  |  |  | -0.25175 | 0 |  |  |  |  | 0 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | 0.004572 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.25175 | 0 | 0 |  |  |  |  | -0.25175 | 0 |  |  |  |  | 0 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | 0.002028 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 |  |  |  |  | 0 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 0.002028 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 |  |  |  |  | 0 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 0.002028 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | 0.2543 | 0 | 0 |  |  |  |  | -0.2543 | 0 |  |  |  |  | 0 | 0
88508 | FALFURRI | F | South | YES | 0.001585 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.25474 | 0 | 0 |  |  |  |  | -0.25474 | 0 |  |  |  |  | 0 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.25633 | 15 | 15 |  |  |  |  | -0.25633 | -3.8449 |  |  |  |  | 0 | 0
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.25633 | 0 | 0 |  |  |  |  | -0.25633 | 0 |  |  |  |  | 0 | 0
5265 | LEON_LCP4G4 | 4 | South | YES | -0.000265 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.25659 | 89 | 89 |  |  |  |  | -0.25659 | -22.8366 |  |  |  |  | 0 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.000265 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.25659 | 58 | 58 |  |  |  |  | -0.25659 | -14.8823 |  |  |  |  | 0 | 0
5269 | LEON_LCPCT4 | 4 | South | YES | -0.000265 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.25659 | 45 | 45 |  |  |  |  | -0.25659 | -11.5466 |  |  |  |  | 0 | 0
5266 | LEON_LCPCT1 | 1 | South | YES | -0.000265 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.25659 | 44 | 44 |  |  |  |  | -0.25659 | -11.29 |  |  |  |  | 0 | 0
5267 | LEON_LCPCT2 | 2 | South | YES | -0.000265 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.25659 | 44 | 44 |  |  |  |  | -0.25659 | -11.29 |  |  |  |  | 0 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | -0.000265 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.25659 | 43 | 43 |  |  |  |  | -0.25659 | -11.0334 |  |  |  |  | 0 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.000719 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.25705 | 407 | 407 |  |  |  |  | -0.25705 | -104.6174 |  |  |  |  | 0 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.000795 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 |  |  |  |  | 0 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.000795 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 |  |  |  |  | 0 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.000795 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.25712 | 0 | 0 |  |  |  |  | -0.25712 | 0 |  |  |  |  | 0 | 0
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.000856 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.25718 | 216 | 216 |  |  |  |  | -0.25718 | -55.5514 |  |  |  |  | 0 | 0
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.000856 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.25718 | 215 | 215 |  |  |  |  | -0.25718 | -55.2942 |  |  |  |  | 0 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.000864 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.25719 | 418 | 418 |  |  |  |  | -0.25719 | -107.5055 |  |  |  |  | 0 | 0
5397 | CALAVER_OWS2 | 2 | South | YES | -0.000864 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.25719 | 400 | 400 |  |  |  |  | -0.25719 | -102.8761 |  |  |  |  | 0 | 0
8935 | FGNTS201 | 3 | South | YES | -0.000871 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.2572 | 173 | 173 |  |  |  |  | -0.2572 | -44.4951 |  |  |  |  | 0 | 0
8934 | FGNTS101 | 2 | South | YES | -0.000871 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.2572 | 147.9 | 147.9 |  |  |  |  | -0.2572 | -38.0395 |  |  |  |  | 0 | 0
8933 | FGNTS001 | 1 | South | YES | -0.000871 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.2572 | 146.5 | 146.5 |  |  |  |  | -0.2572 | -37.6794 |  |  |  |  | 0 | 0
88198 | BEEVILLE | F | South | YES | -0.000901 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.25723 | 0 | 0 |  |  |  |  | -0.25723 | 0 |  |  |  |  | 0 | 0
5111 | CALAVER_JTD1 | 1 | South | YES | -0.00095 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.25728 | 0 | 430 |  |  |  |  | -0.25728 | 0 |  |  |  |  | 0 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.00095 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.25728 | 0 | 430 |  |  |  |  | -0.25728 | 0 |  |  |  |  | 0 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.001181 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | 0.25751 | 0 | 396.3 |  |  |  |  | -0.25751 | 0 |  |  |  |  | 0 | 0
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.001247 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.25757 | 151 | 151 |  |  |  |  | -0.25757 | -38.8936 |  |  |  |  | 0 | 0
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.001247 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.25757 | 95 | 95 |  |  |  |  | -0.25757 | -24.4695 |  |  |  |  | 0 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.001247 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.25757 | 61 | 61 |  |  |  |  | -0.25757 | -15.712 |  |  |  |  | 0 | 0
8983 | HECN3 | 3 | South | YES | -0.001359 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.25769 | 171.9 | 171.9 |  |  |  |  | -0.25769 | -44.2961 |  |  |  |  | 0 | 0
8981 | HECN1 | 1 | South | YES | -0.001359 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.25769 | 144.8 | 144.8 |  |  |  |  | -0.25769 | -37.3128 |  |  |  |  | 0 | 0
8982 | HECN2 | 2 | South | YES | -0.001359 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.25769 | 144.1 | 144.1 |  |  |  |  | -0.25769 | -37.1324 |  |  |  |  | 0 | 0
8938 | MVGN#3 | 3 | South | YES | -0.00136 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.25769 | 250.9 | 250.9 |  |  |  |  | -0.25769 | -64.6535 |  |  |  |  | 0 | 0
8937 | MVGN#2 | 2 | South | YES | -0.00136 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.25769 | 216.7 | 216.7 |  |  |  |  | -0.25769 | -55.8406 |  |  |  |  | 0 | 0
8936 | MVGN#1 | 1 | South | YES | -0.00136 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.25769 | 216.6 | 216.6 |  |  |  |  | -0.25769 | -55.8148 |  |  |  |  | 0 | 0
5477 | BRA_AVR1_ST | 1 | South | YES | -0.001366 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | 0.25769 | 174 | 174 |  |  |  |  | -0.25769 | -44.8384 |  |  |  |  | 0 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.001366 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.25769 | 155 | 155 |  |  |  |  | -0.25769 | -39.9423 |  |  |  |  | 0 | 0
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.001366 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | 0.25769 | 155 | 155 |  |  |  |  | -0.25769 | -39.9423 |  |  |  |  | 0 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.001502 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | 0.25783 | 0 | 562 |  |  |  |  | -0.25783 | 0 |  |  |  |  | 0 | 0
5935 | SI_RAY10 | 10 | South | YES | -0.001567 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.25789 | 47 | 47 |  |  |  |  | -0.25789 | -12.121 |  |  |  |  | 0 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.001567 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.25789 | 38 | 38 |  |  |  |  | -0.25789 | -9.7999 |  |  |  |  | 0 | 0
5933 | SI_RAY6 | 6 | South | YES | -0.001567 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.25789 | 19.3 | 19.3 |  |  |  |  | -0.25789 | -4.9773 |  |  |  |  | 0 | 0
80003 | MILHWYS | F | South | YES | -0.001567 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.25789 | 0 | 0 |  |  |  |  | -0.25789 | 0 |  |  |  |  | 0 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.001676 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.258 | 0 | 0 |  |  |  |  | -0.258 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 3 | South | YES | -0.001696 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 38 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 4 | South | YES | -0.001696 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 19 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 2 | South | YES | -0.001696 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 41 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 1 | South | YES | -0.001696 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 94 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 4 | South | YES | -0.001696 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 22 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 1 | South | YES | -0.001696 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 94 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 3 | South | YES | -0.001696 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 43 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 2 | South | YES | -0.001696 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 36 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.001696 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 50 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.001696 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 148 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.001696 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 50 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.001696 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.25802 | 0 | 55 |  |  |  |  | -0.25802 | 0 |  |  |  |  | 0 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.001777 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.2581 | 0 | 0 |  |  |  |  | -0.2581 | 0 |  |  |  |  | 0 | 0
8506 | VAL #1 | 1 | South | YES | -0.001811 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 |  |  |  |  | 0 | 0
8507 | VAL #2 | 2 | South | YES | -0.001811 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 |  |  |  |  | 0 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.001811 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | 0.25814 | 0 | 0 |  |  |  |  | -0.25814 | 0 |  |  |  |  | 0 | 0
80263 | B_DAVIS31A | 3 | South | YES | -0.001863 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.25819 | 180 | 180 |  |  |  |  | -0.25819 | -46.4741 |  |  |  |  | 0 | 0
80264 | B_DAVIS41A | 4 | South | YES | -0.001863 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | 0.25819 | 180 | 180 |  |  |  |  | -0.25819 | -46.4741 |  |  |  |  | 0 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.001863 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.25819 | 0 | 0 |  |  |  |  | -0.25819 | 0 |  |  |  |  | 0 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.001863 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.25819 | 0 | 0 |  |  |  |  | -0.25819 | 0 |  |  |  |  | 0 | 0
8456 | COSW#1 | 1 | South | YES | -0.001877 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.2582 | 0 | 0 |  |  |  |  | -0.2582 | 0 |  |  |  |  | 0 | 0
8457 | COSW#2 | 2 | South | YES | -0.001877 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.2582 | 0 | 0 |  |  |  |  | -0.2582 | 0 |  |  |  |  | 0 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.001889 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 |  |  |  |  | 0 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.001889 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 |  |  |  |  | 0 | 0
8562 | CNOPST1 | 3 | South | YES | -0.001889 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | 7 | South | YES | -0.001892 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.25822 | 367 | 367 |  |  |  |  | -0.25822 | -94.7661 |  |  |  |  | 0 | 0
8442 | NBEC7 | MB | South | YES | -0.001892 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | 0.25822 | 0 | 0 |  |  |  |  | -0.25822 | 0 |  |  |  |  | 0 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.001991 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.25832 | 0 | 0 |  |  |  |  | -0.25832 | 0 |  |  |  |  | 0 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.002067 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.25839 | 0 | 0 |  |  |  |  | -0.25839 | 0 |  |  |  |  | 0 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.002126 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 |  |  |  |  | 0 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.002126 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 |  |  |  |  | 0 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.002126 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 |  |  |  |  | 0 | 0
8930 | ICPGN10A | 1 | South | YES | -0.002126 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 |  |  |  |  | 0 | 0
8931 | ICPGN20A | 2 | South | YES | -0.002126 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 |  |  |  |  | 0 | 0
8932 | ICPGN30A | 3 | South | YES | -0.002126 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 |  |  |  |  | 0 | 0
80223 | REYSHR G | 1 | South | YES | -0.002126 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.25845 | 0 | 0 |  |  |  |  | -0.25845 | 0 |  |  |  |  | 0 | 0
8161 | COLETO0A | 1 | South | YES | -0.002182 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.25851 | 0 | 633 |  |  |  |  | -0.25851 | 0 |  |  |  |  | 0 | 0
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.002314 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.25864 | 203 | 203 |  |  |  |  | -0.25864 | -52.504 |  |  |  |  | 0 | 0
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.002314 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.25864 | 182 | 182 |  |  |  |  | -0.25864 | -47.0725 |  |  |  |  | 0 | 0
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.002314 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.25864 | 149 | 149 |  |  |  |  | -0.25864 | -38.5374 |  |  |  |  | 0 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.002314 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.25864 | 147 | 147 |  |  |  |  | -0.25864 | -38.0201 |  |  |  |  | 0 | 0
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.002314 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.25864 | 146 | 146 |  |  |  |  | -0.25864 | -37.7615 |  |  |  |  | 0 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.002314 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.25864 | 138 | 138 |  |  |  |  | -0.25864 | -35.6923 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.0024 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.0024 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.0024 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.25873 | 0 | 0 |  |  |  |  | -0.25873 | 0 |  |  |  |  | 0 | 0
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.002549 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.25888 | 293 | 293 |  |  |  |  | -0.25888 | -75.8504 |  |  |  |  | 0 | 0
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.002549 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.25888 | 154 | 154 |  |  |  |  | -0.25888 | -39.8668 |  |  |  |  | 0 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.002549 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.25888 | 148 | 148 |  |  |  |  | -0.25888 | -38.3135 |  |  |  |  | 0 | 0
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.002549 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.25888 | 148 | 148 |  |  |  |  | -0.25888 | -38.3135 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.002697 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.25902 | 0 | 0 |  |  |  |  | -0.25902 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.002697 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.25902 | 0 | 0 |  |  |  |  | -0.25902 | 0 |  |  |  |  | 0 | 0
8189 | CUECPL2A | 1 | South | YES | -0.00272 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.25905 | 0 | 0 |  |  |  |  | -0.25905 | 0 |  |  |  |  | 0 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.002752 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | 0.25908 | 22 | 22 |  |  |  |  | -0.25908 | -5.6997 |  |  |  |  | 0 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | -0.002752 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.25908 | 11 | 11 |  |  |  |  | -0.25908 | -2.8499 |  |  |  |  | 0 | 0
5506 | RAYBURNGEN2 | 1 | South | YES | -0.002752 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.25908 | 11 | 11 |  |  |  |  | -0.25908 | -2.8499 |  |  |  |  | 0 | 0
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.00278 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.25911 | 226.7 | 226.7 |  |  |  |  | -0.25911 | -58.7394 |  |  |  |  | 0 | 0
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.00278 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.25911 | 225 | 225 |  |  |  |  | -0.25911 | -58.2989 |  |  |  |  | 0 | 0
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.00278 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.25911 | 224.6 | 224.6 |  |  |  |  | -0.25911 | -58.1953 |  |  |  |  | 0 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.00278 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.25911 | 223.9 | 223.9 |  |  |  |  | -0.25911 | -58.0139 |  |  |  |  | 0 | 0
5512 | RAYBURNCC8 | 1 | South | YES | -0.002955 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.25928 | 49.3 | 49.3 |  |  |  |  | -0.25928 | -12.7826 |  |  |  |  | 0 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.002955 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.25928 | 47.7 | 47.7 |  |  |  |  | -0.25928 | -12.3677 |  |  |  |  | 0 | 0
5511 | RAYBURNCC7 | 1 | South | YES | -0.002955 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.25928 | 47.5 | 47.5 |  |  |  |  | -0.25928 | -12.3159 |  |  |  |  | 0 | 0
5509 | RAYBURNCC10 | 1 | South | YES | -0.002955 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.25928 | 37.3 | 37.3 |  |  |  |  | -0.25928 | -9.6712 |  |  |  |  | 0 | 0
8174 | VICEC61A | 6 | South | YES | -0.002999 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.25933 | 188 | 188 |  |  |  |  | -0.25933 | -48.7531 |  |  |  |  | 0 | 0
8173 | VICEC51A | 5 | South | YES | -0.002999 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.25933 | 144 | 144 |  |  |  |  | -0.25933 | -37.3428 |  |  |  |  | 0 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.003094 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.25942 | 0 | 0 |  |  |  |  | -0.25942 | 0 |  |  |  |  | 0 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.00321 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.25954 | 0 | 0 |  |  |  |  | -0.25954 | 0 |  |  |  |  | 0 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.00321 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.25954 | 0 | 0 |  |  |  |  | -0.25954 | 0 |  |  |  |  | 0 | 0
80227 | AIRCO G | 1 | South | YES | -0.003228 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.25955 | 0 | 0 |  |  |  |  | -0.25955 | 0 |  |  |  |  | 0 | 0
8147 | UCAR #2 | 10 | South | YES | -0.003309 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 |  |  |  |  | 0 | 0
8148 | UCAR #1 | 2 | South | YES | -0.003309 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 9 | South | YES | -0.003309 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 8 | South | YES | -0.003309 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 |  |  |  |  | 0 | 0
80138 | CSDR7 | 7 | South | YES | -0.003309 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 6 | South | YES | -0.003309 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 5 | South | YES | -0.003309 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 |  |  |  |  | 0 | 0
80140 | CSDR11 | 11 | South | YES | -0.003309 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.25964 | 0 | 0 |  |  |  |  | -0.25964 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.00335 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.25968 | 0 | 0 |  |  |  |  | -0.25968 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.00335 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.25968 | 0 | 0 |  |  |  |  | -0.25968 | 0 |  |  |  |  | 0 | 0
9020 | SANDHG5A | 5A | South | YES | -0.003618 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.25994 | 155 | 155 |  |  |  |  | -0.25994 | -40.2914 |  |  |  |  | 0 | 0
9021 | SANDHG5C | 5C | South | YES | -0.003618 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.25994 | 148 | 148 |  |  |  |  | -0.25994 | -38.4717 |  |  |  |  | 0 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.003618 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.25994 | 49 | 49 |  |  |  |  | -0.25994 | -12.7373 |  |  |  |  | 0 | 0
9019 | SANDH_G4 | 4 | South | YES | -0.003618 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.25994 | 47 | 47 |  |  |  |  | -0.25994 | -12.2174 |  |  |  |  | 0 | 0
9017 | SANDH_G2 | 2 | South | YES | -0.003618 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.25994 | 46 | 46 |  |  |  |  | -0.25994 | -11.9574 |  |  |  |  | 0 | 0
9018 | SANDH_G3 | 3 | South | YES | -0.003618 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.25994 | 46 | 46 |  |  |  |  | -0.25994 | -11.9574 |  |  |  |  | 0 | 0
9001 | DECKR_G2 | 2 | South | YES | -0.003627 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.25995 | 426 | 426 |  |  |  |  | -0.25995 | -110.7401 |  |  |  |  | 0 | 0
9000 | DECKR_G1 | 1 | South | YES | -0.003627 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.25995 | 321 | 321 |  |  |  |  | -0.25995 | -83.445 |  |  |  |  | 0 | 0
80226 | ALCOA G | 1 | South | YES | -0.003687 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.26001 | 0 | 0 |  |  |  |  | -0.26001 | 0 |  |  |  |  | 0 | 0
8134 | FOR #1 | 1 | South | YES | -0.003787 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
8138 | FOR #2 | 2 | South | YES | -0.003787 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
8153 | FOR #3 | 3 | South | YES | -0.003787 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
8154 | FOR #4 | 4 | South | YES | -0.003787 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
8155 | FOR #5 | 5 | South | YES | -0.003787 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
8156 | FOR #6 | 6 | South | YES | -0.003787 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
8157 | FOR #7 | 7 | South | YES | -0.003787 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
80051 | FOR #8 | 8 | South | YES | -0.003787 | 28 | 28 | 28 |  | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
80052 | FOR #9 | 9 | South | YES | -0.003787 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
80053 | FOR #10 | 10 | South | YES | -0.003787 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | 0.26011 | 0 | 0 |  |  |  |  | -0.26011 | 0 |  |  |  |  | 0 | 0
9005 | DECKR_G6 | 6 | South | YES | -0.003822 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.26015 | 47 | 47 |  |  |  |  | -0.26015 | -12.227 |  |  |  |  | 0 | 0
9003 | DECKR_G4 | 4 | South | YES | -0.003822 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.26015 | 44 | 44 |  |  |  |  | -0.26015 | -11.4465 |  |  |  |  | 0 | 0
9004 | DECKR_G5 | 5 | South | YES | -0.003822 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.26015 | 44 | 44 |  |  |  |  | -0.26015 | -11.4465 |  |  |  |  | 0 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.003822 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.26015 | 42 | 42 |  |  |  |  | -0.26015 | -10.9262 |  |  |  |  | 0 | 0
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.004292 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.26062 | 329 | 329 |  |  |  |  | -0.26062 | -85.7434 |  |  |  |  | 0 | 0
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.004292 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.26062 | 139 | 139 |  |  |  |  | -0.26062 | -36.2259 |  |  |  |  | 0 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.004292 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.26062 | 132 | 132 |  |  |  |  | -0.26062 | -34.4016 |  |  |  |  | 0 | 0
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.004759 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.26109 | 232.6 | 232.6 |  |  |  |  | -0.26109 | -60.7284 |  |  |  |  | 0 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.004759 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.26109 | 152.5 | 152.5 |  |  |  |  | -0.26109 | -39.8155 |  |  |  |  | 0 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.004759 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.26109 | 149.5 | 149.5 |  |  |  |  | -0.26109 | -39.0322 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 |  |  |  |  | 0 | 0
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.004827 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.26115 | 50 | 50 |  |  |  |  | -0.26115 | -13.0577 |  |  |  |  | 0 | 0
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.005252 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.26158 | 175 | 175 |  |  |  |  | -0.26158 | -45.7762 |  |  |  |  | 0 | 0
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.005252 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.26158 | 160 | 160 |  |  |  |  | -0.26158 | -41.8525 |  |  |  |  | 0 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.005252 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.26158 | 158 | 158 |  |  |  |  | -0.26158 | -41.3294 |  |  |  |  | 0 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.005273 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 436 |  |  |  |  | -0.2616 | 0 |  |  |  |  | 0 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.005275 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 606 |  |  |  |  | -0.2616 | 0 |  |  |  |  | 0 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.005275 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.2616 | 0 | 598 |  |  |  |  | -0.2616 | 0 |  |  |  |  | 0 | 0
3432 | SANDOW_4G | 4 | South | YES | -0.006951 | 580 | 225 | 580 |  | 1.029 | LIGCO | -1 | 0.26328 | 0 | 580 |  |  |  |  | -0.26328 | 0 |  |  |  |  | 0 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.007142 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.26347 | 0 | 0 |  |  |  |  | -0.26347 | 0 |  |  |  |  | 0 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.007142 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.26347 | 0 | 0 |  |  |  |  | -0.26347 | 0 |  |  |  |  | 0 | 0
48733 | CBE_ST12 | 1 | Houston | YES | -0.007274 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.2636 | 105 | 105 |  |  |  |  | -0.2636 | -27.678 |  |  |  |  | 0 | 0
48736 | CBE_ST34 | 1 | Houston | YES | -0.007274 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.2636 | 105 | 105 |  |  |  |  | -0.2636 | -27.678 |  |  |  |  | 0 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 |  |  |  |  | 0 | 0
48732 | CBE_GT2 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 |  |  |  |  | 0 | 0
48734 | CBE_GT3 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 |  |  |  |  | 0 | 0
48735 | CBE_GT4 | 1 | Houston | YES | -0.007274 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.2636 | 76 | 76 |  |  |  |  | -0.2636 | -20.0336 |  |  |  |  | 0 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.007407 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.26373 | 0 | 0 |  |  |  |  | -0.26373 | 0 |  |  |  |  | 0 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.008243 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.008243 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.008243 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.008243 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.008243 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.008243 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.008243 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.008243 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.008243 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.008243 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.008243 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.008243 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.008243 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.008243 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.008243 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.008243 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.008243 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.008243 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.008243 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.008243 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.26457 | 0 | 0 |  |  |  |  | -0.26457 | 0 |  |  |  |  | 0 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.008279 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | 0.26461 | 0 | 581 |  |  |  |  | -0.26461 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.008444 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.26477 | 0 | 0 |  |  |  |  | -0.26477 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.008444 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.26477 | 0 | 0 |  |  |  |  | -0.26477 | 0 |  |  |  |  | 0 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.008613 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 |  |  |  |  | 0 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.008613 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 |  |  |  |  | 0 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.008613 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 |  |  |  |  | 0 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.008613 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.26494 | 0 | 0 |  |  |  |  | -0.26494 | 0 |  |  |  |  | 0 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.009168 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.26549 | 0 | 0 |  |  |  |  | -0.26549 | 0 |  |  |  |  | 0 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.009208 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 651 |  |  |  |  | -0.26553 | 0 |  |  |  |  | 0 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.009208 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 564 |  |  |  |  | -0.26553 | 0 |  |  |  |  | 0 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.009208 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.26553 | 0 | 603 |  |  |  |  | -0.26553 | 0 |  |  |  |  | 0 | 0
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.009212 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.26554 | 252.4 | 252.4 |  |  |  |  | -0.26554 | -67.0218 |  |  |  |  | 0 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.009212 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.26554 | 167.7 | 167.7 |  |  |  |  | -0.26554 | -44.5308 |  |  |  |  | 0 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.009212 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.26554 | 166.4 | 166.4 |  |  |  |  | -0.26554 | -44.1856 |  |  |  |  | 0 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.009252 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.26558 | 0 | 0 |  |  |  |  | -0.26558 | 0 |  |  |  |  | 0 | 0
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.009316 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.26564 | 546 | 546 |  |  |  |  | -0.26564 | -145.0406 |  |  |  |  | 0 | 0
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.009316 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.26564 | 248 | 248 |  |  |  |  | -0.26564 | -65.8793 |  |  |  |  | 0 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.009316 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.26564 | 166 | 166 |  |  |  |  | -0.26564 | -44.0966 |  |  |  |  | 0 | 0
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.009316 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.26564 | 166 | 166 |  |  |  |  | -0.26564 | -44.0966 |  |  |  |  | 0 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.009316 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.26564 | 13 | 13 |  |  |  |  | -0.26564 | -3.4533 |  |  |  |  | 0 | 0
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.009316 | 620.4 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.26564 | 0 | 654 |  |  |  |  | -0.26564 | 0 |  |  |  |  | 0 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.009621 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.009621 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.009621 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.009621 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.009621 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.009621 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.009621 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.009621 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.009621 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.009621 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.009621 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.009621 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.009621 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.009621 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.009621 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.26595 | 0 | 0 |  |  |  |  | -0.26595 | 0 |  |  |  |  | 0 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.009768 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.26609 | 0 | 0 |  |  |  |  | -0.26609 | 0 |  |  |  |  | 0 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.009872 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 |  |  |  |  | 0 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.009872 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 |  |  |  |  | 0 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.009872 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 |  |  |  |  | 0 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.009872 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 |  |  |  |  | 0 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.009872 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.2662 | 0 | 0 |  |  |  |  | -0.2662 | 0 |  |  |  |  | 0 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.009911 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0 |  |  |  |  | 0 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.009911 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0 |  |  |  |  | 0 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.009911 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0 |  |  |  |  | 0 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.009911 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.26624 | 0 | 0 |  |  |  |  | -0.26624 | 0 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | E | Houston | YES | -0.009973 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.2663 | 57 | 57 |  |  |  |  | -0.2663 | -15.1791 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | D | Houston | YES | -0.009973 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.2663 | 55 | 55 |  |  |  |  | -0.2663 | -14.6465 |  |  |  |  | 0 | 0
48693 | GBY_83841065 | F | Houston | YES | -0.009973 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.2663 | 54 | 54 |  |  |  |  | -0.2663 | -14.3802 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161 |  |  |  |  | 0 | 0
48692 | GBY_81821075 | C | Houston | YES | -0.009973 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.2663 | 47 | 47 |  |  |  |  | -0.2663 | -12.5161 |  |  |  |  | 0 | 0
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.009986 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.26631 | 0 | 0 |  |  |  |  | -0.26631 | 0 |  |  |  |  | 0 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.009986 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.26631 | 0 | 0 |  |  |  |  | -0.26631 | 0 |  |  |  |  | 0 | 0
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.010001 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.26633 | 282 | 282 |  |  |  |  | -0.26633 | -75.1043 |  |  |  |  | 0 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.010001 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.26633 | 163.2 | 163.2 |  |  |  |  | -0.26633 | -43.4646 |  |  |  |  | 0 | 0
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.010001 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.26633 | 157.5 | 157.5 |  |  |  |  | -0.26633 | -41.9465 |  |  |  |  | 0 | 0
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.010001 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.26633 | 157.1 | 157.1 |  |  |  |  | -0.26633 | -41.84 |  |  |  |  | 0 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.010001 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.26633 | 157 | 157 |  |  |  |  | -0.26633 | -41.8134 |  |  |  |  | 0 | 0
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.010025 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.26635 | 0 | 0 |  |  |  |  | -0.26635 | 0 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.010042 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.26637 | 18 | 18 |  |  |  |  | -0.26637 | -4.7946 |  |  |  |  | 0 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | -0.010042 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.26637 | 12 | 12 |  |  |  |  | -0.26637 | -3.1964 |  |  |  |  | 0 | 0
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.010043 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.26637 | 176 | 176 |  |  |  |  | -0.26637 | -46.881 |  |  |  |  | 0 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.010044 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.26637 | 165 | 165 |  |  |  |  | -0.26637 | -43.9511 |  |  |  |  | 0 | 0
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.010045 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.26637 | 0 | 0 |  |  |  |  | -0.26637 | 0 |  |  |  |  | 0 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.010045 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.26637 | 0 | 0 |  |  |  |  | -0.26637 | 0 |  |  |  |  | 0 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.010049 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.26638 | 213 | 213 |  |  |  |  | -0.26638 | -56.7379 |  |  |  |  | 0 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.010049 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.26638 | 16.2 | 16.2 |  |  |  |  | -0.26638 | -4.3153 |  |  |  |  | 0 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.01005 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.26638 | 228 | 228 |  |  |  |  | -0.26638 | -60.7338 |  |  |  |  | 0 | 0
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.01005 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 |  |  |  |  | 0 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.01005 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 |  |  |  |  | 0 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.01005 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 |  |  |  |  | 0 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.01005 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 |  |  |  |  | 0 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.010051 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 |  |  |  |  | 0 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.010051 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 |  |  |  |  | 0 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.010051 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.26638 | 0 | 0 |  |  |  |  | -0.26638 | 0 |  |  |  |  | 0 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.010076 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0 |  |  |  |  | 0 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.010076 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.010076 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.010076 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.2664 | 0 | 0 |  |  |  |  | -0.2664 | 0 |  |  |  |  | 0 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.010116 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | 0.26644 | 0 | 0 |  |  |  |  | -0.26644 | 0 |  |  |  |  | 0 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.010119 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.26645 | 42 | 42 |  |  |  |  | -0.26645 | -11.1907 |  |  |  |  | 0 | 0
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.010119 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.26645 | 42 | 42 |  |  |  |  | -0.26645 | -11.1907 |  |  |  |  | 0 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.010119 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.26645 | 39 | 39 |  |  |  |  | -0.26645 | -10.3914 |  |  |  |  | 0 | 0
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.010119 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.26645 | 39 | 39 |  |  |  |  | -0.26645 | -10.3914 |  |  |  |  | 0 | 0
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.010129 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.26646 | 0 | 0 |  |  |  |  | -0.26646 | 0 |  |  |  |  | 0 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.010129 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.26646 | 0 | 0 |  |  |  |  | -0.26646 | 0 |  |  |  |  | 0 | 0
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.010189 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.26652 | 108 | 108 |  |  |  |  | -0.26652 | -28.7836 |  |  |  |  | 0 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.010189 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.26652 | 107 | 107 |  |  |  |  | -0.26652 | -28.5171 |  |  |  |  | 0 | 0
48881 | THW_4344 | G | Houston | YES | -0.010189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.26652 | 58 | 58 |  |  |  |  | -0.26652 | -15.4579 |  |  |  |  | 0 | 0
48881 | THW_4344 | H | Houston | YES | -0.010189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.26652 | 58 | 58 |  |  |  |  | -0.26652 | -15.4579 |  |  |  |  | 0 | 0
48877 | THW_3334 | D | Houston | YES | -0.010189 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.26652 | 57 | 57 |  |  |  |  | -0.26652 | -15.1914 |  |  |  |  | 0 | 0
48879 | THW_4142 | E | Houston | YES | -0.010189 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.26652 | 56 | 56 |  |  |  |  | -0.26652 | -14.9249 |  |  |  |  | 0 | 0
48875 | THW_3132 | A | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583 |  |  |  |  | 0 | 0
48877 | THW_3334 | C | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583 |  |  |  |  | 0 | 0
48879 | THW_4142 | F | Houston | YES | -0.010189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.26652 | 55 | 55 |  |  |  |  | -0.26652 | -14.6583 |  |  |  |  | 0 | 0
48875 | THW_3132 | B | Houston | YES | -0.010189 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.26652 | 53 | 53 |  |  |  |  | -0.26652 | -14.1253 |  |  |  |  | 0 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.010218 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.26654 | 746 | 746 |  |  |  |  | -0.26654 | -198.842 |  |  |  |  | 0 | 0
49803 | EXN_15GT | 1 | Houston | YES | -0.010247 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.010247 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.010247 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.010247 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.010247 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.010247 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.010247 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.010247 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.010247 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.010247 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.010247 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.26657 | 0 | 0 |  |  |  |  | -0.26657 | 0 |  |  |  |  | 0 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.01025 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.26658 | 12 | 12 |  |  |  |  | -0.26658 | -3.1989 |  |  |  |  | 0 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.010275 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.2666 | 744 | 744 |  |  |  |  | -0.2666 | -198.3513 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.010275 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.010275 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0 |  |  |  |  | 0 | 0
48940 | WARVUE_GT1 | G1 | Houston | YES | -0.010275 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | 0.2666 | 0 | 0 |  |  |  |  | -0.2666 | 0 |  |  |  |  | 0 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.010279 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 |  |  |  |  | 0 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.010279 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 |  |  |  |  | 0 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.010279 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 |  |  |  |  | 0 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.010279 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 |  |  |  |  | 0 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.010279 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 |  |  |  |  | 0 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.010279 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 |  |  |  |  | 0 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.010279 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.26661 | 0 | 0 |  |  |  |  | -0.26661 | 0 |  |  |  |  | 0 | 0
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.010295 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.26662 | 0 | 0 |  |  |  |  | -0.26662 | 0 |  |  |  |  | 0 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595 |  |  |  |  | 0 | 0
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595 |  |  |  |  | 0 | 0
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.010299 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | 0.26663 | 172 | 172 |  |  |  |  | -0.26663 | -45.8595 |  |  |  |  | 0 | 0
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.010346 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.26667 | 269.2 | 269.2 |  |  |  |  | -0.26667 | -71.7882 |  |  |  |  | 0 | 0
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.010346 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.26667 | 162.8 | 162.8 |  |  |  |  | -0.26667 | -43.4142 |  |  |  |  | 0 | 0
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.010346 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.26667 | 161.4 | 161.4 |  |  |  |  | -0.26667 | -43.0409 |  |  |  |  | 0 | 0
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.010346 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.26667 | 158.9 | 158.9 |  |  |  |  | -0.26667 | -42.3742 |  |  |  |  | 0 | 0
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.010366 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.26669 | 398 | 398 |  |  |  |  | -0.26669 | -106.1435 |  |  |  |  | 0 | 0
48885 | THW_5152 | B | Houston | YES | -0.010389 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.26672 | 59 | 59 |  |  |  |  | -0.26672 | -15.7362 |  |  |  |  | 0 | 0
48887 | THW_5556 | E | Houston | YES | -0.010389 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.26672 | 59 | 59 |  |  |  |  | -0.26672 | -15.7362 |  |  |  |  | 0 | 0
48885 | THW_5152 | A | Houston | YES | -0.010389 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.26672 | 58 | 58 |  |  |  |  | -0.26672 | -15.4695 |  |  |  |  | 0 | 0
48886 | THW_5354 | D | Houston | YES | -0.010389 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.26672 | 58 | 58 |  |  |  |  | -0.26672 | -15.4695 |  |  |  |  | 0 | 0
48886 | THW_5354 | C | Houston | YES | -0.010389 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.26672 | 57 | 57 |  |  |  |  | -0.26672 | -15.2028 |  |  |  |  | 0 | 0
48887 | THW_5556 | F | Houston | YES | -0.010389 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.26672 | 57 | 57 |  |  |  |  | -0.26672 | -15.2028 |  |  |  |  | 0 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.010673 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 |  |  |  |  | 0 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.010673 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 |  |  |  |  | 0 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.010673 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 |  |  |  |  | 0 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.010673 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 |  |  |  |  | 0 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.010673 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.267 | 0 | 0 |  |  |  |  | -0.267 | 0 |  |  |  |  | 0 | 0
334 | RWMILLER03 | 3 | North | YES | -0.010926 | 166.4 | 65 | 208 | 0 | 1.04 | GST | -1 | 0.26725 | 208 | 208 |  |  | -2.2726 | 208 | -0.26725 | -55.5885 |  |  |  |  | 0 | 0
333 | RWMILLER02 | 2 | North | YES | -0.010926 | 95.2 | 37 | 119 | 0 | 1.04 | GST | -1 | 0.26725 | 119 | 119 |  |  | -1.3002 | 119 | -0.26725 | -31.803 |  |  |  |  | 0 | 0
335 | RWMILLER04 | 4 | North | YES | -0.010926 | 81.6 | 0 | 102 | 0 | 1.04 | GST | -1 | 0.26725 | 102 | 102 |  |  | -1.1145 | 102 | -0.26725 | -27.2597 |  |  |  |  | 0 | 0
336 | RWMILLER05 | 5 | North | YES | -0.010926 | 80.8 | 0 | 101 | 0 | 1.04 | GST | -1 | 0.26725 | 101 | 101 |  |  | -1.1035 | 101 | -0.26725 | -26.9925 |  |  |  |  | 0 | 0
332 | RWMILLER01 | 1 | North | YES | -0.010926 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | -1 | 0.26725 | 73 | 73 |  |  | -0.7976 | 73 | -0.26725 | -19.5094 |  |  |  |  | 0 | 0
60000 | DSKY2 | 1 | West | YES | 0.24668 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.26775 | 0 | 76.5 | 18.8706 | 76.5 |  |  | 0.26775 | 20.4826 |  |  |  |  | 0 | 0
251 | BOSQUESW803 | 2 | North | YES | -0.01188 | 150 | 0 | 150 | 0 | 1.032 | CC | -1 | 0.26821 | 150 | 150 |  |  | -1.782 | 150 | -0.26821 | -40.2309 |  |  |  |  | 0 | 0
253 | BOSQUESW804 | 2 | North | YES | -0.01188 | 80 | 0 | 80 | 0 | 1.032 | CC | -1 | 0.26821 | 80 | 80 |  |  | -0.9504 | 80 | -0.26821 | -21.4565 |  |  |  |  | 0 | 0
60018 | DSKY1 | 1 | West | YES | 0.24737 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.26844 | 0 | 84 | 20.7789 | 84 |  |  | 0.26844 | 22.5489 |  |  |  |  | 0 | 0
244 | WHITNYDM01 | 1 | North | YES | -0.012393 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.26872 | 0 | 0 |  |  | 0 | 0 | -0.26872 | 0 |  |  |  |  | 0 | 0
245 | WHITNYDM02 | 2 | North | YES | -0.012393 | 15 | 0 | 15 | 0 | 1.035 | Hydro | -1 | 0.26872 | 0 | 0 |  |  | 0 | 0 | -0.26872 | 0 |  |  |  |  | 0 | 0
238 | BOSQUESW505 | 1 | North | YES | -0.013117 | 255 | 0 | 255 | 0 | 1.02 | CC | -1 | 0.26944 | 255 | 255 |  |  | -3.3448 | 255 | -0.26944 | -68.708 |  |  |  |  | 0 | 0
247 | BOSQUESW501 | 2 | North | YES | -0.013117 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | -1 | 0.26944 | 156 | 156 |  |  | -2.0463 | 156 | -0.26944 | -42.0331 |  |  |  |  | 0 | 0
239 | BOSQUESW502 | 1 | North | YES | -0.013117 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | -1 | 0.26944 | 149 | 149 |  |  | -1.9544 | 149 | -0.26944 | -40.147 |  |  |  |  | 0 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | -0.013223 | 380 | 0 | 380 | 0 | 1.0319 | CC | -1 | 0.26955 | 380 | 380 |  |  | -5.0247 | 380 | -0.26955 | -102.4287 |  |  |  |  | 0 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | -0.013223 | 159 | 0 | 159 | 0 | 1.0319 | CC | -1 | 0.26955 | 159 | 159 |  |  | -2.1025 | 159 | -0.26955 | -42.8583 |  |  |  |  | 0 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | -0.013223 | 158 | 0 | 158 | 0 | 1.0319 | CC | -1 | 0.26955 | 158 | 158 |  |  | -2.0892 | 158 | -0.26955 | -42.5888 |  |  |  |  | 0 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | -0.013223 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | -1 | 0.26955 | 154.2 | 154.2 |  |  | -2.039 | 154.2 | -0.26955 | -41.5645 |  |  |  |  | 0 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | -0.013262 | 177.6 | 40 | 222 | 0 | 1.029 | GST | -1 | 0.26959 | 222 | 222 |  |  | -2.9442 | 222 | -0.26959 | -59.8486 |  |  |  |  | 0 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | -0.013262 | 60 | 33 | 75 |  | 1.029 | GST | -1 | 0.26959 | 75 | 75 |  |  | -0.99465 | 75 | -0.26959 | -20.2191 |  |  |  |  | 0 | 0
1898 | COMCHEPK_1G | 1 | North | YES | -0.013425 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | -1 | 0.26975 | 0 | 0 |  |  | 0 | 0 | -0.26975 | 0 |  |  |  |  | 0 | 0
1899 | COMCHEPK_2G | 2 | North | YES | -0.013425 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | -1 | 0.26975 | 0 | 0 |  |  | 0 | 0 | -0.26975 | 0 |  |  |  |  | 0 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | -0.013678 | 84 | 25 | 105 | 0 | 1.035 | GST | -1 | 0.27 | 105 | 105 |  |  | -1.4362 | 105 | -0.27 | -28.3504 |  |  |  |  | 0 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | -0.013678 | 0 | 2 | 48 |  | 1.015 | GST | -1 | 0.27 | 48 | 48 |  |  | -0.65654 | 48 | -0.27 | -12.9602 |  |  |  |  | 0 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | -0.013678 | 46 | 2 | 46 | 0 | 1.015 | GST | -1 | 0.27 | 46 | 46 |  |  | -0.62919 | 46 | -0.27 | -12.4202 |  |  |  |  | 0 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | -0.013721 | 13.6 | 4 | 17 |  | 1.028 | GGT | -1 | 0.27005 | 17 | 17 |  |  | -0.23326 | 17 | -0.27005 | -4.5908 |  |  |  |  | 0 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | -0.013721 | 0 | 5 | 12 |  | 1 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0 |  |  |  |  | 0 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | -0.013721 | 0 | 12 | 51 |  | 1.028 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0 |  |  |  |  | 0 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | -0.013721 | 0 | 5 | 22 |  | 1.031 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0 |  |  |  |  | 0 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | -0.013721 | 0 | 5 | 25 |  | 1.031 | GST | -1 | 0.27005 | 0 | 0 |  |  | 0 | 0 | -0.27005 | 0 |  |  |  |  | 0 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | -0.013737 | 32 | 0 | 32 |  | 1.02 | GST | -1 | 0.27006 | 32 | 32 |  |  | -0.43958 | 32 | -0.27006 | -8.642 |  |  |  |  | 0 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | -0.013752 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | -1 | 0.27008 | 0 | 463 |  |  | 0 | 0 | -0.27008 | 0 |  |  |  |  | 0 | 0
3404 | THOUSE_2G | 2 | North | YES | -0.013971 | 807 | 250 | 807 | 0 | 1.012 | GSC | -1 | 0.2703 | 807 | 807 |  |  | -11.2746 | 807 | -0.2703 | -218.1298 |  |  |  |  | 0 | 0
3403 | THOUSE_1G | 1 | North | YES | -0.013971 | 563 | 200 | 563 | 0 | 1.012 | GSC | -1 | 0.2703 | 563 | 563 |  |  | -7.8657 | 563 | -0.2703 | -152.1773 |  |  |  |  | 0 | 0
1879 | WLFHOLW_3G | 3 | North | YES | -0.014527 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | -1 | 0.27085 | 272.4 | 272.4 |  |  | -3.9572 | 272.4 | -0.27085 | -73.7804 |  |  |  |  | 0 | 0
1877 | WLFHOLW_1G | 1 | North | YES | -0.014527 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | -1 | 0.27085 | 217.3 | 217.3 |  |  | -3.1567 | 217.3 | -0.27085 | -58.8564 |  |  |  |  | 0 | 0
1878 | WLFHOLW_2G | 2 | North | YES | -0.014527 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | -1 | 0.27085 | 215.7 | 215.7 |  |  | -3.1335 | 215.7 | -0.27085 | -58.423 |  |  |  |  | 0 | 0
60017 | ORNNWP1 | 1 | West | YES | 0.24984 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.27091 | 0 | 80 | 19.987 | 80 |  |  | 0.27091 | 21.6726 |  |  |  |  | 0 | 0
344 | MRSSHPRD | 1 | North | YES | -0.014638 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.27096 | 0 | 0 |  |  | 0 | 0 | -0.27096 | 0 |  |  |  |  | 0 | 0
345 | MRSSHPRD01 | 2 | North | YES | -0.014638 | 0 | 0 | 12 |  | 1.03 | Hydro | -1 | 0.27096 | 0 | 0 |  |  | 0 | 0 | -0.27096 | 0 |  |  |  |  | 0 | 0
39960 | TNTNPONE_18 | 1 | North | YES | -0.015463 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | -1 | 0.27179 | 0 | 152.3 |  |  | 0 | 0 | -0.27179 | 0 |  |  |  |  | 0 | 0
39970 | TNTNPONE_28 | 1 | North | YES | -0.015463 | 153 | 30 | 153 |  | 1.04 | LIGCO | -1 | 0.27179 | 0 | 153 |  |  | 0 | 0 | -0.27179 | 0 |  |  |  |  | 0 | 0
366 | JNSNCNTY802 | 1 | North | YES | -0.015703 | 168 | 20 | 168 | 0 | 1.02 | Cogen | -1 | 0.27203 | 0 | 0 |  |  | 0 | 0 | -0.27203 | 0 |  |  |  |  | 0 | 0
367 | JNSNCNTY802 | 2 | North | YES | -0.015703 | 90 | 20 | 90 | 0 | 1.02 | Cogen | -1 | 0.27203 | 0 | 0 |  |  | 0 | 0 | -0.27203 | 0 |  |  |  |  | 0 | 0
1892 | DECRDOVA_2G | A | North | YES | -0.015865 | 65 | 65 | 70 | 0 | 1.025 | GGT | -1 | 0.27219 | 70 | 70 |  |  | -1.1105 | 70 | -0.27219 | -19.0534 |  |  |  |  | 0 | 0
1893 | DECRDOVA_3G | B | North | YES | -0.015865 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.27219 | 69 | 69 |  |  | -1.0947 | 69 | -0.27219 | -18.7812 |  |  |  |  | 0 | 0
1894 | DECRDOVA_4G | C | North | YES | -0.015865 | 65 | 65 | 69 | 0 | 1.025 | GGT | -1 | 0.27219 | 69 | 69 |  |  | -1.0947 | 69 | -0.27219 | -18.7812 |  |  |  |  | 0 | 0
1895 | DECRDOVA_5G | D | North | YES | -0.015865 | 65 | 65 | 68 | 0 | 1.025 | GGT | -1 | 0.27219 | 68 | 68 |  |  | -1.0788 | 68 | -0.27219 | -18.509 |  |  |  |  | 0 | 0
48721 | LEG_1___1 | 1 | North | YES | -0.016148 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | -1 | 0.27247 | 0 | 827 |  |  | 0 | 0 | -0.27247 | 0 |  |  |  |  | 0 | 0
48722 | LEG_2___2 | 2 | North | YES | -0.016148 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | -1 | 0.27247 | 0 | 819 |  |  | 0 | 0 | -0.27247 | 0 |  |  |  |  | 0 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.25162 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | 0.27269 | 0 | 112.5 | 28.3074 | 112.5 |  |  | 0.27269 | 30.6778 |  |  |  |  | 0 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | 0.25162 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 149.5 | 37.6173 | 149.5 |  |  | 0.27269 | 40.7674 |  |  |  |  | 0 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | 0.25162 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 186 | 46.8015 | 186 |  |  | 0.27269 | 50.7207 |  |  |  |  | 0 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | 0.25162 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | 0.27269 | 0 | 214.5 | 53.9727 | 214.5 |  |  | 0.27269 | 58.4924 |  |  |  |  | 0 | 0
36998 | RDCNYNG1 | 1 | West | YES | 0.25225 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.27332 | 0 | 84 | 21.1888 | 84 |  |  | 0.27332 | 22.9588 |  |  |  |  | 0 | 0
3381 | BBRN_1G | 1 | North | YES | -0.018042 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | -1 | 0.27437 | 0 | 618 |  |  | 0 | 0 | -0.27437 | 0 |  |  |  |  | 0 | 0
3382 | BBRN_2G | 2 | North | YES | -0.018042 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | -1 | 0.27437 | 0 | 589 |  |  | 0 | 0 | -0.27437 | 0 |  |  |  |  | 0 | 0
13133 | CALFREST_3G | 3 | North | YES | -0.018346 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | -1 | 0.27467 | 177.4 | 177.4 |  |  | -3.2546 | 177.4 | -0.27467 | -48.7268 |  |  |  |  | 0 | 0
13132 | CALFREST_2G | 2 | North | YES | -0.018346 | 151 | 57 | 151 | 0 | 1.031 | CC | -1 | 0.27467 | 151 | 151 |  |  | -2.7702 | 151 | -0.27467 | -41.4755 |  |  |  |  | 0 | 0
13131 | CALFREST_1G | 1 | North | YES | -0.018346 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | -1 | 0.27467 | 150.7 | 150.7 |  |  | -2.7647 | 150.7 | -0.27467 | -41.3931 |  |  |  |  | 0 | 0
13136 | CALFREST_6G | 6 | North | YES | -0.018414 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | -1 | 0.27474 | 177.5 | 177.5 |  |  | -3.2685 | 177.5 | -0.27474 | -48.7664 |  |  |  |  | 0 | 0
13135 | CALFREST_5G | 5 | North | YES | -0.018414 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | -1 | 0.27474 | 152.3 | 152.3 |  |  | -2.8045 | 152.3 | -0.27474 | -41.8429 |  |  |  |  | 0 | 0
13134 | CALFREST_4G | 4 | North | YES | -0.018414 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | -1 | 0.27474 | 151.5 | 151.5 |  |  | -2.7897 | 151.5 | -0.27474 | -41.6231 |  |  |  |  | 0 | 0
505 | NTHTEXAS03 | 3 | North | YES | -0.018619 | 30.4 | 15 | 38 |  | 1.015 | GST | -1 | 0.27495 | 38 | 38 |  |  | -0.70752 | 38 | -0.27495 | -10.4479 |  |  |  |  | 0 | 0
503 | NTHTEXAS01 | 1 | North | YES | -0.018619 | 0 | 5 | 18 |  | 1.015 | GST | -1 | 0.27495 | 18 | 18 |  |  | -0.33514 | 18 | -0.27495 | -4.949 |  |  |  |  | 0 | 0
504 | NTHTEXAS02 | 2 | North | YES | -0.018619 | 14.4 | 5 | 18 |  | 1.015 | GST | -1 | 0.27495 | 18 | 18 |  |  | -0.33514 | 18 | -0.27495 | -4.949 |  |  |  |  | 0 | 0
1889 | DECRDOVA_1G | 1 | North | YES | -0.018709 | 779 | 255 | 779 | 0 | 1.02 | GSC | -1 | 0.27504 | 779 | 779 |  |  | -14.5743 | 779 | -0.27504 | -214.2524 |  |  |  |  | 0 | 0
3126 | TRINIDAD_6G | 1 | North | YES | -0.019257 | 179.2 | 46 | 224 | 0 | 1 | GST | -1 | 0.27558 | 224 | 224 |  |  | -4.3136 | 224 | -0.27558 | -61.7306 |  |  |  |  | 0 | 0
1938 | MDLTHELP_6G | 6 | North | YES | -0.019338 | 226 | 74 | 226 | 0 | 1 | CC | -1 | 0.27566 | 226 | 226 |  |  | -4.3704 | 226 | -0.27566 | -62.3001 |  |  |  |  | 0 | 0
1937 | MDLTHELP_5G | 5 | North | YES | -0.019338 | 224 | 74 | 224 | 0 | 1 | CC | -1 | 0.27566 | 224 | 224 |  |  | -4.3317 | 224 | -0.27566 | -61.7488 |  |  |  |  | 0 | 0
1943 | MDLTHELP_3G | 3 | North | YES | -0.019338 | 212 | 74 | 212 | 0 | 1 | CC | -1 | 0.27566 | 212 | 212 |  |  | -4.0997 | 212 | -0.27566 | -58.4408 |  |  |  |  | 0 | 0
1944 | MDLTHELP_4G | 4 | North | YES | -0.019338 | 211 | 74 | 211 | 0 | 1 | CC | -1 | 0.27566 | 211 | 211 |  |  | -4.0803 | 211 | -0.27566 | -58.1651 |  |  |  |  | 0 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | -0.01959 | 196 | 130 | 196 | 0 | 1.036 | CC | -1 | 0.27592 | 196 | 196 |  |  | -3.8396 | 196 | -0.27592 | -54.0796 |  |  |  |  | 0 | 0
12323 | ENNSTRAC_2G | 2 | North | YES | -0.01959 | 116 | 100 | 116 | 0 | 1.036 | CC | -1 | 0.27592 | 116 | 116 |  |  | -2.2724 | 116 | -0.27592 | -32.0063 |  |  |  |  | 0 | 0
3108 | STRYKER_2G | 2 | North | YES | -0.019928 | 484 | 75 | 484 | 0 | 1.029 | GST | -1 | 0.27625 | 484 | 484 |  |  | -9.6452 | 484 | -0.27625 | -133.707 |  |  |  |  | 0 | 0
3107 | STRYKER_1G | 1 | North | YES | -0.019928 | 145.6 | 45 | 182 | 0 | 1.029 | GST | -1 | 0.27625 | 182 | 182 |  |  | -3.6269 | 182 | -0.27625 | -50.2783 |  |  |  |  | 0 | 0
3309 | ASPN_G | 1 | North | YES | -0.019961 | 50 | 0 | 50 |  | 1 | Bio | -1 | 0.27629 | 50 | 50 |  |  | -0.99805 | 50 | -0.27629 | -13.8144 |  |  |  |  | 0 | 0
3348 | CHAMPION_1G | MB | North | YES | -0.019978 | 0 | 42 | 42 |  | 1 | Cogen | -1 | 0.2763 | 0 | 0 |  |  | 0 | 0 | -0.2763 | 0 |  |  |  |  | 0 | 0
1941 | MDLTHELP_1G | 1 | North | YES | -0.020066 | 216.4 | 74 | 216.4 | 0 | 1 | CC | -1 | 0.27639 | 216.4 | 216.4 |  |  | -4.3423 | 216.4 | -0.27639 | -59.8113 |  |  |  |  | 0 | 0
1942 | MDLTHELP_2G | 2 | North | YES | -0.020066 | 216.1 | 74 | 216.1 | 0 | 1 | CC | -1 | 0.27639 | 216.1 | 216.1 |  |  | -4.3363 | 216.1 | -0.27639 | -59.7284 |  |  |  |  | 0 | 0
13119 | TGATEWAY_4G | 4 | North | YES | -0.020136 | 399 | 65 | 399 | 0 | 1.0232 | CC | -1 | 0.27646 | 399 | 399 |  |  | -8.0343 | 399 | -0.27646 | -110.3084 |  |  |  |  | 0 | 0
13116 | TGATEWAY_1G | 1 | North | YES | -0.020136 | 151 | 30 | 151 | 0 | 1.0232 | CC | -1 | 0.27646 | 151 | 151 |  |  | -3.0405 | 151 | -0.27646 | -41.7458 |  |  |  |  | 0 | 0
13118 | TGATEWAY_3G | 3 | North | YES | -0.020136 | 148 | 30 | 148 | 0 | 1.0232 | CC | -1 | 0.27646 | 148 | 148 |  |  | -2.9801 | 148 | -0.27646 | -40.9164 |  |  |  |  | 0 | 0
13117 | TGATEWAY_2G | 2 | North | YES | -0.020136 | 130 | 30 | 130 | 0 | 1.0232 | CC | -1 | 0.27646 | 130 | 130 |  |  | -2.6177 | 130 | -0.27646 | -35.9401 |  |  |  |  | 0 | 0
3097 | MARTLAKE_1G | 1 | North | YES | -0.020319 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 790 |  |  | 0 | 0 | -0.27665 | 0 |  |  |  |  | 0 | 0
3098 | MARTLAKE_2G | 2 | North | YES | -0.020319 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 795 |  |  | 0 | 0 | -0.27665 | 0 |  |  |  |  | 0 | 0
3099 | MARTLAKE_3G | 3 | North | YES | -0.020319 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | -1 | 0.27665 | 0 | 804 |  |  | 0 | 0 | -0.27665 | 0 |  |  |  |  | 0 | 0
1600 | BARTNWND_1G | 1 | North | YES | -0.020887 | 12 | 0 | 120 | 0 | 1.022 | Wind | -1 | 0.27721 | 0 | 120 |  |  | 0 | 0 | -0.27721 | 0 |  |  |  |  | 0 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | 0.25649 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 37.5 | 9.6182 | 37.5 |  |  | 0.27756 | 10.4084 |  |  |  |  | 0 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | 0.25649 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 80.5 | 20.6471 | 80.5 |  |  | 0.27756 | 22.3433 |  |  |  |  | 0 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | 0.25649 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 105 | 26.931 | 105 |  |  | 0.27756 | 29.1435 |  |  |  |  | 0 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | 0.25649 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 107.5 | 27.5722 | 107.5 |  |  | 0.27756 | 29.8374 |  |  |  |  | 0 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | 0.25649 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.27756 | 0 | 119 | 30.5218 | 119 |  |  | 0.27756 | 33.0293 |  |  |  |  | 0 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | 0.25649 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.27756 | 0 | 135 | 34.6256 | 135 |  |  | 0.27756 | 37.4702 |  |  |  |  | 0 | 0
2417 | MTCK8_G | 8 | North | YES | -0.021359 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | -1 | 0.27769 | 556 | 556 |  |  | -11.8756 | 556 | -0.27769 | -154.393 |  |  |  |  | 0 | 0
2413 | MTCK6_G | 6 | North | YES | -0.021359 | 0 | 30 | 118 |  | 1.022 | GST | -1 | 0.27769 | 118 | 118 |  |  | -2.5204 | 118 | -0.27769 | -32.7669 |  |  |  |  | 0 | 0
2414 | MTCK7_G | 7 | North | YES | -0.021359 | 0 | 30 | 115 |  | 1.022 | GST | -1 | 0.27769 | 115 | 115 |  |  | -2.4563 | 115 | -0.27769 | -31.9338 |  |  |  |  | 0 | 0
12440 | PARKD_1SVC8 | 1 | North | YES | -0.02162 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.27795 | 0 | 0 |  |  | 0 | 0 | -0.27795 | 0 |  |  |  |  | 0 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | -0.02162 | 0 | 0 | 0 | 0 | 1.007 | GST | -1 | 0.27795 | 0 | 0 |  |  | 0 | 0 | -0.27795 | 0 |  |  |  |  | 0 | 0
12424 | FPLEFR2S_G | 4 | North | YES | -0.021673 | 415 | 191 | 415 | 0 | 1 | CC | -1 | 0.278 | 415 | 415 |  |  | -8.9943 | 415 | -0.278 | -115.3697 |  |  |  |  | 0 | 0
12414 | FPLEFR1S_G | 4 | North | YES | -0.021673 | 414 | 191 | 414 | 0 | 1 | CC | -1 | 0.278 | 414 | 414 |  |  | -8.9726 | 414 | -0.278 | -115.0917 |  |  |  |  | 0 | 0
12412 | FPLEFR1B_G | 2 | North | YES | -0.021673 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.278 | 164 | 164 |  |  | -3.5544 | 164 | -0.278 | -45.5919 |  |  |  |  | 0 | 0
12413 | FPLEFR1C_G | 3 | North | YES | -0.021673 | 164 | 72 | 164 | 0 | 1 | CC | -1 | 0.278 | 164 | 164 |  |  | -3.5544 | 164 | -0.278 | -45.5919 |  |  |  |  | 0 | 0
12423 | FPLEFR2C_G | 3 | North | YES | -0.021673 | 163 | 72 | 163 | 0 | 1 | CC | -1 | 0.278 | 163 | 163 |  |  | -3.5327 | 163 | -0.278 | -45.3139 |  |  |  |  | 0 | 0
12421 | FPLEFR2A_G | 1 | North | YES | -0.021673 | 162 | 72 | 162 | 0 | 1 | CC | -1 | 0.278 | 162 | 162 |  |  | -3.511 | 162 | -0.278 | -45.0359 |  |  |  |  | 0 | 0
12411 | FPLEFR1A_G | 1 | North | YES | -0.021673 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.278 | 161 | 161 |  |  | -3.4894 | 161 | -0.278 | -44.7579 |  |  |  |  | 0 | 0
12422 | FPLEFR2B_G | 2 | North | YES | -0.021673 | 161 | 72 | 161 | 0 | 1 | CC | -1 | 0.278 | 161 | 161 |  |  | -3.4894 | 161 | -0.278 | -44.7579 |  |  |  |  | 0 | 0
2452 | LKHB2_G | 2 | North | YES | -0.021772 | 516 | 80 | 516 | 0 | 1.022 | GST | -1 | 0.2781 | 516 | 516 |  |  | -11.2344 | 516 | -0.2781 | -143.4987 |  |  |  |  | 0 | 0
2451 | LKHB1_G | 1 | North | YES | -0.021772 | 0 | 80 | 391 |  | 1.022 | GST | -1 | 0.2781 | 391 | 391 |  |  | -8.5129 | 391 | -0.2781 | -108.7364 |  |  |  |  | 0 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | 0.25715 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.27822 | 0 | 150 | 38.5729 | 150 |  |  | 0.27822 | 41.7336 |  |  |  |  | 0 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.25739 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.27846 | 0 | 80 | 20.5909 | 80 |  |  | 0.27846 | 22.2765 |  |  |  |  | 0 | 0
60016 | WOODWRD11A | 1 | West | YES | 0.25744 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.27851 | 0 | 80 | 20.5951 | 80 |  |  | 0.27851 | 22.2808 |  |  |  |  | 0 | 0
950 | STEAM3 | 1 | North | YES | -0.022215 | 41 | 13 | 42 | 0 | 1.02 | GST | -1 | 0.27854 | 42 | 42 |  |  | -0.93303 | 42 | -0.27854 | -11.6987 |  |  |  |  | 0 | 0
949 | STEAM2 | 1 | North | YES | -0.022215 | 26 | 8 | 26 | 0 | 0.99 | GST | -1 | 0.27854 | 26 | 26 |  |  | -0.57759 | 26 | -0.27854 | -7.2421 |  |  |  |  | 0 | 0
948 | STEAM1 | 1 | North | YES | -0.022215 | 0 | 12 | 20 |  | 1.02 | GST | -1 | 0.27854 | 20 | 20 |  |  | -0.4443 | 20 | -0.27854 | -5.5708 |  |  |  |  | 0 | 0
837 | NEWMAN_G5 | 1 | North | YES | -0.022234 | 0 | 15 | 40 |  | 1.01 | GST | -1 | 0.27856 | 40 | 40 |  |  | -0.88936 | 40 | -0.27856 | -11.1424 |  |  |  |  | 0 | 0
844 | OLINGER_G3 | 1 | North | YES | -0.02231 | 103.9 | 45 | 150 | 0 | 1.03 | GST | -1 | 0.27864 | 150 | 150 |  |  | -3.3465 | 150 | -0.27864 | -41.7954 |  |  |  |  | 0 | 0
843 | OLINGER_G2 | 1 | North | YES | -0.02231 | 76.2 | 25 | 110 | 0 | 1.03 | GST | -1 | 0.27864 | 110 | 110 |  |  | -2.4541 | 110 | -0.27864 | -30.65 |  |  |  |  | 0 | 0
842 | OLINGER_G1 | 1 | North | YES | -0.02231 | 55.4 | 20 | 79 | 0 | 1.03 | GST | -1 | 0.27864 | 79 | 79 |  |  | -1.7625 | 79 | -0.27864 | -22.0123 |  |  |  |  | 0 | 0
845 | OLINGER_G4 | 1 | North | YES | -0.02231 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | -1 | 0.27864 | 76 | 76 |  |  | -1.6956 | 76 | -0.27864 | -21.1764 |  |  |  |  | 0 | 0
60005 | KING_SE1A | 1 | West | YES | 0.25764 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.27871 | 0 | 40 | 10.3055 | 40 |  |  | 0.27871 | 11.1483 |  |  |  |  | 0 | 0
6016 | SWMESA | 1 | West | YES | 0.25764 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.27871 | 0 | 75 | 19.3228 | 75 |  |  | 0.27871 | 20.9031 |  |  |  |  | 0 | 0
60003 | KING_NE1A | 1 | West | YES | 0.25764 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27871 | 0 | 80 | 20.611 | 80 |  |  | 0.27871 | 22.2966 |  |  |  |  | 0 | 0
1701 | MOSES_1G | 1 | North | YES | -0.022662 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 558 |  |  | 0 | 0 | -0.27899 | 0 |  |  |  |  | 0 | 0
1702 | MOSES_2G | 2 | North | YES | -0.022662 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 579 |  |  | 0 | 0 | -0.27899 | 0 |  |  |  |  | 0 | 0
1703 | MOSES_3G | 3 | North | YES | -0.022662 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | -1 | 0.27899 | 0 | 808 |  |  | 0 | 0 | -0.27899 | 0 |  |  |  |  | 0 | 0
5925 | DCEAST | EQ | North | YES | -0.022662 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | -1 | 0.27899 | 0 | 0 |  |  | 0 | 0 | -0.27899 | 0 |  |  |  |  | 0 | 0
580 | JCKCNTY801 | 1 | North | YES | -0.02276 | 288 | 0 | 288 | 0 | 1.022 | CC | -1 | 0.27909 | 288 | 288 |  |  | -6.5549 | 288 | -0.27909 | -80.3768 |  |  |  |  | 0 | 0
581 | JCKCNTY802 | 2 | North | YES | -0.02276 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.27909 | 147 | 147 |  |  | -3.3457 | 147 | -0.27909 | -41.0257 |  |  |  |  | 0 | 0
582 | JCKCNTY803 | 3 | North | YES | -0.02276 | 147 | 0 | 147 | 0 | 1.022 | CC | -1 | 0.27909 | 147 | 147 |  |  | -3.3457 | 147 | -0.27909 | -41.0257 |  |  |  |  | 0 | 0
1675 | PEC_1G | 1 | North | YES | -0.022769 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0 |  |  |  |  | 0 | 0
1676 | PEC_2G | 2 | North | YES | -0.022769 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0 |  |  |  |  | 0 | 0
1677 | PEC_3G | 3 | North | YES | -0.022769 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | -1 | 0.2791 | 0 | 0 |  |  | 0 | 0 | -0.2791 | 0 |  |  |  |  | 0 | 0
1683 | LAMARPWR_6G | 6 | North | YES | -0.022815 | 198 | 129.1 | 198 | 0 | 1.038 | CC | -1 | 0.27914 | 198 | 198 |  |  | -4.5174 | 198 | -0.27914 | -55.27 |  |  |  |  | 0 | 0
1680 | LAMARPWR_3G | 3 | North | YES | -0.022815 | 196 | 129.1 | 196 | 0 | 1.038 | CC | -1 | 0.27914 | 196 | 196 |  |  | -4.4717 | 196 | -0.27914 | -54.7117 |  |  |  |  | 0 | 0
1678 | LAMARPWR_1G | 1 | North | YES | -0.022815 | 160 | 67.7 | 160 | 0 | 1.038 | CC | -1 | 0.27914 | 160 | 160 |  |  | -3.6504 | 160 | -0.27914 | -44.6626 |  |  |  |  | 0 | 0
1682 | LAMARPWR_5G | 5 | North | YES | -0.022815 | 157 | 67.7 | 157 | 0 | 1.038 | CC | -1 | 0.27914 | 157 | 157 |  |  | -3.582 | 157 | -0.27914 | -43.8252 |  |  |  |  | 0 | 0
1679 | LAMARPWR_2G | 2 | North | YES | -0.022815 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.27914 | 156 | 156 |  |  | -3.5591 | 156 | -0.27914 | -43.546 |  |  |  |  | 0 | 0
1681 | LAMARPWR_4G | 4 | North | YES | -0.022815 | 156 | 67.7 | 156 | 0 | 1.038 | CC | -1 | 0.27914 | 156 | 156 |  |  | -3.5591 | 156 | -0.27914 | -43.546 |  |  |  |  | 0 | 0
1948 | HANDLEY_4G | 4 | North | YES | -0.022866 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.27919 | 435 | 435 |  |  | -9.9467 | 435 | -0.27919 | -121.4486 |  |  |  |  | 0 | 0
1689 | VALLEY_3G | 3 | North | YES | -0.022897 | 0 | 25 | 375 |  | 1.003 | GST | -1 | 0.27922 | 375 | 375 |  |  | -8.5864 | 375 | -0.27922 | -104.7087 |  |  |  |  | 0 | 0
11693 | KMICHIST3_G | 3 | North | YES | -0.022897 | 312 | 60 | 312 | 0 | 1.026 | CC | -1 | 0.27922 | 312 | 312 |  |  | -7.1439 | 312 | -0.27922 | -87.1176 |  |  |  |  | 0 | 0
11696 | KMICHIST6_G | 6 | North | YES | -0.022897 | 310 | 60 | 310 | 0 | 1.026 | CC | -1 | 0.27922 | 310 | 310 |  |  | -7.0981 | 310 | -0.27922 | -86.5592 |  |  |  |  | 0 | 0
11695 | KMICHICT5_G | 5 | North | YES | -0.022897 | 148 | 80 | 148 | 0 | 1.026 | CC | -1 | 0.27922 | 148 | 148 |  |  | -3.3888 | 148 | -0.27922 | -41.325 |  |  |  |  | 0 | 0
11692 | KMICHICT2_G | 2 | North | YES | -0.022897 | 146 | 80 | 146 | 0 | 1.026 | CC | -1 | 0.27922 | 146 | 146 |  |  | -3.343 | 146 | -0.27922 | -40.7666 |  |  |  |  | 0 | 0
11691 | KMICHICT1_G | 1 | North | YES | -0.022897 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.27922 | 144 | 144 |  |  | -3.2972 | 144 | -0.27922 | -40.2081 |  |  |  |  | 0 | 0
11694 | KMICHICT4_G | 4 | North | YES | -0.022897 | 144 | 80 | 144 | 0 | 1.026 | CC | -1 | 0.27922 | 144 | 144 |  |  | -3.2972 | 144 | -0.27922 | -40.2081 |  |  |  |  | 0 | 0
60201 | RIO DRCS | F | West | YES | 0.25816 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.27923 | 0 | 0 | 0 | 0 |  |  | 0.27923 | 0 |  |  |  |  | 0 | 0
1949 | HANDLEY_5G | 5 | North | YES | -0.02294 | 348 | 150 | 435 | 0 | 1.022 | GST | -1 | 0.27927 | 435 | 435 |  |  | -9.9789 | 435 | -0.27927 | -121.4808 |  |  |  |  | 0 | 0
1947 | HANDLEY_3G | 3 | North | YES | -0.02294 | 316 | 100 | 395 | 0 | 1.022 | GST | -1 | 0.27927 | 395 | 395 |  |  | -9.0613 | 395 | -0.27927 | -110.3101 |  |  |  |  | 0 | 0
2383 | NTHLK3_G | 3 | North | YES | -0.023087 | 0 | 50 | 329 |  | 1.022 | GST | -1 | 0.27941 | 329 | 329 |  |  | -7.5956 | 329 | -0.27941 | -91.9269 |  |  |  |  | 0 | 0
2382 | NTHLK2_G | 2 | North | YES | -0.023087 | 0 | 35 | 181 |  | 1.022 | GST | -1 | 0.27941 | 181 | 181 |  |  | -4.1787 | 181 | -0.27941 | -50.5738 |  |  |  |  | 0 | 0
2381 | NTHLK1_G | 1 | North | YES | -0.023087 | 0 | 35 | 156 |  | 1.022 | GST | -1 | 0.27941 | 156 | 156 |  |  | -3.6016 | 156 | -0.27941 | -43.5885 |  |  |  |  | 0 | 0
1688 | VALLEY_2G | 2 | North | YES | -0.023102 | 527 | 90 | 527 | 0 | 1.029 | GSC | -1 | 0.27943 | 527 | 527 |  |  | -12.1748 | 527 | -0.27943 | -147.2587 |  |  |  |  | 0 | 0
1687 | VALLEY_1G | 1 | North | YES | -0.023102 | 136 | 15 | 170 | 0 | 1.029 | GST | -1 | 0.27943 | 170 | 170 |  |  | -3.9273 | 170 | -0.27943 | -47.5028 |  |  |  |  | 0 | 0
6948 | DENISNDM | 1 | North | YES | -0.023261 | 40 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.27959 | 0 | 0 |  |  | 0 | 0 | -0.27959 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 2 | North | YES | -0.023261 | 31 | 5 | 40 |  | 1.015 | Hydro | -1 | 0.27959 | 0 | 0 |  |  | 0 | 0 | -0.27959 | 0 |  |  |  |  | 0 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | 0.25872 | 30 | 0 | 150 |  | 1.02 | Wind | 1 | 0.27979 | 0 | 150 | 38.8074 | 150 |  |  | 0.27979 | 41.968 |  |  |  |  | 0 | 0
60007 | KING_SW1A | 1 | West | YES | 0.25893 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28 | 0 | 80 | 20.7147 | 80 |  |  | 0.28 | 22.4004 |  |  |  |  | 0 | 0
60019 | KING_NW1A | 1 | West | YES | 0.25893 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28 | 0 | 80 | 20.7147 | 80 |  |  | 0.28 | 22.4004 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 1 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 2 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 2 | North | YES | -0.023726 | 13.6 | 12 | 17 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 1 | North | YES | -0.023726 | 16 | 12 | 20 | 0 | 1 | Cogen | -1 | 0.28005 | 0 | 0 |  |  | 0 | 0 | -0.28005 | 0 |  |  |  |  | 0 | 0
2371 | COLLIN_1G | MB | North | YES | -0.02385 | 0 | 40 | 138 |  | 1.022 | GST | -1 | 0.28018 | 0 | 0 |  |  | 0 | 0 | -0.28018 | 0 |  |  |  |  | 0 | 0
728 | WOLFRIDGE801 | 1 | North | YES | -0.024491 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | -1 | 0.28082 | 0 | 112.5 |  |  | 0 | 0 | -0.28082 | 0 |  |  |  |  | 0 | 0
1349 | WESTXWIN_1G | 1 | West | YES | 0.26137 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.28244 | 0 | 6.6 | 1.725 | 6.6 |  |  | 0.28244 | 1.8641 |  |  |  |  | 0 | 0
1350 | NWPWRG1_1G | 1 | West | YES | 0.26137 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.28244 | 0 | 34.3 | 8.9649 | 34.3 |  |  | 0.28244 | 9.6876 |  |  |  |  | 0 | 0
1433 | GRHAMSES_1G | 1 | North | YES | -0.026119 | 242 | 60 | 242 | 0 | 1.038 | GST | -1 | 0.28245 | 242 | 242 |  |  | -6.3208 | 242 | -0.28245 | -68.3517 |  |  |  |  | 0 | 0
1861 | EAGLEMNT_1G | MB | North | YES | -0.026521 | 0 | 30 | 112 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0 |  |  |  |  | 0 | 0
1862 | EAGLEMNT_2G | MB | North | YES | -0.026521 | 0 | 40 | 100 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0 |  |  |  |  | 0 | 0
1863 | EAGLEMNT_3G | MB | North | YES | -0.026521 | 0 | 50 | 378 |  | 1.022 | GST | -1 | 0.28285 | 0 | 0 |  |  | 0 | 0 | -0.28285 | 0 |  |  |  |  | 0 | 0
1069 | KINDERMG_1G | 1 | West | YES | 0.26256 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0 |  |  |  |  | 0 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.26256 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0 |  |  |  |  | 0 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.26256 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.28364 | 0 | 0 | 0 | 0 |  |  | 0.28364 | 0 |  |  |  |  | 0 | 0
1062 | CIELOGEN_2G | 1 | West | YES | 0.26256 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.28364 | 0 | 61 | 16.0165 | 61 |  |  | 0.28364 | 17.3018 |  |  |  |  | 0 | 0
1061 | CIELOGEN_1G | 1 | West | YES | 0.26256 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.28364 | 0 | 99 | 25.9939 | 99 |  |  | 0.28364 | 28.0799 |  |  |  |  | 0 | 0
1073 | SCURRYCW_2G | 2 | West | YES | 0.26283 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | 0.28391 | 0 | 120 | 31.5402 | 120 |  |  | 0.28391 | 34.0687 |  |  |  |  | 0 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.26283 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | 0.28391 | 0 | 141 | 37.0597 | 141 |  |  | 0.28391 | 40.0307 |  |  |  |  | 0 | 0
924 | SPENCER_G5 | 1 | North | YES | -0.028142 | 52 | 20 | 66 | 0 | 1.03 | GST | -1 | 0.28447 | 66 | 66 |  |  | -1.8574 | 66 | -0.28447 | -18.7749 |  |  |  |  | 0 | 0
923 | SPENCER_G4 | 1 | North | YES | -0.028142 | 48 | 20 | 61 | 0 | 1.03 | GST | -1 | 0.28447 | 61 | 61 |  |  | -1.7167 | 61 | -0.28447 | -17.3526 |  |  |  |  | 0 | 0
6637 | SNYDERW1A | 1 | West | YES | 0.26571 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.28678 | 0 | 63 | 16.7397 | 63 |  |  | 0.28678 | 18.0672 |  |  |  |  | 0 | 0
11309 | BULLCREK_2G | 1 | West | YES | 0.26996 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | 0.29103 | 0 | 180 | 48.5919 | 180 |  |  | 0.29103 | 52.3846 |  |  |  |  | 0 | 0
11310 | BULLCREK_1G | 1 | West | YES | 0.26996 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | 0.29103 | 0 | 180 | 48.5919 | 180 |  |  | 0.29103 | 52.3846 |  |  |  |  | 0 | 0
11320 | COYOTE_1G | 1 | West | YES | 0.2705 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | 0.29157 | 0 | 225 | 60.8625 | 225 |  |  | 0.29157 | 65.6034 |  |  |  |  | 0 | 0
1416 | SWETWATR_1G | 1 | West | YES | 0.27072 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.29179 | 30 | 30 | 8.1217 | 30 |  |  | 0.29179 | 8.7538 |  |  |  |  | 0 | 0
1419 | SWETWATR_4G | 4 | West | YES | 0.27072 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.29179 | 61 | 61 | 16.514 | 61 |  |  | 0.29179 | 17.7994 |  |  |  |  | 0 | 0
1418 | SWETWATR_3G | 3 | West | YES | 0.27072 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.29179 | 68 | 68 | 18.4091 | 68 |  |  | 0.29179 | 19.8419 |  |  |  |  | 0 | 0
1417 | SWETWATR_2G | 2 | West | YES | 0.27072 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.29179 | 72 | 72 | 19.492 | 72 |  |  | 0.29179 | 21.0091 |  |  |  |  | 0 | 0
1320 | BSP 1 | 1 | West | YES | 0.27101 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.29208 | 0 | 0 | 0 | 0 |  |  | 0.29208 | 0 |  |  |  |  | 0 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | 0.27338 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | 0.29445 | 0 | 120 | 32.806 | 120 |  |  | 0.29445 | 35.3345 |  |  |  |  | 0 | 0
1327 | WILDHRSE_1G | 1 | West | YES | 0.27488 | 0 | 0 | 120 |  | 1 | Wind | 1 | 0.29595 | 0 | 120 | 32.986 | 120 |  |  | 0.29595 | 35.5145 |  |  |  |  | 0 | 0
1455 | WCPWRCO_3G | 3 | North | YES | -0.041156 | 242 | 50 | 242 |  | 1.02 | CC | -1 | 0.29748 | 242 | 242 |  |  | -9.9598 | 242 | -0.29748 | -71.9907 |  |  |  |  | 0 | 0
1453 | WCPWRCO_1G | 1 | North | YES | -0.041156 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.29748 | 204 | 204 |  |  | -8.3958 | 204 | -0.29748 | -60.6864 |  |  |  |  | 0 | 0
1454 | WCPWRCO_2G | 2 | North | YES | -0.041156 | 204 | 50 | 204 | 0 | 1.02 | CC | -1 | 0.29748 | 204 | 204 |  |  | -8.3958 | 204 | -0.29748 | -60.6864 |  |  |  |  | 0 | 0
1333 | MCDDONAL_8 | 1 | West | YES | 0.27836 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.29943 | 0 | 214.2 | 59.6254 | 214.2 |  |  | 0.29943 | 64.1387 |  |  |  |  | 0 | 0
1328 | OCOTILLO_1G | 1 | West | YES | 0.27857 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.29964 | 0 | 58 | 16.1571 | 58 |  |  | 0.29964 | 17.3792 |  |  |  |  | 0 | 0
1044 | MRGNFG_6G | F | West | YES | 0.28106 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.30213 | 66 | 66 | 18.5497 | 66 |  |  | 0.30213 | 19.9404 |  |  |  |  | 0 | 0
1042 | MRGNDG_4G | D | West | YES | 0.28106 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.30213 | 68 | 68 | 19.1118 | 68 |  |  | 0.30213 | 20.5446 |  |  |  |  | 0 | 0
1039 | MRGNAG_1G | A | West | YES | 0.28106 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.30213 | 69 | 69 | 19.3929 | 69 |  |  | 0.30213 | 20.8467 |  |  |  |  | 0 | 0
1041 | MRGNCG_3G | C | West | YES | 0.28106 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.30213 | 70 | 70 | 19.6739 | 70 |  |  | 0.30213 | 21.1489 |  |  |  |  | 0 | 0
1043 | MRGNEG_5G | E | West | YES | 0.28106 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.30213 | 70 | 70 | 19.6739 | 70 |  |  | 0.30213 | 21.1489 |  |  |  |  | 0 | 0
1040 | MRGNBG_2G | B | West | YES | 0.28106 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.30213 | 71 | 71 | 19.955 | 71 |  |  | 0.30213 | 21.451 |  |  |  |  | 0 | 0
1037 | MORGAN5G_5G | 5 | West | YES | 0.28106 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.30213 | 137 | 137 | 38.5047 | 137 |  |  | 0.30213 | 41.3914 |  |  |  |  | 0 | 0
1326 | STANTONW_8 | 1 | West | YES | 0.28117 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.30224 | 0 | 100.5 | 28.2574 | 100.5 |  |  | 0.30224 | 30.375 |  |  |  |  | 0 | 0
11147 | NOTREES_1G | 1 | West | YES | 0.28221 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.30329 | 0 | 149 | 42.05 | 149 |  |  | 0.30329 | 45.1896 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.28257 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.30364 | 0 | 30 | 8.477 | 30 |  |  | 0.30364 | 9.1091 |  |  |  |  | 0 | 0
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.28257 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.30364 | 0 | 35 | 9.8898 | 35 |  |  | 0.30364 | 10.6273 |  |  |  |  | 0 | 0
1002 | PBCTAGE_1G | A | West | YES | 0.28269 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.30376 | 66 | 66 | 18.6577 | 66 |  |  | 0.30376 | 20.0483 |  |  |  |  | 0 | 0
1003 | PBCTBGE_2G | B | West | YES | 0.28269 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.30376 | 66 | 66 | 18.6577 | 66 |  |  | 0.30376 | 20.0483 |  |  |  |  | 0 | 0
1004 | PBCTCGE_3G | C | West | YES | 0.28269 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.30376 | 67 | 67 | 18.9404 | 67 |  |  | 0.30376 | 20.3521 |  |  |  |  | 0 | 0
1006 | PBCTEGE_5G | E | West | YES | 0.28269 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.30376 | 67 | 67 | 18.9404 | 67 |  |  | 0.30376 | 20.3521 |  |  |  |  | 0 | 0
1005 | PBCTDGE_4G | D | West | YES | 0.28269 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.30376 | 68 | 68 | 19.2231 | 68 |  |  | 0.30376 | 20.6559 |  |  |  |  | 0 | 0
1007 | PB5GEN_6G | 5 | West | YES | 0.28269 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.30376 | 114 | 114 | 32.2269 | 114 |  |  | 0.30376 | 34.629 |  |  |  |  | 0 | 0
1008 | PB6GEN_7G | 6 | West | YES | 0.28269 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.30376 | 515 | 515 | 145.5864 | 515 |  |  | 0.30376 | 156.4378 |  |  |  |  | 0 | 0
11022 | TIEHVCG_2G | 1 | West | YES | 0.28801 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.30908 | 132.4 | 132.4 | 38.1328 | 132.4 |  |  | 0.30908 | 40.9226 |  |  |  |  | 0 | 0
11023 | TIEHVCG_3G | 1 | West | YES | 0.28801 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.30908 | 137.4 | 137.4 | 39.5728 | 137.4 |  |  | 0.30908 | 42.468 |  |  |  |  | 0 | 0
11021 | TIEHVCG_1G | 1 | West | YES | 0.28801 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.30908 | 142.1 | 142.1 | 40.9265 | 142.1 |  |  | 0.30908 | 43.9207 |  |  |  |  | 0 | 0
11024 | TIEHVCG_4G | 1 | West | YES | 0.28801 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.30908 | 147 | 147 | 42.3378 | 147 |  |  | 0.30908 | 45.4352 |  |  |  |  | 0 | 0
11020 | TIEHVSG_1G | 1 | West | YES | 0.28801 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.30908 | 208.2 | 208.2 | 59.9641 | 208.2 |  |  | 0.30908 | 64.351 |  |  |  |  | 0 | 0
11025 | TIEHVSG_2G | 1 | West | YES | 0.28801 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.30908 | 213.2 | 213.2 | 61.4042 | 213.2 |  |  | 0.30908 | 65.8965 |  |  |  |  | 0 | 0
11001 | NAV1CT | 1 | West | YES | 0.28807 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.30914 | 70.4 | 70.4 | 20.2803 | 70.4 |  |  | 0.30914 | 21.7637 |  |  |  |  | 0 | 0
11009 | NAV2CT | 1 | West | YES | 0.28807 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.30914 | 71.4 | 71.4 | 20.5684 | 71.4 |  |  | 0.30914 | 22.0729 |  |  |  |  | 0 | 0
11012 | NAV4CT | 1 | West | YES | 0.28807 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30914 | 80 | 80 | 23.0458 | 80 |  |  | 0.30914 | 24.7315 |  |  |  |  | 0 | 0
11013 | NAV5CT | 1 | West | YES | 0.28807 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30914 | 80 | 80 | 23.0458 | 80 |  |  | 0.30914 | 24.7315 |  |  |  |  | 0 | 0
11011 | NAV3ST | 1 | West | YES | 0.28807 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.30914 | 92.8 | 92.8 | 26.7332 | 92.8 |  |  | 0.30914 | 28.6885 |  |  |  |  | 0 | 0
11014 | NAV6ST | 1 | West | YES | 0.28807 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.30914 | 115 | 115 | 33.1284 | 115 |  |  | 0.30914 | 35.5515 |  |  |  |  | 0 | 0
1045 | CALENG1G_1G | 1 | West | YES | 0.29237 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0 |  |  |  |  | 0 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.29237 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0 |  |  |  |  | 0 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.29237 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.31344 | 0 | 0 | 0 | 0 |  |  | 0.31344 | 0 |  |  |  |  | 0 | 0
11065 | ELBOWCK_1G | 1 | West | YES | 0.29363 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | 0.3147 | 0 | 121.9 | 35.7934 | 121.9 |  |  | 0.3147 | 38.3619 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 1 | West | YES | 0.29363 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.3147 | 0 | 150 | 44.0444 | 150 |  |  | 0.3147 | 47.205 |  |  |  |  | 0 | 0
1058 | LONGSHORE_5 | 2 | West | YES | 0.29363 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.3147 | 0 | 220 | 64.5984 | 220 |  |  | 0.3147 | 69.234 |  |  |  |  | 0 | 0
1432 | GRHAMSES_2G | 2 | North | YES | -0.07511 | 294.9 | 90 | 366 | 0 | 1.014 | GST | -1 | 0.33144 | 366 | 366 |  |  | -27.4903 | 366 | -0.33144 | -121.3056 |  |  |  |  | 0 | 0
11057 | CHAMPION_1G | 1 | West | YES | 0.37703 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | 0.3981 | 0 | 126.5 | 47.694 | 126.5 |  |  | 0.3981 | 50.3595 |  |  |  |  | 0 | 0
11059 | INADALE_1G | 1 | West | YES | 0.37703 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | 0.3981 | 0 | 197 | 74.2745 | 197 |  |  | 0.3981 | 78.4255 |  |  |  |  | 0 | 0
11056 | ROSCOE_1G | 1 | West | YES | 0.37703 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | 0.3981 | 0 | 209 | 78.7989 | 209 |  |  | 0.3981 | 83.2026 |  |  |  |  | 0 | 0
11058 | PYRON_1G | 1 | West | YES | 0.37703 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | 0.3981 | 0 | 249 | 93.88 | 249 |  |  | 0.3981 | 99.1266 |  |  |  |  | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0

## Zones
Houston | -1
North | -1
South | -1
West | 1
SET UP AREA, copy & paste values to cell B1
Source | West |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | North | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1073 | SCURRYCW_2G | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3126 | TRINIDAD_6G | GST
3309 | ASPN_G | Bio
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5920 | WELSHDC1 | DCTie
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6096 | NORTHDC7 | DCTie
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NBEC7 | GST
8442 | NBEC7 | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11056 | ROSCOE_1G | Wind
11057 | CHAMPION_1G | Wind
11058 | PYRON_1G | Wind
11059 | INADALE_1G | Wind
11065 | ELBOWCK_1G | Wind
11147 | NOTREES_1G | Wind
11309 | BULLCREK_2G | Wind
11310 | BULLCREK_1G | Wind
11320 | COYOTE_1G | Wind
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
48940 | WARVUE_GT1 | Cogen
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
71061 | L_SWEETW1_5N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
76095 | L_CAPRSI1_1N | Wind
76096 | L_CAPRSI1_2N | Wind
76097 | L_CAPRGE1_1N | Wind
80003 | MILHWYS | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80263 | B_DAVIS31A | CC
80264 | B_DAVIS41A | CC
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
86104 | CID-138 | DCTie
86105 | CID-230 | DCTie
86106 | CUF-230 | DCTie
86107 | CUF-138 | DCTie
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR